## History
History:
Version | Date | Descriptions
0.10 | 2021-01-04 | First release
0.20 | 2021-01-27 | With SNMP 0.30 a15
0.30 | 2021-03-04 | Fixed the INLET leakage current unit
0.40 | 2021-04-27 | Fixed the EMD humidity, inlet/outlet energy and current unit, OUTLET closing delay time
0.50 | 2021-11-03 | Add PF alarm
0.60 | 2022-01-12 | Add Power Share
0.70 | 2022-01-27 | Modify Power Share.
0.80 | 2022-03-22 | Fixed the address problem.
0.90 | 2023-01-18 | Add Outlet Sequential Startup Configuration Remove Off Delay Time Status and On Delay Time Status
1.00 | 2023-02-24 | Intlet/Outlet Power Factor unit cnahge 0.1 to 0.01
1.01 | 2024-03-10 | Master PDU status

## 0x03 Holdings
PDU Address (DEC) | Parameter Name | Access | Size | Remark
0 | Master Inlet Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1 | Slave01 Inlet Valid | RO | 2 bytes | 1:Valid; 0:Invalid
2 | Slave02 Inlet Valid | RO | 2 bytes | 1:Valid; 0:Invalid
3 | Slave03 Inlet Valid | RO | 2 bytes | 1:Valid; 0:Invalid
4 | Slave04 Inlet Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5 | Slave05 Inlet Valid | RO | 2 bytes | 1:Valid; 0:Invalid
6 | Slave06 Inlet Valid | RO | 2 bytes | 1:Valid; 0:Invalid
7 | Slave07 Inlet Valid | RO | 2 bytes | 1:Valid; 0:Invalid
8 | Slave08 Inlet Valid | RO | 2 bytes | 1:Valid; 0:Invalid
9 | Slave09 Inlet Valid | RO | 2 bytes | 1:Valid; 0:Invalid
10 | Slave10 Inlet Valid | RO | 2 bytes | 1:Valid; 0:Invalid
11 | Slave11 Inlet Valid | RO | 2 bytes | 1:Valid; 0:Invalid
12 | Slave12 Inlet Valid | RO | 2 bytes | 1:Valid; 0:Invalid
13 | Slave13 Inlet Valid | RO | 2 bytes | 1:Valid; 0:Invalid
14 | Slave14 Inlet Valid | RO | 2 bytes | 1:Valid; 0:Invalid
15 | Slave15 Inlet Valid | RO | 2 bytes | 1:Valid; 0:Invalid
16 | Master Inlet Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1]; Bit10:CT Channel. 1CH[0]/2CH[1]; Bit11:Current Breaker. 16A[0]/32A[1];Bit15:A2 Format Bitmap; must is 1
17 | Slave01 Inlet Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1]; Bit10:CT Channel. 1CH[0]/2CH[1]; Bit11:Current Breaker. 16A[0]/32A[1];Bit15:A2 Format Bitmap; must is 1
18 | Slave02 Inlet Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1]; Bit10:CT Channel. 1CH[0]/2CH[1]; Bit11:Current Breaker. 16A[0]/32A[1];Bit15:A2 Format Bitmap; must is 1
19 | Slave03 Inlet Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1]; Bit10:CT Channel. 1CH[0]/2CH[1]; Bit11:Current Breaker. 16A[0]/32A[1];Bit15:A2 Format Bitmap; must is 1
20 | Slave04 Inlet Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1]; Bit10:CT Channel. 1CH[0]/2CH[1]; Bit11:Current Breaker. 16A[0]/32A[1];Bit15:A2 Format Bitmap; must is 1
21 | Slave05 Inlet Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1]; Bit10:CT Channel. 1CH[0]/2CH[1]; Bit11:Current Breaker. 16A[0]/32A[1];Bit15:A2 Format Bitmap; must is 1
22 | Slave06 Inlet Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1]; Bit10:CT Channel. 1CH[0]/2CH[1]; Bit11:Current Breaker. 16A[0]/32A[1];Bit15:A2 Format Bitmap; must is 1
23 | Slave07 Inlet Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1]; Bit10:CT Channel. 1CH[0]/2CH[1]; Bit11:Current Breaker. 16A[0]/32A[1];Bit15:A2 Format Bitmap; must is 1
24 | Slave08 Inlet Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1]; Bit10:CT Channel. 1CH[0]/2CH[1]; Bit11:Current Breaker. 16A[0]/32A[1];Bit15:A2 Format Bitmap; must is 1
25 | Slave09 Inlet Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1]; Bit10:CT Channel. 1CH[0]/2CH[1]; Bit11:Current Breaker. 16A[0]/32A[1];Bit15:A2 Format Bitmap; must is 1
26 | Slave10 Inlet Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1]; Bit10:CT Channel. 1CH[0]/2CH[1]; Bit11:Current Breaker. 16A[0]/32A[1];Bit15:A2 Format Bitmap; must is 1
27 | Slave11 Inlet Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1]; Bit10:CT Channel. 1CH[0]/2CH[1]; Bit11:Current Breaker. 16A[0]/32A[1];Bit15:A2 Format Bitmap; must is 1
28 | Slave12 Inlet Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1]; Bit10:CT Channel. 1CH[0]/2CH[1]; Bit11:Current Breaker. 16A[0]/32A[1];Bit15:A2 Format Bitmap; must is 1
29 | Slave13 Inlet Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1]; Bit10:CT Channel. 1CH[0]/2CH[1]; Bit11:Current Breaker. 16A[0]/32A[1];Bit15:A2 Format Bitmap; must is 1
30 | Slave14 Inlet Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1]; Bit10:CT Channel. 1CH[0]/2CH[1]; Bit11:Current Breaker. 16A[0]/32A[1];Bit15:A2 Format Bitmap; must is 1
31 | Slave15 Inlet Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1]; Bit10:CT Channel. 1CH[0]/2CH[1]; Bit11:Current Breaker. 16A[0]/32A[1];Bit15:A2 Format Bitmap; must is 1
32 | Master Inlet Over Load Status | RO | 2 bytes | Bit0:Critical; Bit1:Warning
33 | Slave01 Inlet Over Load Status | RO | 2 bytes | Bit0:Critical; Bit1:Warning
34 | Slave02 Inlet Over Load Status | RO | 2 bytes | Bit0:Critical; Bit1:Warning
35 | Slave03 Inlet Over Load Status | RO | 2 bytes | Bit0:Critical; Bit1:Warning
36 | Slave04 Inlet Over Load Status | RO | 2 bytes | Bit0:Critical; Bit1:Warning
37 | Slave05 Inlet Over Load Status | RO | 2 bytes | Bit0:Critical; Bit1:Warning
38 | Slave06 Inlet Over Load Status | RO | 2 bytes | Bit0:Critical; Bit1:Warning
39 | Slave07 Inlet Over Load Status | RO | 2 bytes | Bit0:Critical; Bit1:Warning
40 | Slave08 Inlet Over Load Status | RO | 2 bytes | Bit0:Critical; Bit1:Warning
41 | Slave09 Inlet Over Load Status | RO | 2 bytes | Bit0:Critical; Bit1:Warning
42 | Slave10 Inlet Over Load Status | RO | 2 bytes | Bit0:Critical; Bit1:Warning
43 | Slave11 Inlet Over Load Status | RO | 2 bytes | Bit0:Critical; Bit1:Warning
44 | Slave12 Inlet Over Load Status | RO | 2 bytes | Bit0:Critical; Bit1:Warning
45 | Slave13 Inlet Over Load Status | RO | 2 bytes | Bit0:Critical; Bit1:Warning
46 | Slave14 Inlet Over Load Status | RO | 2 bytes | Bit0:Critical; Bit1:Warning
47 | Slave15 Inlet Over Load Status | RO | 2 bytes | Bit0:Critical; Bit1:Warning
48 | Master Inlet Phase1 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Branch1 Over Cueent Critical;Bit3:Branch1 Over Cueent Warning;Bit4:Branch1 Over Voltage Critical;Bit5:Branch1 Over Voltage Warning; Bit6:Branch2 Over Cueent Critical;Bit7:Branch2 Over Cueent Warning;Bit8:Total Over Cueent Critical;Bit9:Total Over Cueent Warning;Bit10:Branch1 Over PF Warning;Bit11:Branch1 Over PF Critical;Bit12:Branch2 Over PF Warning;Bit13:Branch2 Over PF Critical
49 | Slave01 Inlet Phase1 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Branch1 Over Cueent Critical;Bit3:Branch1 Over Cueent Warning;Bit4:Branch1 Over Voltage Critical;Bit5:Branch1 Over Voltage Warning; Bit6:Branch2 Over Cueent Critical;Bit7:Branch2 Over Cueent Warning;Bit8:Total Over Cueent Critical;Bit9:Total Over Cueent Warning;Bit10:Branch1 Over PF Warning;Bit11:Branch1 Over PF Critical;Bit12:Branch2 Over PF Warning;Bit13:Branch2 Over PF Critical
50 | Slave02 Inlet Phase1 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Branch1 Over Cueent Critical;Bit3:Branch1 Over Cueent Warning;Bit4:Branch1 Over Voltage Critical;Bit5:Branch1 Over Voltage Warning; Bit6:Branch2 Over Cueent Critical;Bit7:Branch2 Over Cueent Warning;Bit8:Total Over Cueent Critical;Bit9:Total Over Cueent Warning;Bit10:Branch1 Over PF Warning;Bit11:Branch1 Over PF Critical;Bit12:Branch2 Over PF Warning;Bit13:Branch2 Over PF Critical
51 | Slave03 Inlet Phase1 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Branch1 Over Cueent Critical;Bit3:Branch1 Over Cueent Warning;Bit4:Branch1 Over Voltage Critical;Bit5:Branch1 Over Voltage Warning; Bit6:Branch2 Over Cueent Critical;Bit7:Branch2 Over Cueent Warning;Bit8:Total Over Cueent Critical;Bit9:Total Over Cueent Warning;Bit10:Branch1 Over PF Warning;Bit11:Branch1 Over PF Critical;Bit12:Branch2 Over PF Warning;Bit13:Branch2 Over PF Critical
52 | Slave04 Inlet Phase1 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Branch1 Over Cueent Critical;Bit3:Branch1 Over Cueent Warning;Bit4:Branch1 Over Voltage Critical;Bit5:Branch1 Over Voltage Warning; Bit6:Branch2 Over Cueent Critical;Bit7:Branch2 Over Cueent Warning;Bit8:Total Over Cueent Critical;Bit9:Total Over Cueent Warning;Bit10:Branch1 Over PF Warning;Bit11:Branch1 Over PF Critical;Bit12:Branch2 Over PF Warning;Bit13:Branch2 Over PF Critical
53 | Slave05 Inlet Phase1 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Branch1 Over Cueent Critical;Bit3:Branch1 Over Cueent Warning;Bit4:Branch1 Over Voltage Critical;Bit5:Branch1 Over Voltage Warning; Bit6:Branch2 Over Cueent Critical;Bit7:Branch2 Over Cueent Warning;Bit8:Total Over Cueent Critical;Bit9:Total Over Cueent Warning;Bit10:Branch1 Over PF Warning;Bit11:Branch1 Over PF Critical;Bit12:Branch2 Over PF Warning;Bit13:Branch2 Over PF Critical
54 | Slave06 Inlet Phase1 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Branch1 Over Cueent Critical;Bit3:Branch1 Over Cueent Warning;Bit4:Branch1 Over Voltage Critical;Bit5:Branch1 Over Voltage Warning; Bit6:Branch2 Over Cueent Critical;Bit7:Branch2 Over Cueent Warning;Bit8:Total Over Cueent Critical;Bit9:Total Over Cueent Warning;Bit10:Branch1 Over PF Warning;Bit11:Branch1 Over PF Critical;Bit12:Branch2 Over PF Warning;Bit13:Branch2 Over PF Critical
55 | Slave07 Inlet Phase1 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Branch1 Over Cueent Critical;Bit3:Branch1 Over Cueent Warning;Bit4:Branch1 Over Voltage Critical;Bit5:Branch1 Over Voltage Warning; Bit6:Branch2 Over Cueent Critical;Bit7:Branch2 Over Cueent Warning;Bit8:Total Over Cueent Critical;Bit9:Total Over Cueent Warning;Bit10:Branch1 Over PF Warning;Bit11:Branch1 Over PF Critical;Bit12:Branch2 Over PF Warning;Bit13:Branch2 Over PF Critical
56 | Slave08 Inlet Phase1 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Branch1 Over Cueent Critical;Bit3:Branch1 Over Cueent Warning;Bit4:Branch1 Over Voltage Critical;Bit5:Branch1 Over Voltage Warning; Bit6:Branch2 Over Cueent Critical;Bit7:Branch2 Over Cueent Warning;Bit8:Total Over Cueent Critical;Bit9:Total Over Cueent Warning;Bit10:Branch1 Over PF Warning;Bit11:Branch1 Over PF Critical;Bit12:Branch2 Over PF Warning;Bit13:Branch2 Over PF Critical
57 | Slave09 Inlet Phase1 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Branch1 Over Cueent Critical;Bit3:Branch1 Over Cueent Warning;Bit4:Branch1 Over Voltage Critical;Bit5:Branch1 Over Voltage Warning; Bit6:Branch2 Over Cueent Critical;Bit7:Branch2 Over Cueent Warning;Bit8:Total Over Cueent Critical;Bit9:Total Over Cueent Warning;Bit10:Branch1 Over PF Warning;Bit11:Branch1 Over PF Critical;Bit12:Branch2 Over PF Warning;Bit13:Branch2 Over PF Critical
58 | Slave10 Inlet Phase1 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Branch1 Over Cueent Critical;Bit3:Branch1 Over Cueent Warning;Bit4:Branch1 Over Voltage Critical;Bit5:Branch1 Over Voltage Warning; Bit6:Branch2 Over Cueent Critical;Bit7:Branch2 Over Cueent Warning;Bit8:Total Over Cueent Critical;Bit9:Total Over Cueent Warning;Bit10:Branch1 Over PF Warning;Bit11:Branch1 Over PF Critical;Bit12:Branch2 Over PF Warning;Bit13:Branch2 Over PF Critical
59 | Slave11 Inlet Phase1 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Branch1 Over Cueent Critical;Bit3:Branch1 Over Cueent Warning;Bit4:Branch1 Over Voltage Critical;Bit5:Branch1 Over Voltage Warning; Bit6:Branch2 Over Cueent Critical;Bit7:Branch2 Over Cueent Warning;Bit8:Total Over Cueent Critical;Bit9:Total Over Cueent Warning;Bit10:Branch1 Over PF Warning;Bit11:Branch1 Over PF Critical;Bit12:Branch2 Over PF Warning;Bit13:Branch2 Over PF Critical
60 | Slave12 Inlet Phase1 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Branch1 Over Cueent Critical;Bit3:Branch1 Over Cueent Warning;Bit4:Branch1 Over Voltage Critical;Bit5:Branch1 Over Voltage Warning; Bit6:Branch2 Over Cueent Critical;Bit7:Branch2 Over Cueent Warning;Bit8:Total Over Cueent Critical;Bit9:Total Over Cueent Warning;Bit10:Branch1 Over PF Warning;Bit11:Branch1 Over PF Critical;Bit12:Branch2 Over PF Warning;Bit13:Branch2 Over PF Critical
61 | Slave13 Inlet Phase1 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Branch1 Over Cueent Critical;Bit3:Branch1 Over Cueent Warning;Bit4:Branch1 Over Voltage Critical;Bit5:Branch1 Over Voltage Warning; Bit6:Branch2 Over Cueent Critical;Bit7:Branch2 Over Cueent Warning;Bit8:Total Over Cueent Critical;Bit9:Total Over Cueent Warning;Bit10:Branch1 Over PF Warning;Bit11:Branch1 Over PF Critical;Bit12:Branch2 Over PF Warning;Bit13:Branch2 Over PF Critical
62 | Slave14 Inlet Phase1 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Branch1 Over Cueent Critical;Bit3:Branch1 Over Cueent Warning;Bit4:Branch1 Over Voltage Critical;Bit5:Branch1 Over Voltage Warning; Bit6:Branch2 Over Cueent Critical;Bit7:Branch2 Over Cueent Warning;Bit8:Total Over Cueent Critical;Bit9:Total Over Cueent Warning;Bit10:Branch1 Over PF Warning;Bit11:Branch1 Over PF Critical;Bit12:Branch2 Over PF Warning;Bit13:Branch2 Over PF Critical
63 | Slave15 Inlet Phase1 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Branch1 Over Cueent Critical;Bit3:Branch1 Over Cueent Warning;Bit4:Branch1 Over Voltage Critical;Bit5:Branch1 Over Voltage Warning; Bit6:Branch2 Over Cueent Critical;Bit7:Branch2 Over Cueent Warning;Bit8:Total Over Cueent Critical;Bit9:Total Over Cueent Warning;Bit10:Branch1 Over PF Warning;Bit11:Branch1 Over PF Critical;Bit12:Branch2 Over PF Warning;Bit13:Branch2 Over PF Critical
64 | Master Inlet Phase2 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Branch1 Over Cueent Critical;Bit3:Branch1 Over Cueent Warning;Bit4:Branch1 Over Voltage Critical;Bit5:Branch1 Over Voltage Warning; Bit6:Branch2 Over Cueent Critical;Bit7:Branch2 Over Cueent Warning;Bit8:Total Over Cueent Critical;Bit9:Total Over Cueent Warning;Bit10:Branch1 Over PF Warning;Bit11:Branch1 Over PF Critical;Bit12:Branch2 Over PF Warning;Bit13:Branch2 Over PF Critical
65 | Slave01 Inlet Phase2 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Branch1 Over Cueent Critical;Bit3:Branch1 Over Cueent Warning;Bit4:Branch1 Over Voltage Critical;Bit5:Branch1 Over Voltage Warning; Bit6:Branch2 Over Cueent Critical;Bit7:Branch2 Over Cueent Warning;Bit8:Total Over Cueent Critical;Bit9:Total Over Cueent Warning;Bit10:Branch1 Over PF Warning;Bit11:Branch1 Over PF Critical;Bit12:Branch2 Over PF Warning;Bit13:Branch2 Over PF Critical
66 | Slave02 Inlet Phase2 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Branch1 Over Cueent Critical;Bit3:Branch1 Over Cueent Warning;Bit4:Branch1 Over Voltage Critical;Bit5:Branch1 Over Voltage Warning; Bit6:Branch2 Over Cueent Critical;Bit7:Branch2 Over Cueent Warning;Bit8:Total Over Cueent Critical;Bit9:Total Over Cueent Warning;Bit10:Branch1 Over PF Warning;Bit11:Branch1 Over PF Critical;Bit12:Branch2 Over PF Warning;Bit13:Branch2 Over PF Critical
67 | Slave03 Inlet Phase2 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Branch1 Over Cueent Critical;Bit3:Branch1 Over Cueent Warning;Bit4:Branch1 Over Voltage Critical;Bit5:Branch1 Over Voltage Warning; Bit6:Branch2 Over Cueent Critical;Bit7:Branch2 Over Cueent Warning;Bit8:Total Over Cueent Critical;Bit9:Total Over Cueent Warning;Bit10:Branch1 Over PF Warning;Bit11:Branch1 Over PF Critical;Bit12:Branch2 Over PF Warning;Bit13:Branch2 Over PF Critical
68 | Slave04 Inlet Phase2 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Branch1 Over Cueent Critical;Bit3:Branch1 Over Cueent Warning;Bit4:Branch1 Over Voltage Critical;Bit5:Branch1 Over Voltage Warning; Bit6:Branch2 Over Cueent Critical;Bit7:Branch2 Over Cueent Warning;Bit8:Total Over Cueent Critical;Bit9:Total Over Cueent Warning;Bit10:Branch1 Over PF Warning;Bit11:Branch1 Over PF Critical;Bit12:Branch2 Over PF Warning;Bit13:Branch2 Over PF Critical
69 | Slave05 Inlet Phase2 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Branch1 Over Cueent Critical;Bit3:Branch1 Over Cueent Warning;Bit4:Branch1 Over Voltage Critical;Bit5:Branch1 Over Voltage Warning; Bit6:Branch2 Over Cueent Critical;Bit7:Branch2 Over Cueent Warning;Bit8:Total Over Cueent Critical;Bit9:Total Over Cueent Warning;Bit10:Branch1 Over PF Warning;Bit11:Branch1 Over PF Critical;Bit12:Branch2 Over PF Warning;Bit13:Branch2 Over PF Critical
70 | Slave06 Inlet Phase2 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Branch1 Over Cueent Critical;Bit3:Branch1 Over Cueent Warning;Bit4:Branch1 Over Voltage Critical;Bit5:Branch1 Over Voltage Warning; Bit6:Branch2 Over Cueent Critical;Bit7:Branch2 Over Cueent Warning;Bit8:Total Over Cueent Critical;Bit9:Total Over Cueent Warning;Bit10:Branch1 Over PF Warning;Bit11:Branch1 Over PF Critical;Bit12:Branch2 Over PF Warning;Bit13:Branch2 Over PF Critical
71 | Slave07 Inlet Phase2 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Branch1 Over Cueent Critical;Bit3:Branch1 Over Cueent Warning;Bit4:Branch1 Over Voltage Critical;Bit5:Branch1 Over Voltage Warning; Bit6:Branch2 Over Cueent Critical;Bit7:Branch2 Over Cueent Warning;Bit8:Total Over Cueent Critical;Bit9:Total Over Cueent Warning;Bit10:Branch1 Over PF Warning;Bit11:Branch1 Over PF Critical;Bit12:Branch2 Over PF Warning;Bit13:Branch2 Over PF Critical
72 | Slave08 Inlet Phase2 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Branch1 Over Cueent Critical;Bit3:Branch1 Over Cueent Warning;Bit4:Branch1 Over Voltage Critical;Bit5:Branch1 Over Voltage Warning; Bit6:Branch2 Over Cueent Critical;Bit7:Branch2 Over Cueent Warning;Bit8:Total Over Cueent Critical;Bit9:Total Over Cueent Warning;Bit10:Branch1 Over PF Warning;Bit11:Branch1 Over PF Critical;Bit12:Branch2 Over PF Warning;Bit13:Branch2 Over PF Critical
73 | Slave09 Inlet Phase2 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Branch1 Over Cueent Critical;Bit3:Branch1 Over Cueent Warning;Bit4:Branch1 Over Voltage Critical;Bit5:Branch1 Over Voltage Warning; Bit6:Branch2 Over Cueent Critical;Bit7:Branch2 Over Cueent Warning;Bit8:Total Over Cueent Critical;Bit9:Total Over Cueent Warning;Bit10:Branch1 Over PF Warning;Bit11:Branch1 Over PF Critical;Bit12:Branch2 Over PF Warning;Bit13:Branch2 Over PF Critical
74 | Slave10 Inlet Phase2 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Branch1 Over Cueent Critical;Bit3:Branch1 Over Cueent Warning;Bit4:Branch1 Over Voltage Critical;Bit5:Branch1 Over Voltage Warning; Bit6:Branch2 Over Cueent Critical;Bit7:Branch2 Over Cueent Warning;Bit8:Total Over Cueent Critical;Bit9:Total Over Cueent Warning;Bit10:Branch1 Over PF Warning;Bit11:Branch1 Over PF Critical;Bit12:Branch2 Over PF Warning;Bit13:Branch2 Over PF Critical
75 | Slave11 Inlet Phase2 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Branch1 Over Cueent Critical;Bit3:Branch1 Over Cueent Warning;Bit4:Branch1 Over Voltage Critical;Bit5:Branch1 Over Voltage Warning; Bit6:Branch2 Over Cueent Critical;Bit7:Branch2 Over Cueent Warning;Bit8:Total Over Cueent Critical;Bit9:Total Over Cueent Warning;Bit10:Branch1 Over PF Warning;Bit11:Branch1 Over PF Critical;Bit12:Branch2 Over PF Warning;Bit13:Branch2 Over PF Critical
76 | Slave12 Inlet Phase2 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Branch1 Over Cueent Critical;Bit3:Branch1 Over Cueent Warning;Bit4:Branch1 Over Voltage Critical;Bit5:Branch1 Over Voltage Warning; Bit6:Branch2 Over Cueent Critical;Bit7:Branch2 Over Cueent Warning;Bit8:Total Over Cueent Critical;Bit9:Total Over Cueent Warning;Bit10:Branch1 Over PF Warning;Bit11:Branch1 Over PF Critical;Bit12:Branch2 Over PF Warning;Bit13:Branch2 Over PF Critical
77 | Slave13 Inlet Phase2 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Branch1 Over Cueent Critical;Bit3:Branch1 Over Cueent Warning;Bit4:Branch1 Over Voltage Critical;Bit5:Branch1 Over Voltage Warning; Bit6:Branch2 Over Cueent Critical;Bit7:Branch2 Over Cueent Warning;Bit8:Total Over Cueent Critical;Bit9:Total Over Cueent Warning;Bit10:Branch1 Over PF Warning;Bit11:Branch1 Over PF Critical;Bit12:Branch2 Over PF Warning;Bit13:Branch2 Over PF Critical
78 | Slave14 Inlet Phase2 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Branch1 Over Cueent Critical;Bit3:Branch1 Over Cueent Warning;Bit4:Branch1 Over Voltage Critical;Bit5:Branch1 Over Voltage Warning; Bit6:Branch2 Over Cueent Critical;Bit7:Branch2 Over Cueent Warning;Bit8:Total Over Cueent Critical;Bit9:Total Over Cueent Warning;Bit10:Branch1 Over PF Warning;Bit11:Branch1 Over PF Critical;Bit12:Branch2 Over PF Warning;Bit13:Branch2 Over PF Critical
79 | Slave15 Inlet Phase2 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Branch1 Over Cueent Critical;Bit3:Branch1 Over Cueent Warning;Bit4:Branch1 Over Voltage Critical;Bit5:Branch1 Over Voltage Warning; Bit6:Branch2 Over Cueent Critical;Bit7:Branch2 Over Cueent Warning;Bit8:Total Over Cueent Critical;Bit9:Total Over Cueent Warning;Bit10:Branch1 Over PF Warning;Bit11:Branch1 Over PF Critical;Bit12:Branch2 Over PF Warning;Bit13:Branch2 Over PF Critical
80 | Master Inlet Phase3 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Branch1 Over Cueent Critical;Bit3:Branch1 Over Cueent Warning;Bit4:Branch1 Over Voltage Critical;Bit5:Branch1 Over Voltage Warning; Bit6:Branch2 Over Cueent Critical;Bit7:Branch2 Over Cueent Warning;Bit8:Total Over Cueent Critical;Bit9:Total Over Cueent Warning;Bit10:Branch1 Over PF Warning;Bit11:Branch1 Over PF Critical;Bit12:Branch2 Over PF Warning;Bit13:Branch2 Over PF Critical
81 | Slave01 Inlet Phase3 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Branch1 Over Cueent Critical;Bit3:Branch1 Over Cueent Warning;Bit4:Branch1 Over Voltage Critical;Bit5:Branch1 Over Voltage Warning; Bit6:Branch2 Over Cueent Critical;Bit7:Branch2 Over Cueent Warning;Bit8:Total Over Cueent Critical;Bit9:Total Over Cueent Warning;Bit10:Branch1 Over PF Warning;Bit11:Branch1 Over PF Critical;Bit12:Branch2 Over PF Warning;Bit13:Branch2 Over PF Critical
82 | Slave02 Inlet Phase3 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Branch1 Over Cueent Critical;Bit3:Branch1 Over Cueent Warning;Bit4:Branch1 Over Voltage Critical;Bit5:Branch1 Over Voltage Warning; Bit6:Branch2 Over Cueent Critical;Bit7:Branch2 Over Cueent Warning;Bit8:Total Over Cueent Critical;Bit9:Total Over Cueent Warning;Bit10:Branch1 Over PF Warning;Bit11:Branch1 Over PF Critical;Bit12:Branch2 Over PF Warning;Bit13:Branch2 Over PF Critical
83 | Slave03 Inlet Phase3 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Branch1 Over Cueent Critical;Bit3:Branch1 Over Cueent Warning;Bit4:Branch1 Over Voltage Critical;Bit5:Branch1 Over Voltage Warning; Bit6:Branch2 Over Cueent Critical;Bit7:Branch2 Over Cueent Warning;Bit8:Total Over Cueent Critical;Bit9:Total Over Cueent Warning;Bit10:Branch1 Over PF Warning;Bit11:Branch1 Over PF Critical;Bit12:Branch2 Over PF Warning;Bit13:Branch2 Over PF Critical
84 | Slave04 Inlet Phase3 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Branch1 Over Cueent Critical;Bit3:Branch1 Over Cueent Warning;Bit4:Branch1 Over Voltage Critical;Bit5:Branch1 Over Voltage Warning; Bit6:Branch2 Over Cueent Critical;Bit7:Branch2 Over Cueent Warning;Bit8:Total Over Cueent Critical;Bit9:Total Over Cueent Warning;Bit10:Branch1 Over PF Warning;Bit11:Branch1 Over PF Critical;Bit12:Branch2 Over PF Warning;Bit13:Branch2 Over PF Critical
85 | Slave05 Inlet Phase3 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Branch1 Over Cueent Critical;Bit3:Branch1 Over Cueent Warning;Bit4:Branch1 Over Voltage Critical;Bit5:Branch1 Over Voltage Warning; Bit6:Branch2 Over Cueent Critical;Bit7:Branch2 Over Cueent Warning;Bit8:Total Over Cueent Critical;Bit9:Total Over Cueent Warning;Bit10:Branch1 Over PF Warning;Bit11:Branch1 Over PF Critical;Bit12:Branch2 Over PF Warning;Bit13:Branch2 Over PF Critical
86 | Slave06 Inlet Phase3 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Branch1 Over Cueent Critical;Bit3:Branch1 Over Cueent Warning;Bit4:Branch1 Over Voltage Critical;Bit5:Branch1 Over Voltage Warning; Bit6:Branch2 Over Cueent Critical;Bit7:Branch2 Over Cueent Warning;Bit8:Total Over Cueent Critical;Bit9:Total Over Cueent Warning;Bit10:Branch1 Over PF Warning;Bit11:Branch1 Over PF Critical;Bit12:Branch2 Over PF Warning;Bit13:Branch2 Over PF Critical
87 | Slave07 Inlet Phase3 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Branch1 Over Cueent Critical;Bit3:Branch1 Over Cueent Warning;Bit4:Branch1 Over Voltage Critical;Bit5:Branch1 Over Voltage Warning; Bit6:Branch2 Over Cueent Critical;Bit7:Branch2 Over Cueent Warning;Bit8:Total Over Cueent Critical;Bit9:Total Over Cueent Warning;Bit10:Branch1 Over PF Warning;Bit11:Branch1 Over PF Critical;Bit12:Branch2 Over PF Warning;Bit13:Branch2 Over PF Critical
88 | Slave08 Inlet Phase3 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Branch1 Over Cueent Critical;Bit3:Branch1 Over Cueent Warning;Bit4:Branch1 Over Voltage Critical;Bit5:Branch1 Over Voltage Warning; Bit6:Branch2 Over Cueent Critical;Bit7:Branch2 Over Cueent Warning;Bit8:Total Over Cueent Critical;Bit9:Total Over Cueent Warning;Bit10:Branch1 Over PF Warning;Bit11:Branch1 Over PF Critical;Bit12:Branch2 Over PF Warning;Bit13:Branch2 Over PF Critical
89 | Slave09 Inlet Phase3 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Branch1 Over Cueent Critical;Bit3:Branch1 Over Cueent Warning;Bit4:Branch1 Over Voltage Critical;Bit5:Branch1 Over Voltage Warning; Bit6:Branch2 Over Cueent Critical;Bit7:Branch2 Over Cueent Warning;Bit8:Total Over Cueent Critical;Bit9:Total Over Cueent Warning;Bit10:Branch1 Over PF Warning;Bit11:Branch1 Over PF Critical;Bit12:Branch2 Over PF Warning;Bit13:Branch2 Over PF Critical
90 | Slave10 Inlet Phase3 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Branch1 Over Cueent Critical;Bit3:Branch1 Over Cueent Warning;Bit4:Branch1 Over Voltage Critical;Bit5:Branch1 Over Voltage Warning; Bit6:Branch2 Over Cueent Critical;Bit7:Branch2 Over Cueent Warning;Bit8:Total Over Cueent Critical;Bit9:Total Over Cueent Warning;Bit10:Branch1 Over PF Warning;Bit11:Branch1 Over PF Critical;Bit12:Branch2 Over PF Warning;Bit13:Branch2 Over PF Critical
91 | Slave11 Inlet Phase3 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Branch1 Over Cueent Critical;Bit3:Branch1 Over Cueent Warning;Bit4:Branch1 Over Voltage Critical;Bit5:Branch1 Over Voltage Warning; Bit6:Branch2 Over Cueent Critical;Bit7:Branch2 Over Cueent Warning;Bit8:Total Over Cueent Critical;Bit9:Total Over Cueent Warning;Bit10:Branch1 Over PF Warning;Bit11:Branch1 Over PF Critical;Bit12:Branch2 Over PF Warning;Bit13:Branch2 Over PF Critical
92 | Slave12 Inlet Phase3 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Branch1 Over Cueent Critical;Bit3:Branch1 Over Cueent Warning;Bit4:Branch1 Over Voltage Critical;Bit5:Branch1 Over Voltage Warning; Bit6:Branch2 Over Cueent Critical;Bit7:Branch2 Over Cueent Warning;Bit8:Total Over Cueent Critical;Bit9:Total Over Cueent Warning;Bit10:Branch1 Over PF Warning;Bit11:Branch1 Over PF Critical;Bit12:Branch2 Over PF Warning;Bit13:Branch2 Over PF Critical
93 | Slave13 Inlet Phase3 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Branch1 Over Cueent Critical;Bit3:Branch1 Over Cueent Warning;Bit4:Branch1 Over Voltage Critical;Bit5:Branch1 Over Voltage Warning; Bit6:Branch2 Over Cueent Critical;Bit7:Branch2 Over Cueent Warning;Bit8:Total Over Cueent Critical;Bit9:Total Over Cueent Warning;Bit10:Branch1 Over PF Warning;Bit11:Branch1 Over PF Critical;Bit12:Branch2 Over PF Warning;Bit13:Branch2 Over PF Critical
94 | Slave14 Inlet Phase3 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Branch1 Over Cueent Critical;Bit3:Branch1 Over Cueent Warning;Bit4:Branch1 Over Voltage Critical;Bit5:Branch1 Over Voltage Warning; Bit6:Branch2 Over Cueent Critical;Bit7:Branch2 Over Cueent Warning;Bit8:Total Over Cueent Critical;Bit9:Total Over Cueent Warning;Bit10:Branch1 Over PF Warning;Bit11:Branch1 Over PF Critical;Bit12:Branch2 Over PF Warning;Bit13:Branch2 Over PF Critical
95 | Slave15 Inlet Phase3 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Branch1 Over Cueent Critical;Bit3:Branch1 Over Cueent Warning;Bit4:Branch1 Over Voltage Critical;Bit5:Branch1 Over Voltage Warning; Bit6:Branch2 Over Cueent Critical;Bit7:Branch2 Over Cueent Warning;Bit8:Total Over Cueent Critical;Bit9:Total Over Cueent Warning;Bit10:Branch1 Over PF Warning;Bit11:Branch1 Over PF Critical;Bit12:Branch2 Over PF Warning;Bit13:Branch2 Over PF Critical
96 | Master Inlet Balance Status | RO | 2 bytes | Bit0:Critical; Bit1:Warning
97 | Slave01 Inlet Balance Status | RO | 2 bytes | Bit0:Critical; Bit1:Warning
98 | Slave02 Inlet Balance Status | RO | 2 bytes | Bit0:Critical; Bit1:Warning
99 | Slave03 Inlet Balance Status | RO | 2 bytes | Bit0:Critical; Bit1:Warning
100 | Slave04 Inlet Balance Status | RO | 2 bytes | Bit0:Critical; Bit1:Warning
101 | Slave05 Inlet Balance Status | RO | 2 bytes | Bit0:Critical; Bit1:Warning
102 | Slave06 Inlet Balance Status | RO | 2 bytes | Bit0:Critical; Bit1:Warning
103 | Slave07 Inlet Balance Status | RO | 2 bytes | Bit0:Critical; Bit1:Warning
104 | Slave08 Inlet Balance Status | RO | 2 bytes | Bit0:Critical; Bit1:Warning
105 | Slave09 Inlet Balance Status | RO | 2 bytes | Bit0:Critical; Bit1:Warning
106 | Slave10 Inlet Balance Status | RO | 2 bytes | Bit0:Critical; Bit1:Warning
107 | Slave11 Inlet Balance Status | RO | 2 bytes | Bit0:Critical; Bit1:Warning
108 | Slave12 Inlet Balance Status | RO | 2 bytes | Bit0:Critical; Bit1:Warning
109 | Slave13 Inlet Balance Status | RO | 2 bytes | Bit0:Critical; Bit1:Warning
110 | Slave14 Inlet Balance Status | RO | 2 bytes | Bit0:Critical; Bit1:Warning
111 | Slave15 Inlet Balance Status | RO | 2 bytes | Bit0:Critical; Bit1:Warning
112 | Master Inlet Phase1 Voltage | RO | 2 bytes | Unit:0.1
113 | Slave01 Inlet Phase1 Voltage | RO | 2 bytes | Unit:0.1
114 | Slave02 Inlet Phase1 Voltage | RO | 2 bytes | Unit:0.1
115 | Slave03 Inlet Phase1 Voltage | RO | 2 bytes | Unit:0.1
116 | Slave04 Inlet Phase1 Voltage | RO | 2 bytes | Unit:0.1
117 | Slave05 Inlet Phase1 Voltage | RO | 2 bytes | Unit:0.1
118 | Slave06 Inlet Phase1 Voltage | RO | 2 bytes | Unit:0.1
119 | Slave07 Inlet Phase1 Voltage | RO | 2 bytes | Unit:0.1
120 | Slave08 Inlet Phase1 Voltage | RO | 2 bytes | Unit:0.1
121 | Slave09 Inlet Phase1 Voltage | RO | 2 bytes | Unit:0.1
122 | Slave10 Inlet Phase1 Voltage | RO | 2 bytes | Unit:0.1
123 | Slave11 Inlet Phase1 Voltage | RO | 2 bytes | Unit:0.1
124 | Slave12 Inlet Phase1 Voltage | RO | 2 bytes | Unit:0.1
125 | Slave13 Inlet Phase1 Voltage | RO | 2 bytes | Unit:0.1
126 | Slave14 Inlet Phase1 Voltage | RO | 2 bytes | Unit:0.1
127 | Slave15 Inlet Phase1 Voltage | RO | 2 bytes | Unit:0.1
128 | Master Inlet Phase2 Voltage | RO | 2 bytes | Unit:0.1
129 | Slave01 Inlet Phase2 Voltage | RO | 2 bytes | Unit:0.1
130 | Slave02 Inlet Phase2 Voltage | RO | 2 bytes | Unit:0.1
131 | Slave03 Inlet Phase2 Voltage | RO | 2 bytes | Unit:0.1
132 | Slave04 Inlet Phase2 Voltage | RO | 2 bytes | Unit:0.1
133 | Slave05 Inlet Phase2 Voltage | RO | 2 bytes | Unit:0.1
134 | Slave06 Inlet Phase2 Voltage | RO | 2 bytes | Unit:0.1
135 | Slave07 Inlet Phase2 Voltage | RO | 2 bytes | Unit:0.1
136 | Slave08 Inlet Phase2 Voltage | RO | 2 bytes | Unit:0.1
137 | Slave09 Inlet Phase2 Voltage | RO | 2 bytes | Unit:0.1
138 | Slave10 Inlet Phase2 Voltage | RO | 2 bytes | Unit:0.1
139 | Slave11 Inlet Phase2 Voltage | RO | 2 bytes | Unit:0.1
140 | Slave12 Inlet Phase2 Voltage | RO | 2 bytes | Unit:0.1
141 | Slave13 Inlet Phase2 Voltage | RO | 2 bytes | Unit:0.1
142 | Slave14 Inlet Phase2 Voltage | RO | 2 bytes | Unit:0.1
143 | Slave15 Inlet Phase2 Voltage | RO | 2 bytes | Unit:0.1
144 | Master Inlet Phase3 Voltage | RO | 2 bytes | Unit:0.1
145 | Slave01 Inlet Phase3 Voltage | RO | 2 bytes | Unit:0.1
146 | Slave02 Inlet Phase3 Voltage | RO | 2 bytes | Unit:0.1
147 | Slave03 Inlet Phase3 Voltage | RO | 2 bytes | Unit:0.1
148 | Slave04 Inlet Phase3 Voltage | RO | 2 bytes | Unit:0.1
149 | Slave05 Inlet Phase3 Voltage | RO | 2 bytes | Unit:0.1
150 | Slave06 Inlet Phase3 Voltage | RO | 2 bytes | Unit:0.1
151 | Slave07 Inlet Phase3 Voltage | RO | 2 bytes | Unit:0.1
152 | Slave08 Inlet Phase3 Voltage | RO | 2 bytes | Unit:0.1
153 | Slave09 Inlet Phase3 Voltage | RO | 2 bytes | Unit:0.1
154 | Slave10 Inlet Phase3 Voltage | RO | 2 bytes | Unit:0.1
155 | Slave11 Inlet Phase3 Voltage | RO | 2 bytes | Unit:0.1
156 | Slave12 Inlet Phase3 Voltage | RO | 2 bytes | Unit:0.1
157 | Slave13 Inlet Phase3 Voltage | RO | 2 bytes | Unit:0.1
158 | Slave14 Inlet Phase3 Voltage | RO | 2 bytes | Unit:0.1
159 | Slave15 Inlet Phase3 Voltage | RO | 2 bytes | Unit:0.1
160 | Master Inlet Phase1 Frequency | RO | 2 bytes | Unit:0.01
161 | Slave01 Inlet Phase1 Frequency | RO | 2 bytes | Unit:0.01
162 | Slave02 Inlet Phase1 Frequency | RO | 2 bytes | Unit:0.01
163 | Slave03 Inlet Phase1 Frequency | RO | 2 bytes | Unit:0.01
164 | Slave04 Inlet Phase1 Frequency | RO | 2 bytes | Unit:0.01
165 | Slave05 Inlet Phase1 Frequency | RO | 2 bytes | Unit:0.01
166 | Slave06 Inlet Phase1 Frequency | RO | 2 bytes | Unit:0.01
167 | Slave07 Inlet Phase1 Frequency | RO | 2 bytes | Unit:0.01
168 | Slave08 Inlet Phase1 Frequency | RO | 2 bytes | Unit:0.01
169 | Slave09 Inlet Phase1 Frequency | RO | 2 bytes | Unit:0.01
170 | Slave10 Inlet Phase1 Frequency | RO | 2 bytes | Unit:0.01
171 | Slave11 Inlet Phase1 Frequency | RO | 2 bytes | Unit:0.01
172 | Slave12 Inlet Phase1 Frequency | RO | 2 bytes | Unit:0.01
173 | Slave13 Inlet Phase1 Frequency | RO | 2 bytes | Unit:0.01
174 | Slave14 Inlet Phase1 Frequency | RO | 2 bytes | Unit:0.01
175 | Slave15 Inlet Phase1 Frequency | RO | 2 bytes | Unit:0.01
176 | Master Inlet Phase2 Frequency | RO | 2 bytes | Unit:0.01
177 | Slave01 Inlet Phase2 Frequency | RO | 2 bytes | Unit:0.01
178 | Slave02 Inlet Phase2 Frequency | RO | 2 bytes | Unit:0.01
179 | Slave03 Inlet Phase2 Frequency | RO | 2 bytes | Unit:0.01
180 | Slave04 Inlet Phase2 Frequency | RO | 2 bytes | Unit:0.01
181 | Slave05 Inlet Phase2 Frequency | RO | 2 bytes | Unit:0.01
182 | Slave06 Inlet Phase2 Frequency | RO | 2 bytes | Unit:0.01
183 | Slave07 Inlet Phase2 Frequency | RO | 2 bytes | Unit:0.01
184 | Slave08 Inlet Phase2 Frequency | RO | 2 bytes | Unit:0.01
185 | Slave09 Inlet Phase2 Frequency | RO | 2 bytes | Unit:0.01
186 | Slave10 Inlet Phase2 Frequency | RO | 2 bytes | Unit:0.01
187 | Slave11 Inlet Phase2 Frequency | RO | 2 bytes | Unit:0.01
188 | Slave12 Inlet Phase2 Frequency | RO | 2 bytes | Unit:0.01
189 | Slave13 Inlet Phase2 Frequency | RO | 2 bytes | Unit:0.01
190 | Slave14 Inlet Phase2 Frequency | RO | 2 bytes | Unit:0.01
191 | Slave15 Inlet Phase2 Frequency | RO | 2 bytes | Unit:0.01
192 | Master Inlet Phase3 Frequency | RO | 2 bytes | Unit:0.01
193 | Slave01 Inlet Phase3 Frequency | RO | 2 bytes | Unit:0.01
194 | Slave02 Inlet Phase3 Frequency | RO | 2 bytes | Unit:0.01
195 | Slave03 Inlet Phase3 Frequency | RO | 2 bytes | Unit:0.01
196 | Slave04 Inlet Phase3 Frequency | RO | 2 bytes | Unit:0.01
197 | Slave05 Inlet Phase3 Frequency | RO | 2 bytes | Unit:0.01
198 | Slave06 Inlet Phase3 Frequency | RO | 2 bytes | Unit:0.01
199 | Slave07 Inlet Phase3 Frequency | RO | 2 bytes | Unit:0.01
200 | Slave08 Inlet Phase3 Frequency | RO | 2 bytes | Unit:0.01
201 | Slave09 Inlet Phase3 Frequency | RO | 2 bytes | Unit:0.01
202 | Slave10 Inlet Phase3 Frequency | RO | 2 bytes | Unit:0.01
203 | Slave11 Inlet Phase3 Frequency | RO | 2 bytes | Unit:0.01
204 | Slave12 Inlet Phase3 Frequency | RO | 2 bytes | Unit:0.01
205 | Slave13 Inlet Phase3 Frequency | RO | 2 bytes | Unit:0.01
206 | Slave14 Inlet Phase3 Frequency | RO | 2 bytes | Unit:0.01
207 | Slave15 Inlet Phase3 Frequency | RO | 2 bytes | Unit:0.01
208 | Master Inlet Phase1 PF for Branch1 | RO | 2 bytes | Unit:0.01
209 | Slave01 Inlet Phase1 PF for Branch1 | RO | 2 bytes | Unit:0.01
210 | Slave02 Inlet Phase1 PF for Branch1 | RO | 2 bytes | Unit:0.01
211 | Slave03 Inlet Phase1 PF for Branch1 | RO | 2 bytes | Unit:0.01
212 | Slave04 Inlet Phase1 PF for Branch1 | RO | 2 bytes | Unit:0.01
213 | Slave05 Inlet Phase1 PF for Branch1 | RO | 2 bytes | Unit:0.01
214 | Slave06 Inlet Phase1 PF for Branch1 | RO | 2 bytes | Unit:0.01
215 | Slave07 Inlet Phase1 PF for Branch1 | RO | 2 bytes | Unit:0.01
216 | Slave08 Inlet Phase1 PF for Branch1 | RO | 2 bytes | Unit:0.01
217 | Slave09 Inlet Phase1 PF for Branch1 | RO | 2 bytes | Unit:0.01
218 | Slave10 Inlet Phase1 PF for Branch1 | RO | 2 bytes | Unit:0.01
219 | Slave11 Inlet Phase1 PF for Branch1 | RO | 2 bytes | Unit:0.01
220 | Slave12 Inlet Phase1 PF for Branch1 | RO | 2 bytes | Unit:0.01
221 | Slave13 Inlet Phase1 PF for Branch1 | RO | 2 bytes | Unit:0.01
222 | Slave14 Inlet Phase1 PF for Branch1 | RO | 2 bytes | Unit:0.01
223 | Slave15 Inlet Phase1 PF for Branch1 | RO | 2 bytes | Unit:0.01
224 | Master Inlet Phase2 PF for Branch1 | RO | 2 bytes | Unit:0.01
225 | Slave01 Inlet Phase2 PF for Branch1 | RO | 2 bytes | Unit:0.01
226 | Slave02 Inlet Phase2 PF for Branch1 | RO | 2 bytes | Unit:0.01
227 | Slave03 Inlet Phase2 PF for Branch1 | RO | 2 bytes | Unit:0.01
228 | Slave04 Inlet Phase2 PF for Branch1 | RO | 2 bytes | Unit:0.01
229 | Slave05 Inlet Phase2 PF for Branch1 | RO | 2 bytes | Unit:0.01
230 | Slave06 Inlet Phase2 PF for Branch1 | RO | 2 bytes | Unit:0.01
231 | Slave07 Inlet Phase2 PF for Branch1 | RO | 2 bytes | Unit:0.01
232 | Slave08 Inlet Phase2 PF for Branch1 | RO | 2 bytes | Unit:0.01
233 | Slave09 Inlet Phase2 PF for Branch1 | RO | 2 bytes | Unit:0.01
234 | Slave10 Inlet Phase2 PF for Branch1 | RO | 2 bytes | Unit:0.01
235 | Slave11 Inlet Phase2 PF for Branch1 | RO | 2 bytes | Unit:0.01
236 | Slave12 Inlet Phase2 PF for Branch1 | RO | 2 bytes | Unit:0.01
237 | Slave13 Inlet Phase2 PF for Branch1 | RO | 2 bytes | Unit:0.01
238 | Slave14 Inlet Phase2 PF for Branch1 | RO | 2 bytes | Unit:0.01
239 | Slave15 Inlet Phase2 PF for Branch1 | RO | 2 bytes | Unit:0.01
240 | Master Inlet Phase3 PF for Branch1 | RO | 2 bytes | Unit:0.01
241 | Slave01 Inlet Phase3 PF for Branch1 | RO | 2 bytes | Unit:0.01
242 | Slave02 Inlet Phase3 PF for Branch1 | RO | 2 bytes | Unit:0.01
243 | Slave03 Inlet Phase3 PF for Branch1 | RO | 2 bytes | Unit:0.01
244 | Slave04 Inlet Phase3 PF for Branch1 | RO | 2 bytes | Unit:0.01
245 | Slave05 Inlet Phase3 PF for Branch1 | RO | 2 bytes | Unit:0.01
246 | Slave06 Inlet Phase3 PF for Branch1 | RO | 2 bytes | Unit:0.01
247 | Slave07 Inlet Phase3 PF for Branch1 | RO | 2 bytes | Unit:0.01
248 | Slave08 Inlet Phase3 PF for Branch1 | RO | 2 bytes | Unit:0.01
249 | Slave09 Inlet Phase3 PF for Branch1 | RO | 2 bytes | Unit:0.01
250 | Slave10 Inlet Phase3 PF for Branch1 | RO | 2 bytes | Unit:0.01
251 | Slave11 Inlet Phase3 PF for Branch1 | RO | 2 bytes | Unit:0.01
252 | Slave12 Inlet Phase3 PF for Branch1 | RO | 2 bytes | Unit:0.01
253 | Slave13 Inlet Phase3 PF for Branch1 | RO | 2 bytes | Unit:0.01
254 | Slave14 Inlet Phase3 PF for Branch1 | RO | 2 bytes | Unit:0.01
255 | Slave15 Inlet Phase3 PF for Branch1 | RO | 2 bytes | Unit:0.01
256 | Master Inlet Phase1 PF for Branch2 | RO | 2 bytes | Unit:0.01
257 | Slave01 Inlet Phase1 PF for Branch2 | RO | 2 bytes | Unit:0.01
258 | Slave02 Inlet Phase1 PF for Branch2 | RO | 2 bytes | Unit:0.01
259 | Slave03 Inlet Phase1 PF for Branch2 | RO | 2 bytes | Unit:0.01
260 | Slave04 Inlet Phase1 PF for Branch2 | RO | 2 bytes | Unit:0.01
261 | Slave05 Inlet Phase1 PF for Branch2 | RO | 2 bytes | Unit:0.01
262 | Slave06 Inlet Phase1 PF for Branch2 | RO | 2 bytes | Unit:0.01
263 | Slave07 Inlet Phase1 PF for Branch2 | RO | 2 bytes | Unit:0.01
264 | Slave08 Inlet Phase1 PF for Branch2 | RO | 2 bytes | Unit:0.01
265 | Slave09 Inlet Phase1 PF for Branch2 | RO | 2 bytes | Unit:0.01
266 | Slave10 Inlet Phase1 PF for Branch2 | RO | 2 bytes | Unit:0.01
267 | Slave11 Inlet Phase1 PF for Branch2 | RO | 2 bytes | Unit:0.01
268 | Slave12 Inlet Phase1 PF for Branch2 | RO | 2 bytes | Unit:0.01
269 | Slave13 Inlet Phase1 PF for Branch2 | RO | 2 bytes | Unit:0.01
270 | Slave14 Inlet Phase1 PF for Branch2 | RO | 2 bytes | Unit:0.01
271 | Slave15 Inlet Phase1 PF for Branch2 | RO | 2 bytes | Unit:0.01
272 | Master Inlet Phase2 PF for Branch2 | RO | 2 bytes | Unit:0.01
273 | Slave01 Inlet Phase2 PF for Branch2 | RO | 2 bytes | Unit:0.01
274 | Slave02 Inlet Phase2 PF for Branch2 | RO | 2 bytes | Unit:0.01
275 | Slave03 Inlet Phase2 PF for Branch2 | RO | 2 bytes | Unit:0.01
276 | Slave04 Inlet Phase2 PF for Branch2 | RO | 2 bytes | Unit:0.01
277 | Slave05 Inlet Phase2 PF for Branch2 | RO | 2 bytes | Unit:0.01
278 | Slave06 Inlet Phase2 PF for Branch2 | RO | 2 bytes | Unit:0.01
279 | Slave07 Inlet Phase2 PF for Branch2 | RO | 2 bytes | Unit:0.01
280 | Slave08 Inlet Phase2 PF for Branch2 | RO | 2 bytes | Unit:0.01
281 | Slave09 Inlet Phase2 PF for Branch2 | RO | 2 bytes | Unit:0.01
282 | Slave10 Inlet Phase2 PF for Branch2 | RO | 2 bytes | Unit:0.01
283 | Slave11 Inlet Phase2 PF for Branch2 | RO | 2 bytes | Unit:0.01
284 | Slave12 Inlet Phase2 PF for Branch2 | RO | 2 bytes | Unit:0.01
285 | Slave13 Inlet Phase2 PF for Branch2 | RO | 2 bytes | Unit:0.01
286 | Slave14 Inlet Phase2 PF for Branch2 | RO | 2 bytes | Unit:0.01
287 | Slave15 Inlet Phase2 PF for Branch2 | RO | 2 bytes | Unit:0.01
288 | Master Inlet Phase3 PF for Branch2 | RO | 2 bytes | Unit:0.01
289 | Slave01 Inlet Phase3 PF for Branch2 | RO | 2 bytes | Unit:0.01
290 | Slave02 Inlet Phase3 PF for Branch2 | RO | 2 bytes | Unit:0.01
291 | Slave03 Inlet Phase3 PF for Branch2 | RO | 2 bytes | Unit:0.01
292 | Slave04 Inlet Phase3 PF for Branch2 | RO | 2 bytes | Unit:0.01
293 | Slave05 Inlet Phase3 PF for Branch2 | RO | 2 bytes | Unit:0.01
294 | Slave06 Inlet Phase3 PF for Branch2 | RO | 2 bytes | Unit:0.01
295 | Slave07 Inlet Phase3 PF for Branch2 | RO | 2 bytes | Unit:0.01
296 | Slave08 Inlet Phase3 PF for Branch2 | RO | 2 bytes | Unit:0.01
297 | Slave09 Inlet Phase3 PF for Branch2 | RO | 2 bytes | Unit:0.01
298 | Slave10 Inlet Phase3 PF for Branch2 | RO | 2 bytes | Unit:0.01
299 | Slave11 Inlet Phase3 PF for Branch2 | RO | 2 bytes | Unit:0.01
300 | Slave12 Inlet Phase3 PF for Branch2 | RO | 2 bytes | Unit:0.01
301 | Slave13 Inlet Phase3 PF for Branch2 | RO | 2 bytes | Unit:0.01
302 | Slave14 Inlet Phase3 PF for Branch2 | RO | 2 bytes | Unit:0.01
303 | Slave15 Inlet Phase3 PF for Branch2 | RO | 2 bytes | Unit:0.01
304 | Master Inlet Phase1 Current for Branch1 | RO | 2 bytes | Unit:0.01
305 | Slave01 Inlet Phase1 Current for Branch1 | RO | 2 bytes | Unit:0.01
306 | Slave02 Inlet Phase1 Current for Branch1 | RO | 2 bytes | Unit:0.01
307 | Slave03 Inlet Phase1 Current for Branch1 | RO | 2 bytes | Unit:0.01
308 | Slave04 Inlet Phase1 Current for Branch1 | RO | 2 bytes | Unit:0.01
309 | Slave05 Inlet Phase1 Current for Branch1 | RO | 2 bytes | Unit:0.01
310 | Slave06 Inlet Phase1 Current for Branch1 | RO | 2 bytes | Unit:0.01
311 | Slave07 Inlet Phase1 Current for Branch1 | RO | 2 bytes | Unit:0.01
312 | Slave08 Inlet Phase1 Current for Branch1 | RO | 2 bytes | Unit:0.01
313 | Slave09 Inlet Phase1 Current for Branch1 | RO | 2 bytes | Unit:0.01
314 | Slave10 Inlet Phase1 Current for Branch1 | RO | 2 bytes | Unit:0.01
315 | Slave11 Inlet Phase1 Current for Branch1 | RO | 2 bytes | Unit:0.01
316 | Slave12 Inlet Phase1 Current for Branch1 | RO | 2 bytes | Unit:0.01
317 | Slave13 Inlet Phase1 Current for Branch1 | RO | 2 bytes | Unit:0.01
318 | Slave14 Inlet Phase1 Current for Branch1 | RO | 2 bytes | Unit:0.01
319 | Slave15 Inlet Phase1 Current for Branch1 | RO | 2 bytes | Unit:0.01
320 | Master Inlet Phase2 Current for Branch1 | RO | 2 bytes | Unit:0.01
321 | Slave01 Inlet Phase2 Current for Branch1 | RO | 2 bytes | Unit:0.01
322 | Slave02 Inlet Phase2 Current for Branch1 | RO | 2 bytes | Unit:0.01
323 | Slave03 Inlet Phase2 Current for Branch1 | RO | 2 bytes | Unit:0.01
324 | Slave04 Inlet Phase2 Current for Branch1 | RO | 2 bytes | Unit:0.01
325 | Slave05 Inlet Phase2 Current for Branch1 | RO | 2 bytes | Unit:0.01
326 | Slave06 Inlet Phase2 Current for Branch1 | RO | 2 bytes | Unit:0.01
327 | Slave07 Inlet Phase2 Current for Branch1 | RO | 2 bytes | Unit:0.01
328 | Slave08 Inlet Phase2 Current for Branch1 | RO | 2 bytes | Unit:0.01
329 | Slave09 Inlet Phase2 Current for Branch1 | RO | 2 bytes | Unit:0.01
330 | Slave10 Inlet Phase2 Current for Branch1 | RO | 2 bytes | Unit:0.01
331 | Slave11 Inlet Phase2 Current for Branch1 | RO | 2 bytes | Unit:0.01
332 | Slave12 Inlet Phase2 Current for Branch1 | RO | 2 bytes | Unit:0.01
333 | Slave13 Inlet Phase2 Current for Branch1 | RO | 2 bytes | Unit:0.01
334 | Slave14 Inlet Phase2 Current for Branch1 | RO | 2 bytes | Unit:0.01
335 | Slave15 Inlet Phase2 Current for Branch1 | RO | 2 bytes | Unit:0.01
336 | Master Inlet Phase3 Current for Branch1 | RO | 2 bytes | Unit:0.01
337 | Slave01 Inlet Phase3 Current for Branch1 | RO | 2 bytes | Unit:0.01
338 | Slave02 Inlet Phase3 Current for Branch1 | RO | 2 bytes | Unit:0.01
339 | Slave03 Inlet Phase3 Current for Branch1 | RO | 2 bytes | Unit:0.01
340 | Slave04 Inlet Phase3 Current for Branch1 | RO | 2 bytes | Unit:0.01
341 | Slave05 Inlet Phase3 Current for Branch1 | RO | 2 bytes | Unit:0.01
342 | Slave06 Inlet Phase3 Current for Branch1 | RO | 2 bytes | Unit:0.01
343 | Slave07 Inlet Phase3 Current for Branch1 | RO | 2 bytes | Unit:0.01
344 | Slave08 Inlet Phase3 Current for Branch1 | RO | 2 bytes | Unit:0.01
345 | Slave09 Inlet Phase3 Current for Branch1 | RO | 2 bytes | Unit:0.01
346 | Slave10 Inlet Phase3 Current for Branch1 | RO | 2 bytes | Unit:0.01
347 | Slave11 Inlet Phase3 Current for Branch1 | RO | 2 bytes | Unit:0.01
348 | Slave12 Inlet Phase3 Current for Branch1 | RO | 2 bytes | Unit:0.01
349 | Slave13 Inlet Phase3 Current for Branch1 | RO | 2 bytes | Unit:0.01
350 | Slave14 Inlet Phase3 Current for Branch1 | RO | 2 bytes | Unit:0.01
351 | Slave15 Inlet Phase3 Current for Branch1 | RO | 2 bytes | Unit:0.01
352 | Master Inlet Phase1 Current for Branch2 | RO | 2 bytes | Unit:0.01
353 | Slave01 Inlet Phase1 Current for Branch2 | RO | 2 bytes | Unit:0.01
354 | Slave02 Inlet Phase1 Current for Branch2 | RO | 2 bytes | Unit:0.01
355 | Slave03 Inlet Phase1 Current for Branch2 | RO | 2 bytes | Unit:0.01
356 | Slave04 Inlet Phase1 Current for Branch2 | RO | 2 bytes | Unit:0.01
357 | Slave05 Inlet Phase1 Current for Branch2 | RO | 2 bytes | Unit:0.01
358 | Slave06 Inlet Phase1 Current for Branch2 | RO | 2 bytes | Unit:0.01
359 | Slave07 Inlet Phase1 Current for Branch2 | RO | 2 bytes | Unit:0.01
360 | Slave08 Inlet Phase1 Current for Branch2 | RO | 2 bytes | Unit:0.01
361 | Slave09 Inlet Phase1 Current for Branch2 | RO | 2 bytes | Unit:0.01
362 | Slave10 Inlet Phase1 Current for Branch2 | RO | 2 bytes | Unit:0.01
363 | Slave11 Inlet Phase1 Current for Branch2 | RO | 2 bytes | Unit:0.01
364 | Slave12 Inlet Phase1 Current for Branch2 | RO | 2 bytes | Unit:0.01
365 | Slave13 Inlet Phase1 Current for Branch2 | RO | 2 bytes | Unit:0.01
366 | Slave14 Inlet Phase1 Current for Branch2 | RO | 2 bytes | Unit:0.01
367 | Slave15 Inlet Phase1 Current for Branch2 | RO | 2 bytes | Unit:0.01
368 | Master Inlet Phase2 Current for Branch2 | RO | 2 bytes | Unit:0.01
369 | Slave01 Inlet Phase2 Current for Branch2 | RO | 2 bytes | Unit:0.01
370 | Slave02 Inlet Phase2 Current for Branch2 | RO | 2 bytes | Unit:0.01
371 | Slave03 Inlet Phase2 Current for Branch2 | RO | 2 bytes | Unit:0.01
372 | Slave04 Inlet Phase2 Current for Branch2 | RO | 2 bytes | Unit:0.01
373 | Slave05 Inlet Phase2 Current for Branch2 | RO | 2 bytes | Unit:0.01
374 | Slave06 Inlet Phase2 Current for Branch2 | RO | 2 bytes | Unit:0.01
375 | Slave07 Inlet Phase2 Current for Branch2 | RO | 2 bytes | Unit:0.01
376 | Slave08 Inlet Phase2 Current for Branch2 | RO | 2 bytes | Unit:0.01
377 | Slave09 Inlet Phase2 Current for Branch2 | RO | 2 bytes | Unit:0.01
378 | Slave10 Inlet Phase2 Current for Branch2 | RO | 2 bytes | Unit:0.01
379 | Slave11 Inlet Phase2 Current for Branch2 | RO | 2 bytes | Unit:0.01
380 | Slave12 Inlet Phase2 Current for Branch2 | RO | 2 bytes | Unit:0.01
381 | Slave13 Inlet Phase2 Current for Branch2 | RO | 2 bytes | Unit:0.01
382 | Slave14 Inlet Phase2 Current for Branch2 | RO | 2 bytes | Unit:0.01
383 | Slave15 Inlet Phase2 Current for Branch2 | RO | 2 bytes | Unit:0.01
384 | Master Inlet Phase3 Current for Branch2 | RO | 2 bytes | Unit:0.01
385 | Slave01 Inlet Phase3 Current for Branch2 | RO | 2 bytes | Unit:0.01
386 | Slave02 Inlet Phase3 Current for Branch2 | RO | 2 bytes | Unit:0.01
387 | Slave03 Inlet Phase3 Current for Branch2 | RO | 2 bytes | Unit:0.01
388 | Slave04 Inlet Phase3 Current for Branch2 | RO | 2 bytes | Unit:0.01
389 | Slave05 Inlet Phase3 Current for Branch2 | RO | 2 bytes | Unit:0.01
390 | Slave06 Inlet Phase3 Current for Branch2 | RO | 2 bytes | Unit:0.01
391 | Slave07 Inlet Phase3 Current for Branch2 | RO | 2 bytes | Unit:0.01
392 | Slave08 Inlet Phase3 Current for Branch2 | RO | 2 bytes | Unit:0.01
393 | Slave09 Inlet Phase3 Current for Branch2 | RO | 2 bytes | Unit:0.01
394 | Slave10 Inlet Phase3 Current for Branch2 | RO | 2 bytes | Unit:0.01
395 | Slave11 Inlet Phase3 Current for Branch2 | RO | 2 bytes | Unit:0.01
396 | Slave12 Inlet Phase3 Current for Branch2 | RO | 2 bytes | Unit:0.01
397 | Slave13 Inlet Phase3 Current for Branch2 | RO | 2 bytes | Unit:0.01
398 | Slave14 Inlet Phase3 Current for Branch2 | RO | 2 bytes | Unit:0.01
399 | Slave15 Inlet Phase3 Current for Branch2 | RO | 2 bytes | Unit:0.01
400 | Master Inlet Leakage Current Valid | RO | 2 bytes | 1:Valid; 0:Invalid
401 | Slave01 Inlet Leakage Current Valid | RO | 2 bytes | 1:Valid; 0:Invalid
402 | Slave02 Inlet Leakage Current Valid | RO | 2 bytes | 1:Valid; 0:Invalid
403 | Slave03 Inlet Leakage Current Valid | RO | 2 bytes | 1:Valid; 0:Invalid
404 | Slave04 Inlet Leakage Current Valid | RO | 2 bytes | 1:Valid; 0:Invalid
405 | Slave05 Inlet Leakage Current Valid | RO | 2 bytes | 1:Valid; 0:Invalid
406 | Slave06 Inlet Leakage Current Valid | RO | 2 bytes | 1:Valid; 0:Invalid
407 | Slave07 Inlet Leakage Current Valid | RO | 2 bytes | 1:Valid; 0:Invalid
408 | Slave08 Inlet Leakage Current Valid | RO | 2 bytes | 1:Valid; 0:Invalid
409 | Slave09 Inlet Leakage Current Valid | RO | 2 bytes | 1:Valid; 0:Invalid
410 | Slave10 Inlet Leakage Current Valid | RO | 2 bytes | 1:Valid; 0:Invalid
411 | Slave11 Inlet Leakage Current Valid | RO | 2 bytes | 1:Valid; 0:Invalid
412 | Slave12 Inlet Leakage Current Valid | RO | 2 bytes | 1:Valid; 0:Invalid
413 | Slave13 Inlet Leakage Current Valid | RO | 2 bytes | 1:Valid; 0:Invalid
414 | Slave14 Inlet Leakage Current Valid | RO | 2 bytes | 1:Valid; 0:Invalid
415 | Slave15 Inlet Leakage Current Valid | RO | 2 bytes | 1:Valid; 0:Invalid
416 | Master Inlet Leakage Current Value | RO | 2 bytes | Unit:0.1mA
417 | Slave01 Inlet Leakage Current Value | RO | 2 bytes | Unit:0.1mA
418 | Slave02 Inlet Leakage Current Value | RO | 2 bytes | Unit:0.1mA
419 | Slave03 Inlet Leakage Current Value | RO | 2 bytes | Unit:0.1mA
420 | Slave04 Inlet Leakage Current Value | RO | 2 bytes | Unit:0.1mA
421 | Slave05 Inlet Leakage Current Value | RO | 2 bytes | Unit:0.1mA
422 | Slave06 Inlet Leakage Current Value | RO | 2 bytes | Unit:0.1mA
423 | Slave07 Inlet Leakage Current Value | RO | 2 bytes | Unit:0.1mA
424 | Slave08 Inlet Leakage Current Value | RO | 2 bytes | Unit:0.1mA
425 | Slave09 Inlet Leakage Current Value | RO | 2 bytes | Unit:0.1mA
426 | Slave10 Inlet Leakage Current Value | RO | 2 bytes | Unit:0.1mA
427 | Slave11 Inlet Leakage Current Value | RO | 2 bytes | Unit:0.1mA
428 | Slave12 Inlet Leakage Current Value | RO | 2 bytes | Unit:0.1mA
429 | Slave13 Inlet Leakage Current Value | RO | 2 bytes | Unit:0.1mA
430 | Slave14 Inlet Leakage Current Value | RO | 2 bytes | Unit:0.1mA
431 | Slave15 Inlet Leakage Current Value | RO | 2 bytes | Unit:0.1mA
432 | Master Inlet Leakage Current Status | RO | 2 bytes | 0:normal; 1:alarm
433 | Slave01 Inlet Leakage Current Status | RO | 2 bytes | 0:normal; 1:alarm
434 | Slave02 Inlet Leakage Current Status | RO | 2 bytes | 0:normal; 1:alarm
435 | Slave03 Inlet Leakage Current Status | RO | 2 bytes | 0:normal; 1:alarm
436 | Slave04 Inlet Leakage Current Status | RO | 2 bytes | 0:normal; 1:alarm
437 | Slave05 Inlet Leakage Current Status | RO | 2 bytes | 0:normal; 1:alarm
438 | Slave06 Inlet Leakage Current Status | RO | 2 bytes | 0:normal; 1:alarm
439 | Slave07 Inlet Leakage Current Status | RO | 2 bytes | 0:normal; 1:alarm
440 | Slave08 Inlet Leakage Current Status | RO | 2 bytes | 0:normal; 1:alarm
441 | Slave09 Inlet Leakage Current Status | RO | 2 bytes | 0:normal; 1:alarm
442 | Slave10 Inlet Leakage Current Status | RO | 2 bytes | 0:normal; 1:alarm
443 | Slave11 Inlet Leakage Current Status | RO | 2 bytes | 0:normal; 1:alarm
444 | Slave12 Inlet Leakage Current Status | RO | 2 bytes | 0:normal; 1:alarm
445 | Slave13 Inlet Leakage Current Status | RO | 2 bytes | 0:normal; 1:alarm
446 | Slave14 Inlet Leakage Current Status | RO | 2 bytes | 0:normal; 1:alarm
447 | Slave15 Inlet Leakage Current Status | RO | 2 bytes | 0:normal; 1:alarm
448 | Master Inlet Power Share Status | RO | 2 bytes | 0:invalid; 1:Inactive | 2:Active/Backup Power | 3:Active/Main Power
449 | Slave01 Inlet Power Share Status | RO | 2 bytes | 0:invalid; 1:Inactive | 2:Active/Backup Power | 3:Active/Main Power
450 | Slave02 Inlet Power Share Status | RO | 2 bytes | 0:invalid; 1:Inactive | 2:Active/Backup Power | 3:Active/Main Power
451 | Slave03 Inlet Power Share Status | RO | 2 bytes | 0:invalid; 1:Inactive | 2:Active/Backup Power | 3:Active/Main Power
452 | Slave04 Inlet Power Share Status | RO | 2 bytes | 0:invalid; 1:Inactive | 2:Active/Backup Power | 3:Active/Main Power
453 | Slave05 Inlet Power Share Status | RO | 2 bytes | 0:invalid; 1:Inactive | 2:Active/Backup Power | 3:Active/Main Power
454 | Slave06 Inlet Power Share Status | RO | 2 bytes | 0:invalid; 1:Inactive | 2:Active/Backup Power | 3:Active/Main Power
455 | Slave07 Inlet Power Share Status | RO | 2 bytes | 0:invalid; 1:Inactive | 2:Active/Backup Power | 3:Active/Main Power
456 | Slave08 Inlet Power Share Status | RO | 2 bytes | 0:invalid; 1:Inactive | 2:Active/Backup Power | 3:Active/Main Power
457 | Slave09 Inlet Power Share Status | RO | 2 bytes | 0:invalid; 1:Inactive | 2:Active/Backup Power | 3:Active/Main Power
458 | Slave10 Inlet Power Share Status | RO | 2 bytes | 0:invalid; 1:Inactive | 2:Active/Backup Power | 3:Active/Main Power
459 | Slave11 Inlet Power Share Status | RO | 2 bytes | 0:invalid; 1:Inactive | 2:Active/Backup Power | 3:Active/Main Power
460 | Slave12 Inlet Power Share Status | RO | 2 bytes | 0:invalid; 1:Inactive | 2:Active/Backup Power | 3:Active/Main Power
461 | Slave13 Inlet Power Share Status | RO | 2 bytes | 0:invalid; 1:Inactive | 2:Active/Backup Power | 3:Active/Main Power
462 | Slave14 Inlet Power Share Status | RO | 2 bytes | 0:invalid; 1:Inactive | 2:Active/Backup Power | 3:Active/Main Power
463 | Slave15 Inlet Power Share Status | RO | 2 bytes | 0:invalid; 1:Inactive | 2:Active/Backup Power | 3:Active/Main Power
464 | Master Outlet Port01 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
465 | Master Outlet Port02 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
466 | Master Outlet Port03 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
467 | Master Outlet Port04 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
468 | Master Outlet Port05 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
469 | Master Outlet Port06 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
470 | Master Outlet Port07 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
471 | Master Outlet Port08 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
472 | Master Outlet Port09 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
473 | Master Outlet Port10 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
474 | Master Outlet Port11 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
475 | Master Outlet Port12 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
476 | Master Outlet Port13 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
477 | Master Outlet Port14 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
478 | Master Outlet Port15 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
479 | Master Outlet Port16 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
480 | Master Outlet Port17 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
481 | Master Outlet Port18 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
482 | Master Outlet Port19 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
483 | Master Outlet Port20 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
484 | Master Outlet Port21 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
485 | Master Outlet Port22 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
486 | Master Outlet Port23 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
487 | Master Outlet Port24 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
488 | Master Outlet Port25 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
489 | Master Outlet Port26 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
490 | Master Outlet Port27 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
491 | Master Outlet Port28 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
492 | Master Outlet Port29 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
493 | Master Outlet Port30 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
494 | Master Outlet Port31 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
495 | Master Outlet Port32 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
496 | Master Outlet Port33 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
497 | Master Outlet Port34 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
498 | Master Outlet Port35 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
499 | Master Outlet Port36 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
500 | Master Outlet Port37 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
501 | Master Outlet Port38 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
502 | Master Outlet Port39 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
503 | Master Outlet Port40 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
504 | Master Outlet Port41 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
505 | Master Outlet Port42 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
506 | Slave01 Outlet Port01 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
507 | Slave01 Outlet Port02 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
508 | Slave01 Outlet Port03 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
509 | Slave01 Outlet Port04 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
510 | Slave01 Outlet Port05 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
511 | Slave01 Outlet Port06 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
512 | Slave01 Outlet Port07 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
513 | Slave01 Outlet Port08 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
514 | Slave01 Outlet Port09 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
515 | Slave01 Outlet Port10 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
516 | Slave01 Outlet Port11 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
517 | Slave01 Outlet Port12 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
518 | Slave01 Outlet Port13 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
519 | Slave01 Outlet Port14 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
520 | Slave01 Outlet Port15 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
521 | Slave01 Outlet Port16 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
522 | Slave01 Outlet Port17 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
523 | Slave01 Outlet Port18 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
524 | Slave01 Outlet Port19 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
525 | Slave01 Outlet Port20 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
526 | Slave01 Outlet Port21 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
527 | Slave01 Outlet Port22 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
528 | Slave01 Outlet Port23 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
529 | Slave01 Outlet Port24 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
530 | Slave01 Outlet Port25 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
531 | Slave01 Outlet Port26 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
532 | Slave01 Outlet Port27 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
533 | Slave01 Outlet Port28 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
534 | Slave01 Outlet Port29 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
535 | Slave01 Outlet Port30 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
536 | Slave01 Outlet Port31 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
537 | Slave01 Outlet Port32 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
538 | Slave01 Outlet Port33 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
539 | Slave01 Outlet Port34 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
540 | Slave01 Outlet Port35 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
541 | Slave01 Outlet Port36 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
542 | Slave01 Outlet Port37 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
543 | Slave01 Outlet Port38 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
544 | Slave01 Outlet Port39 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
545 | Slave01 Outlet Port40 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
546 | Slave01 Outlet Port41 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
547 | Slave01 Outlet Port42 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
548 | Slave02 Outlet Port01 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
549 | Slave02 Outlet Port02 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
550 | Slave02 Outlet Port03 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
551 | Slave02 Outlet Port04 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
552 | Slave02 Outlet Port05 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
553 | Slave02 Outlet Port06 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
554 | Slave02 Outlet Port07 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
555 | Slave02 Outlet Port08 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
556 | Slave02 Outlet Port09 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
557 | Slave02 Outlet Port10 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
558 | Slave02 Outlet Port11 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
559 | Slave02 Outlet Port12 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
560 | Slave02 Outlet Port13 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
561 | Slave02 Outlet Port14 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
562 | Slave02 Outlet Port15 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
563 | Slave02 Outlet Port16 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
564 | Slave02 Outlet Port17 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
565 | Slave02 Outlet Port18 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
566 | Slave02 Outlet Port19 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
567 | Slave02 Outlet Port20 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
568 | Slave02 Outlet Port21 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
569 | Slave02 Outlet Port22 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
570 | Slave02 Outlet Port23 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
571 | Slave02 Outlet Port24 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
572 | Slave02 Outlet Port25 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
573 | Slave02 Outlet Port26 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
574 | Slave02 Outlet Port27 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
575 | Slave02 Outlet Port28 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
576 | Slave02 Outlet Port29 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
577 | Slave02 Outlet Port30 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
578 | Slave02 Outlet Port31 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
579 | Slave02 Outlet Port32 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
580 | Slave02 Outlet Port33 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
581 | Slave02 Outlet Port34 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
582 | Slave02 Outlet Port35 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
583 | Slave02 Outlet Port36 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
584 | Slave02 Outlet Port37 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
585 | Slave02 Outlet Port38 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
586 | Slave02 Outlet Port39 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
587 | Slave02 Outlet Port40 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
588 | Slave02 Outlet Port41 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
589 | Slave02 Outlet Port42 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
590 | Slave03 Outlet Port01 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
591 | Slave03 Outlet Port02 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
592 | Slave03 Outlet Port03 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
593 | Slave03 Outlet Port04 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
594 | Slave03 Outlet Port05 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
595 | Slave03 Outlet Port06 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
596 | Slave03 Outlet Port07 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
597 | Slave03 Outlet Port08 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
598 | Slave03 Outlet Port09 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
599 | Slave03 Outlet Port10 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
600 | Slave03 Outlet Port11 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
601 | Slave03 Outlet Port12 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
602 | Slave03 Outlet Port13 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
603 | Slave03 Outlet Port14 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
604 | Slave03 Outlet Port15 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
605 | Slave03 Outlet Port16 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
606 | Slave03 Outlet Port17 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
607 | Slave03 Outlet Port18 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
608 | Slave03 Outlet Port19 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
609 | Slave03 Outlet Port20 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
610 | Slave03 Outlet Port21 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
611 | Slave03 Outlet Port22 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
612 | Slave03 Outlet Port23 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
613 | Slave03 Outlet Port24 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
614 | Slave03 Outlet Port25 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
615 | Slave03 Outlet Port26 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
616 | Slave03 Outlet Port27 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
617 | Slave03 Outlet Port28 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
618 | Slave03 Outlet Port29 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
619 | Slave03 Outlet Port30 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
620 | Slave03 Outlet Port31 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
621 | Slave03 Outlet Port32 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
622 | Slave03 Outlet Port33 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
623 | Slave03 Outlet Port34 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
624 | Slave03 Outlet Port35 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
625 | Slave03 Outlet Port36 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
626 | Slave03 Outlet Port37 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
627 | Slave03 Outlet Port38 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
628 | Slave03 Outlet Port39 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
629 | Slave03 Outlet Port40 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
630 | Slave03 Outlet Port41 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
631 | Slave03 Outlet Port42 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
632 | Slave04 Outlet Port01 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
633 | Slave04 Outlet Port02 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
634 | Slave04 Outlet Port03 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
635 | Slave04 Outlet Port04 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
636 | Slave04 Outlet Port05 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
637 | Slave04 Outlet Port06 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
638 | Slave04 Outlet Port07 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
639 | Slave04 Outlet Port08 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
640 | Slave04 Outlet Port09 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
641 | Slave04 Outlet Port10 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
642 | Slave04 Outlet Port11 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
643 | Slave04 Outlet Port12 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
644 | Slave04 Outlet Port13 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
645 | Slave04 Outlet Port14 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
646 | Slave04 Outlet Port15 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
647 | Slave04 Outlet Port16 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
648 | Slave04 Outlet Port17 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
649 | Slave04 Outlet Port18 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
650 | Slave04 Outlet Port19 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
651 | Slave04 Outlet Port20 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
652 | Slave04 Outlet Port21 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
653 | Slave04 Outlet Port22 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
654 | Slave04 Outlet Port23 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
655 | Slave04 Outlet Port24 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
656 | Slave04 Outlet Port25 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
657 | Slave04 Outlet Port26 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
658 | Slave04 Outlet Port27 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
659 | Slave04 Outlet Port28 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
660 | Slave04 Outlet Port29 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
661 | Slave04 Outlet Port30 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
662 | Slave04 Outlet Port31 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
663 | Slave04 Outlet Port32 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
664 | Slave04 Outlet Port33 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
665 | Slave04 Outlet Port34 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
666 | Slave04 Outlet Port35 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
667 | Slave04 Outlet Port36 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
668 | Slave04 Outlet Port37 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
669 | Slave04 Outlet Port38 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
670 | Slave04 Outlet Port39 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
671 | Slave04 Outlet Port40 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
672 | Slave04 Outlet Port41 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
673 | Slave04 Outlet Port42 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
674 | Slave05 Outlet Port01 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
675 | Slave05 Outlet Port02 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
676 | Slave05 Outlet Port03 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
677 | Slave05 Outlet Port04 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
678 | Slave05 Outlet Port05 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
679 | Slave05 Outlet Port06 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
680 | Slave05 Outlet Port07 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
681 | Slave05 Outlet Port08 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
682 | Slave05 Outlet Port09 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
683 | Slave05 Outlet Port10 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
684 | Slave05 Outlet Port11 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
685 | Slave05 Outlet Port12 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
686 | Slave05 Outlet Port13 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
687 | Slave05 Outlet Port14 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
688 | Slave05 Outlet Port15 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
689 | Slave05 Outlet Port16 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
690 | Slave05 Outlet Port17 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
691 | Slave05 Outlet Port18 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
692 | Slave05 Outlet Port19 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
693 | Slave05 Outlet Port20 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
694 | Slave05 Outlet Port21 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
695 | Slave05 Outlet Port22 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
696 | Slave05 Outlet Port23 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
697 | Slave05 Outlet Port24 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
698 | Slave05 Outlet Port25 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
699 | Slave05 Outlet Port26 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
700 | Slave05 Outlet Port27 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
701 | Slave05 Outlet Port28 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
702 | Slave05 Outlet Port29 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
703 | Slave05 Outlet Port30 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
704 | Slave05 Outlet Port31 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
705 | Slave05 Outlet Port32 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
706 | Slave05 Outlet Port33 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
707 | Slave05 Outlet Port34 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
708 | Slave05 Outlet Port35 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
709 | Slave05 Outlet Port36 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
710 | Slave05 Outlet Port37 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
711 | Slave05 Outlet Port38 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
712 | Slave05 Outlet Port39 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
713 | Slave05 Outlet Port40 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
714 | Slave05 Outlet Port41 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
715 | Slave05 Outlet Port42 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
716 | Slave06 Outlet Port01 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
717 | Slave06 Outlet Port02 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
718 | Slave06 Outlet Port03 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
719 | Slave06 Outlet Port04 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
720 | Slave06 Outlet Port05 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
721 | Slave06 Outlet Port06 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
722 | Slave06 Outlet Port07 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
723 | Slave06 Outlet Port08 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
724 | Slave06 Outlet Port09 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
725 | Slave06 Outlet Port10 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
726 | Slave06 Outlet Port11 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
727 | Slave06 Outlet Port12 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
728 | Slave06 Outlet Port13 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
729 | Slave06 Outlet Port14 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
730 | Slave06 Outlet Port15 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
731 | Slave06 Outlet Port16 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
732 | Slave06 Outlet Port17 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
733 | Slave06 Outlet Port18 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
734 | Slave06 Outlet Port19 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
735 | Slave06 Outlet Port20 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
736 | Slave06 Outlet Port21 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
737 | Slave06 Outlet Port22 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
738 | Slave06 Outlet Port23 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
739 | Slave06 Outlet Port24 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
740 | Slave06 Outlet Port25 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
741 | Slave06 Outlet Port26 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
742 | Slave06 Outlet Port27 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
743 | Slave06 Outlet Port28 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
744 | Slave06 Outlet Port29 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
745 | Slave06 Outlet Port30 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
746 | Slave06 Outlet Port31 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
747 | Slave06 Outlet Port32 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
748 | Slave06 Outlet Port33 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
749 | Slave06 Outlet Port34 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
750 | Slave06 Outlet Port35 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
751 | Slave06 Outlet Port36 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
752 | Slave06 Outlet Port37 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
753 | Slave06 Outlet Port38 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
754 | Slave06 Outlet Port39 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
755 | Slave06 Outlet Port40 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
756 | Slave06 Outlet Port41 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
757 | Slave06 Outlet Port42 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
758 | Slave07 Outlet Port01 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
759 | Slave07 Outlet Port02 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
760 | Slave07 Outlet Port03 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
761 | Slave07 Outlet Port04 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
762 | Slave07 Outlet Port05 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
763 | Slave07 Outlet Port06 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
764 | Slave07 Outlet Port07 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
765 | Slave07 Outlet Port08 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
766 | Slave07 Outlet Port09 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
767 | Slave07 Outlet Port10 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
768 | Slave07 Outlet Port11 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
769 | Slave07 Outlet Port12 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
770 | Slave07 Outlet Port13 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
771 | Slave07 Outlet Port14 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
772 | Slave07 Outlet Port15 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
773 | Slave07 Outlet Port16 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
774 | Slave07 Outlet Port17 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
775 | Slave07 Outlet Port18 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
776 | Slave07 Outlet Port19 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
777 | Slave07 Outlet Port20 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
778 | Slave07 Outlet Port21 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
779 | Slave07 Outlet Port22 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
780 | Slave07 Outlet Port23 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
781 | Slave07 Outlet Port24 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
782 | Slave07 Outlet Port25 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
783 | Slave07 Outlet Port26 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
784 | Slave07 Outlet Port27 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
785 | Slave07 Outlet Port28 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
786 | Slave07 Outlet Port29 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
787 | Slave07 Outlet Port30 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
788 | Slave07 Outlet Port31 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
789 | Slave07 Outlet Port32 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
790 | Slave07 Outlet Port33 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
791 | Slave07 Outlet Port34 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
792 | Slave07 Outlet Port35 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
793 | Slave07 Outlet Port36 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
794 | Slave07 Outlet Port37 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
795 | Slave07 Outlet Port38 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
796 | Slave07 Outlet Port39 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
797 | Slave07 Outlet Port40 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
798 | Slave07 Outlet Port41 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
799 | Slave07 Outlet Port42 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
800 | Slave08 Outlet Port01 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
801 | Slave08 Outlet Port02 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
802 | Slave08 Outlet Port03 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
803 | Slave08 Outlet Port04 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
804 | Slave08 Outlet Port05 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
805 | Slave08 Outlet Port06 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
806 | Slave08 Outlet Port07 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
807 | Slave08 Outlet Port08 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
808 | Slave08 Outlet Port09 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
809 | Slave08 Outlet Port10 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
810 | Slave08 Outlet Port11 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
811 | Slave08 Outlet Port12 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
812 | Slave08 Outlet Port13 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
813 | Slave08 Outlet Port14 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
814 | Slave08 Outlet Port15 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
815 | Slave08 Outlet Port16 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
816 | Slave08 Outlet Port17 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
817 | Slave08 Outlet Port18 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
818 | Slave08 Outlet Port19 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
819 | Slave08 Outlet Port20 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
820 | Slave08 Outlet Port21 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
821 | Slave08 Outlet Port22 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
822 | Slave08 Outlet Port23 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
823 | Slave08 Outlet Port24 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
824 | Slave08 Outlet Port25 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
825 | Slave08 Outlet Port26 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
826 | Slave08 Outlet Port27 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
827 | Slave08 Outlet Port28 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
828 | Slave08 Outlet Port29 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
829 | Slave08 Outlet Port30 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
830 | Slave08 Outlet Port31 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
831 | Slave08 Outlet Port32 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
832 | Slave08 Outlet Port33 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
833 | Slave08 Outlet Port34 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
834 | Slave08 Outlet Port35 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
835 | Slave08 Outlet Port36 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
836 | Slave08 Outlet Port37 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
837 | Slave08 Outlet Port38 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
838 | Slave08 Outlet Port39 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
839 | Slave08 Outlet Port40 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
840 | Slave08 Outlet Port41 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
841 | Slave08 Outlet Port42 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
842 | Slave09 Outlet Port01 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
843 | Slave09 Outlet Port02 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
844 | Slave09 Outlet Port03 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
845 | Slave09 Outlet Port04 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
846 | Slave09 Outlet Port05 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
847 | Slave09 Outlet Port06 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
848 | Slave09 Outlet Port07 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
849 | Slave09 Outlet Port08 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
850 | Slave09 Outlet Port09 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
851 | Slave09 Outlet Port10 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
852 | Slave09 Outlet Port11 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
853 | Slave09 Outlet Port12 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
854 | Slave09 Outlet Port13 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
855 | Slave09 Outlet Port14 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
856 | Slave09 Outlet Port15 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
857 | Slave09 Outlet Port16 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
858 | Slave09 Outlet Port17 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
859 | Slave09 Outlet Port18 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
860 | Slave09 Outlet Port19 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
861 | Slave09 Outlet Port20 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
862 | Slave09 Outlet Port21 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
863 | Slave09 Outlet Port22 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
864 | Slave09 Outlet Port23 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
865 | Slave09 Outlet Port24 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
866 | Slave09 Outlet Port25 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
867 | Slave09 Outlet Port26 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
868 | Slave09 Outlet Port27 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
869 | Slave09 Outlet Port28 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
870 | Slave09 Outlet Port29 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
871 | Slave09 Outlet Port30 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
872 | Slave09 Outlet Port31 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
873 | Slave09 Outlet Port32 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
874 | Slave09 Outlet Port33 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
875 | Slave09 Outlet Port34 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
876 | Slave09 Outlet Port35 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
877 | Slave09 Outlet Port36 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
878 | Slave09 Outlet Port37 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
879 | Slave09 Outlet Port38 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
880 | Slave09 Outlet Port39 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
881 | Slave09 Outlet Port40 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
882 | Slave09 Outlet Port41 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
883 | Slave09 Outlet Port42 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
884 | Slave10 Outlet Port01 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
885 | Slave10 Outlet Port02 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
886 | Slave10 Outlet Port03 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
887 | Slave10 Outlet Port04 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
888 | Slave10 Outlet Port05 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
889 | Slave10 Outlet Port06 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
890 | Slave10 Outlet Port07 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
891 | Slave10 Outlet Port08 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
892 | Slave10 Outlet Port09 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
893 | Slave10 Outlet Port10 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
894 | Slave10 Outlet Port11 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
895 | Slave10 Outlet Port12 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
896 | Slave10 Outlet Port13 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
897 | Slave10 Outlet Port14 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
898 | Slave10 Outlet Port15 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
899 | Slave10 Outlet Port16 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
900 | Slave10 Outlet Port17 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
901 | Slave10 Outlet Port18 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
902 | Slave10 Outlet Port19 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
903 | Slave10 Outlet Port20 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
904 | Slave10 Outlet Port21 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
905 | Slave10 Outlet Port22 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
906 | Slave10 Outlet Port23 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
907 | Slave10 Outlet Port24 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
908 | Slave10 Outlet Port25 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
909 | Slave10 Outlet Port26 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
910 | Slave10 Outlet Port27 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
911 | Slave10 Outlet Port28 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
912 | Slave10 Outlet Port29 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
913 | Slave10 Outlet Port30 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
914 | Slave10 Outlet Port31 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
915 | Slave10 Outlet Port32 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
916 | Slave10 Outlet Port33 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
917 | Slave10 Outlet Port34 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
918 | Slave10 Outlet Port35 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
919 | Slave10 Outlet Port36 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
920 | Slave10 Outlet Port37 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
921 | Slave10 Outlet Port38 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
922 | Slave10 Outlet Port39 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
923 | Slave10 Outlet Port40 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
924 | Slave10 Outlet Port41 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
925 | Slave10 Outlet Port42 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
926 | Slave11 Outlet Port01 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
927 | Slave11 Outlet Port02 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
928 | Slave11 Outlet Port03 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
929 | Slave11 Outlet Port04 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
930 | Slave11 Outlet Port05 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
931 | Slave11 Outlet Port06 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
932 | Slave11 Outlet Port07 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
933 | Slave11 Outlet Port08 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
934 | Slave11 Outlet Port09 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
935 | Slave11 Outlet Port10 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
936 | Slave11 Outlet Port11 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
937 | Slave11 Outlet Port12 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
938 | Slave11 Outlet Port13 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
939 | Slave11 Outlet Port14 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
940 | Slave11 Outlet Port15 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
941 | Slave11 Outlet Port16 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
942 | Slave11 Outlet Port17 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
943 | Slave11 Outlet Port18 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
944 | Slave11 Outlet Port19 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
945 | Slave11 Outlet Port20 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
946 | Slave11 Outlet Port21 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
947 | Slave11 Outlet Port22 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
948 | Slave11 Outlet Port23 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
949 | Slave11 Outlet Port24 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
950 | Slave11 Outlet Port25 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
951 | Slave11 Outlet Port26 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
952 | Slave11 Outlet Port27 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
953 | Slave11 Outlet Port28 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
954 | Slave11 Outlet Port29 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
955 | Slave11 Outlet Port30 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
956 | Slave11 Outlet Port31 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
957 | Slave11 Outlet Port32 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
958 | Slave11 Outlet Port33 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
959 | Slave11 Outlet Port34 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
960 | Slave11 Outlet Port35 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
961 | Slave11 Outlet Port36 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
962 | Slave11 Outlet Port37 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
963 | Slave11 Outlet Port38 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
964 | Slave11 Outlet Port39 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
965 | Slave11 Outlet Port40 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
966 | Slave11 Outlet Port41 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
967 | Slave11 Outlet Port42 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
968 | Slave12 Outlet Port01 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
969 | Slave12 Outlet Port02 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
970 | Slave12 Outlet Port03 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
971 | Slave12 Outlet Port04 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
972 | Slave12 Outlet Port05 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
973 | Slave12 Outlet Port06 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
974 | Slave12 Outlet Port07 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
975 | Slave12 Outlet Port08 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
976 | Slave12 Outlet Port09 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
977 | Slave12 Outlet Port10 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
978 | Slave12 Outlet Port11 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
979 | Slave12 Outlet Port12 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
980 | Slave12 Outlet Port13 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
981 | Slave12 Outlet Port14 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
982 | Slave12 Outlet Port15 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
983 | Slave12 Outlet Port16 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
984 | Slave12 Outlet Port17 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
985 | Slave12 Outlet Port18 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
986 | Slave12 Outlet Port19 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
987 | Slave12 Outlet Port20 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
988 | Slave12 Outlet Port21 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
989 | Slave12 Outlet Port22 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
990 | Slave12 Outlet Port23 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
991 | Slave12 Outlet Port24 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
992 | Slave12 Outlet Port25 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
993 | Slave12 Outlet Port26 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
994 | Slave12 Outlet Port27 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
995 | Slave12 Outlet Port28 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
996 | Slave12 Outlet Port29 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
997 | Slave12 Outlet Port30 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
998 | Slave12 Outlet Port31 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
999 | Slave12 Outlet Port32 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1000 | Slave12 Outlet Port33 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1001 | Slave12 Outlet Port34 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1002 | Slave12 Outlet Port35 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1003 | Slave12 Outlet Port36 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1004 | Slave12 Outlet Port37 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1005 | Slave12 Outlet Port38 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1006 | Slave12 Outlet Port39 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1007 | Slave12 Outlet Port40 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1008 | Slave12 Outlet Port41 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1009 | Slave12 Outlet Port42 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1010 | Slave13 Outlet Port01 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1011 | Slave13 Outlet Port02 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1012 | Slave13 Outlet Port03 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1013 | Slave13 Outlet Port04 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1014 | Slave13 Outlet Port05 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1015 | Slave13 Outlet Port06 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1016 | Slave13 Outlet Port07 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1017 | Slave13 Outlet Port08 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1018 | Slave13 Outlet Port09 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1019 | Slave13 Outlet Port10 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1020 | Slave13 Outlet Port11 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1021 | Slave13 Outlet Port12 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1022 | Slave13 Outlet Port13 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1023 | Slave13 Outlet Port14 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1024 | Slave13 Outlet Port15 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1025 | Slave13 Outlet Port16 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1026 | Slave13 Outlet Port17 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1027 | Slave13 Outlet Port18 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1028 | Slave13 Outlet Port19 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1029 | Slave13 Outlet Port20 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1030 | Slave13 Outlet Port21 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1031 | Slave13 Outlet Port22 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1032 | Slave13 Outlet Port23 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1033 | Slave13 Outlet Port24 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1034 | Slave13 Outlet Port25 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1035 | Slave13 Outlet Port26 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1036 | Slave13 Outlet Port27 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1037 | Slave13 Outlet Port28 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1038 | Slave13 Outlet Port29 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1039 | Slave13 Outlet Port30 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1040 | Slave13 Outlet Port31 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1041 | Slave13 Outlet Port32 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1042 | Slave13 Outlet Port33 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1043 | Slave13 Outlet Port34 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1044 | Slave13 Outlet Port35 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1045 | Slave13 Outlet Port36 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1046 | Slave13 Outlet Port37 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1047 | Slave13 Outlet Port38 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1048 | Slave13 Outlet Port39 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1049 | Slave13 Outlet Port40 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1050 | Slave13 Outlet Port41 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1051 | Slave13 Outlet Port42 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1052 | Slave14 Outlet Port01 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1053 | Slave14 Outlet Port02 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1054 | Slave14 Outlet Port03 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1055 | Slave14 Outlet Port04 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1056 | Slave14 Outlet Port05 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1057 | Slave14 Outlet Port06 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1058 | Slave14 Outlet Port07 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1059 | Slave14 Outlet Port08 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1060 | Slave14 Outlet Port09 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1061 | Slave14 Outlet Port10 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1062 | Slave14 Outlet Port11 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1063 | Slave14 Outlet Port12 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1064 | Slave14 Outlet Port13 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1065 | Slave14 Outlet Port14 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1066 | Slave14 Outlet Port15 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1067 | Slave14 Outlet Port16 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1068 | Slave14 Outlet Port17 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1069 | Slave14 Outlet Port18 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1070 | Slave14 Outlet Port19 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1071 | Slave14 Outlet Port20 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1072 | Slave14 Outlet Port21 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1073 | Slave14 Outlet Port22 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1074 | Slave14 Outlet Port23 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1075 | Slave14 Outlet Port24 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1076 | Slave14 Outlet Port25 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1077 | Slave14 Outlet Port26 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1078 | Slave14 Outlet Port27 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1079 | Slave14 Outlet Port28 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1080 | Slave14 Outlet Port29 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1081 | Slave14 Outlet Port30 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1082 | Slave14 Outlet Port31 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1083 | Slave14 Outlet Port32 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1084 | Slave14 Outlet Port33 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1085 | Slave14 Outlet Port34 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1086 | Slave14 Outlet Port35 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1087 | Slave14 Outlet Port36 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1088 | Slave14 Outlet Port37 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1089 | Slave14 Outlet Port38 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1090 | Slave14 Outlet Port39 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1091 | Slave14 Outlet Port40 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1092 | Slave14 Outlet Port41 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1093 | Slave14 Outlet Port42 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1094 | Slave15 Outlet Port01 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1095 | Slave15 Outlet Port02 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1096 | Slave15 Outlet Port03 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1097 | Slave15 Outlet Port04 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1098 | Slave15 Outlet Port05 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1099 | Slave15 Outlet Port06 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1100 | Slave15 Outlet Port07 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1101 | Slave15 Outlet Port08 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1102 | Slave15 Outlet Port09 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1103 | Slave15 Outlet Port10 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1104 | Slave15 Outlet Port11 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1105 | Slave15 Outlet Port12 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1106 | Slave15 Outlet Port13 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1107 | Slave15 Outlet Port14 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1108 | Slave15 Outlet Port15 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1109 | Slave15 Outlet Port16 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1110 | Slave15 Outlet Port17 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1111 | Slave15 Outlet Port18 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1112 | Slave15 Outlet Port19 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1113 | Slave15 Outlet Port20 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1114 | Slave15 Outlet Port21 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1115 | Slave15 Outlet Port22 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1116 | Slave15 Outlet Port23 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1117 | Slave15 Outlet Port24 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1118 | Slave15 Outlet Port25 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1119 | Slave15 Outlet Port26 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1120 | Slave15 Outlet Port27 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1121 | Slave15 Outlet Port28 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1122 | Slave15 Outlet Port29 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1123 | Slave15 Outlet Port30 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1124 | Slave15 Outlet Port31 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1125 | Slave15 Outlet Port32 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1126 | Slave15 Outlet Port33 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1127 | Slave15 Outlet Port34 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1128 | Slave15 Outlet Port35 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1129 | Slave15 Outlet Port36 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1130 | Slave15 Outlet Port37 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1131 | Slave15 Outlet Port38 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1132 | Slave15 Outlet Port39 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1133 | Slave15 Outlet Port40 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1134 | Slave15 Outlet Port41 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1135 | Slave15 Outlet Port42 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1136 | Master Outlet Port01 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1137 | Master Outlet Port02 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1138 | Master Outlet Port03 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1139 | Master Outlet Port04 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1140 | Master Outlet Port05 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1141 | Master Outlet Port06 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1142 | Master Outlet Port07 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1143 | Master Outlet Port08 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1144 | Master Outlet Port09 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1145 | Master Outlet Port10 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1146 | Master Outlet Port11 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1147 | Master Outlet Port12 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1148 | Master Outlet Port13 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1149 | Master Outlet Port14 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1150 | Master Outlet Port15 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1151 | Master Outlet Port16 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1152 | Master Outlet Port17 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1153 | Master Outlet Port18 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1154 | Master Outlet Port19 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1155 | Master Outlet Port20 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1156 | Master Outlet Port21 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1157 | Master Outlet Port22 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1158 | Master Outlet Port23 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1159 | Master Outlet Port24 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1160 | Master Outlet Port25 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1161 | Master Outlet Port26 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1162 | Master Outlet Port27 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1163 | Master Outlet Port28 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1164 | Master Outlet Port29 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1165 | Master Outlet Port30 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1166 | Master Outlet Port31 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1167 | Master Outlet Port32 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1168 | Master Outlet Port33 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1169 | Master Outlet Port34 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1170 | Master Outlet Port35 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1171 | Master Outlet Port36 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1172 | Master Outlet Port37 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1173 | Master Outlet Port38 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1174 | Master Outlet Port39 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1175 | Master Outlet Port40 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1176 | Master Outlet Port41 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1177 | Master Outlet Port42 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1178 | Slave01 Outlet Port01 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1179 | Slave01 Outlet Port02 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1180 | Slave01 Outlet Port03 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1181 | Slave01 Outlet Port04 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1182 | Slave01 Outlet Port05 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1183 | Slave01 Outlet Port06 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1184 | Slave01 Outlet Port07 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1185 | Slave01 Outlet Port08 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1186 | Slave01 Outlet Port09 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1187 | Slave01 Outlet Port10 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1188 | Slave01 Outlet Port11 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1189 | Slave01 Outlet Port12 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1190 | Slave01 Outlet Port13 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1191 | Slave01 Outlet Port14 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1192 | Slave01 Outlet Port15 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1193 | Slave01 Outlet Port16 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1194 | Slave01 Outlet Port17 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1195 | Slave01 Outlet Port18 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1196 | Slave01 Outlet Port19 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1197 | Slave01 Outlet Port20 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1198 | Slave01 Outlet Port21 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1199 | Slave01 Outlet Port22 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1200 | Slave01 Outlet Port23 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1201 | Slave01 Outlet Port24 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1202 | Slave01 Outlet Port25 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1203 | Slave01 Outlet Port26 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1204 | Slave01 Outlet Port27 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1205 | Slave01 Outlet Port28 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1206 | Slave01 Outlet Port29 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1207 | Slave01 Outlet Port30 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1208 | Slave01 Outlet Port31 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1209 | Slave01 Outlet Port32 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1210 | Slave01 Outlet Port33 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1211 | Slave01 Outlet Port34 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1212 | Slave01 Outlet Port35 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1213 | Slave01 Outlet Port36 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1214 | Slave01 Outlet Port37 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1215 | Slave01 Outlet Port38 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1216 | Slave01 Outlet Port39 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1217 | Slave01 Outlet Port40 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1218 | Slave01 Outlet Port41 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1219 | Slave01 Outlet Port42 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1220 | Slave02 Outlet Port01 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1221 | Slave02 Outlet Port02 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1222 | Slave02 Outlet Port03 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1223 | Slave02 Outlet Port04 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1224 | Slave02 Outlet Port05 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1225 | Slave02 Outlet Port06 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1226 | Slave02 Outlet Port07 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1227 | Slave02 Outlet Port08 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1228 | Slave02 Outlet Port09 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1229 | Slave02 Outlet Port10 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1230 | Slave02 Outlet Port11 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1231 | Slave02 Outlet Port12 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1232 | Slave02 Outlet Port13 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1233 | Slave02 Outlet Port14 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1234 | Slave02 Outlet Port15 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1235 | Slave02 Outlet Port16 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1236 | Slave02 Outlet Port17 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1237 | Slave02 Outlet Port18 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1238 | Slave02 Outlet Port19 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1239 | Slave02 Outlet Port20 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1240 | Slave02 Outlet Port21 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1241 | Slave02 Outlet Port22 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1242 | Slave02 Outlet Port23 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1243 | Slave02 Outlet Port24 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1244 | Slave02 Outlet Port25 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1245 | Slave02 Outlet Port26 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1246 | Slave02 Outlet Port27 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1247 | Slave02 Outlet Port28 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1248 | Slave02 Outlet Port29 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1249 | Slave02 Outlet Port30 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1250 | Slave02 Outlet Port31 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1251 | Slave02 Outlet Port32 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1252 | Slave02 Outlet Port33 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1253 | Slave02 Outlet Port34 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1254 | Slave02 Outlet Port35 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1255 | Slave02 Outlet Port36 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1256 | Slave02 Outlet Port37 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1257 | Slave02 Outlet Port38 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1258 | Slave02 Outlet Port39 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1259 | Slave02 Outlet Port40 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1260 | Slave02 Outlet Port41 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1261 | Slave02 Outlet Port42 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1262 | Slave03 Outlet Port01 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1263 | Slave03 Outlet Port02 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1264 | Slave03 Outlet Port03 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1265 | Slave03 Outlet Port04 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1266 | Slave03 Outlet Port05 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1267 | Slave03 Outlet Port06 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1268 | Slave03 Outlet Port07 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1269 | Slave03 Outlet Port08 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1270 | Slave03 Outlet Port09 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1271 | Slave03 Outlet Port10 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1272 | Slave03 Outlet Port11 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1273 | Slave03 Outlet Port12 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1274 | Slave03 Outlet Port13 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1275 | Slave03 Outlet Port14 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1276 | Slave03 Outlet Port15 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1277 | Slave03 Outlet Port16 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1278 | Slave03 Outlet Port17 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1279 | Slave03 Outlet Port18 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1280 | Slave03 Outlet Port19 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1281 | Slave03 Outlet Port20 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1282 | Slave03 Outlet Port21 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1283 | Slave03 Outlet Port22 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1284 | Slave03 Outlet Port23 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1285 | Slave03 Outlet Port24 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1286 | Slave03 Outlet Port25 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1287 | Slave03 Outlet Port26 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1288 | Slave03 Outlet Port27 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1289 | Slave03 Outlet Port28 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1290 | Slave03 Outlet Port29 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1291 | Slave03 Outlet Port30 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1292 | Slave03 Outlet Port31 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1293 | Slave03 Outlet Port32 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1294 | Slave03 Outlet Port33 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1295 | Slave03 Outlet Port34 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1296 | Slave03 Outlet Port35 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1297 | Slave03 Outlet Port36 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1298 | Slave03 Outlet Port37 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1299 | Slave03 Outlet Port38 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1300 | Slave03 Outlet Port39 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1301 | Slave03 Outlet Port40 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1302 | Slave03 Outlet Port41 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1303 | Slave03 Outlet Port42 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1304 | Slave04 Outlet Port01 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1305 | Slave04 Outlet Port02 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1306 | Slave04 Outlet Port03 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1307 | Slave04 Outlet Port04 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1308 | Slave04 Outlet Port05 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1309 | Slave04 Outlet Port06 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1310 | Slave04 Outlet Port07 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1311 | Slave04 Outlet Port08 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1312 | Slave04 Outlet Port09 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1313 | Slave04 Outlet Port10 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1314 | Slave04 Outlet Port11 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1315 | Slave04 Outlet Port12 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1316 | Slave04 Outlet Port13 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1317 | Slave04 Outlet Port14 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1318 | Slave04 Outlet Port15 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1319 | Slave04 Outlet Port16 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1320 | Slave04 Outlet Port17 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1321 | Slave04 Outlet Port18 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1322 | Slave04 Outlet Port19 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1323 | Slave04 Outlet Port20 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1324 | Slave04 Outlet Port21 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1325 | Slave04 Outlet Port22 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1326 | Slave04 Outlet Port23 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1327 | Slave04 Outlet Port24 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1328 | Slave04 Outlet Port25 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1329 | Slave04 Outlet Port26 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1330 | Slave04 Outlet Port27 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1331 | Slave04 Outlet Port28 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1332 | Slave04 Outlet Port29 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1333 | Slave04 Outlet Port30 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1334 | Slave04 Outlet Port31 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1335 | Slave04 Outlet Port32 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1336 | Slave04 Outlet Port33 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1337 | Slave04 Outlet Port34 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1338 | Slave04 Outlet Port35 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1339 | Slave04 Outlet Port36 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1340 | Slave04 Outlet Port37 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1341 | Slave04 Outlet Port38 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1342 | Slave04 Outlet Port39 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1343 | Slave04 Outlet Port40 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1344 | Slave04 Outlet Port41 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1345 | Slave04 Outlet Port42 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1346 | Slave05 Outlet Port01 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1347 | Slave05 Outlet Port02 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1348 | Slave05 Outlet Port03 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1349 | Slave05 Outlet Port04 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1350 | Slave05 Outlet Port05 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1351 | Slave05 Outlet Port06 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1352 | Slave05 Outlet Port07 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1353 | Slave05 Outlet Port08 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1354 | Slave05 Outlet Port09 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1355 | Slave05 Outlet Port10 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1356 | Slave05 Outlet Port11 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1357 | Slave05 Outlet Port12 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1358 | Slave05 Outlet Port13 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1359 | Slave05 Outlet Port14 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1360 | Slave05 Outlet Port15 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1361 | Slave05 Outlet Port16 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1362 | Slave05 Outlet Port17 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1363 | Slave05 Outlet Port18 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1364 | Slave05 Outlet Port19 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1365 | Slave05 Outlet Port20 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1366 | Slave05 Outlet Port21 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1367 | Slave05 Outlet Port22 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1368 | Slave05 Outlet Port23 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1369 | Slave05 Outlet Port24 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1370 | Slave05 Outlet Port25 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1371 | Slave05 Outlet Port26 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1372 | Slave05 Outlet Port27 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1373 | Slave05 Outlet Port28 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1374 | Slave05 Outlet Port29 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1375 | Slave05 Outlet Port30 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1376 | Slave05 Outlet Port31 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1377 | Slave05 Outlet Port32 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1378 | Slave05 Outlet Port33 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1379 | Slave05 Outlet Port34 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1380 | Slave05 Outlet Port35 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1381 | Slave05 Outlet Port36 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1382 | Slave05 Outlet Port37 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1383 | Slave05 Outlet Port38 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1384 | Slave05 Outlet Port39 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1385 | Slave05 Outlet Port40 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1386 | Slave05 Outlet Port41 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1387 | Slave05 Outlet Port42 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1388 | Slave06 Outlet Port01 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1389 | Slave06 Outlet Port02 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1390 | Slave06 Outlet Port03 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1391 | Slave06 Outlet Port04 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1392 | Slave06 Outlet Port05 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1393 | Slave06 Outlet Port06 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1394 | Slave06 Outlet Port07 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1395 | Slave06 Outlet Port08 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1396 | Slave06 Outlet Port09 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1397 | Slave06 Outlet Port10 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1398 | Slave06 Outlet Port11 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1399 | Slave06 Outlet Port12 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1400 | Slave06 Outlet Port13 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1401 | Slave06 Outlet Port14 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1402 | Slave06 Outlet Port15 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1403 | Slave06 Outlet Port16 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1404 | Slave06 Outlet Port17 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1405 | Slave06 Outlet Port18 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1406 | Slave06 Outlet Port19 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1407 | Slave06 Outlet Port20 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1408 | Slave06 Outlet Port21 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1409 | Slave06 Outlet Port22 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1410 | Slave06 Outlet Port23 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1411 | Slave06 Outlet Port24 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1412 | Slave06 Outlet Port25 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1413 | Slave06 Outlet Port26 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1414 | Slave06 Outlet Port27 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1415 | Slave06 Outlet Port28 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1416 | Slave06 Outlet Port29 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1417 | Slave06 Outlet Port30 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1418 | Slave06 Outlet Port31 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1419 | Slave06 Outlet Port32 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1420 | Slave06 Outlet Port33 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1421 | Slave06 Outlet Port34 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1422 | Slave06 Outlet Port35 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1423 | Slave06 Outlet Port36 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1424 | Slave06 Outlet Port37 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1425 | Slave06 Outlet Port38 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1426 | Slave06 Outlet Port39 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1427 | Slave06 Outlet Port40 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1428 | Slave06 Outlet Port41 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1429 | Slave06 Outlet Port42 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1430 | Slave07 Outlet Port01 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1431 | Slave07 Outlet Port02 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1432 | Slave07 Outlet Port03 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1433 | Slave07 Outlet Port04 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1434 | Slave07 Outlet Port05 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1435 | Slave07 Outlet Port06 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1436 | Slave07 Outlet Port07 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1437 | Slave07 Outlet Port08 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1438 | Slave07 Outlet Port09 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1439 | Slave07 Outlet Port10 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1440 | Slave07 Outlet Port11 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1441 | Slave07 Outlet Port12 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1442 | Slave07 Outlet Port13 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1443 | Slave07 Outlet Port14 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1444 | Slave07 Outlet Port15 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1445 | Slave07 Outlet Port16 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1446 | Slave07 Outlet Port17 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1447 | Slave07 Outlet Port18 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1448 | Slave07 Outlet Port19 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1449 | Slave07 Outlet Port20 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1450 | Slave07 Outlet Port21 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1451 | Slave07 Outlet Port22 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1452 | Slave07 Outlet Port23 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1453 | Slave07 Outlet Port24 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1454 | Slave07 Outlet Port25 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1455 | Slave07 Outlet Port26 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1456 | Slave07 Outlet Port27 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1457 | Slave07 Outlet Port28 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1458 | Slave07 Outlet Port29 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1459 | Slave07 Outlet Port30 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1460 | Slave07 Outlet Port31 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1461 | Slave07 Outlet Port32 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1462 | Slave07 Outlet Port33 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1463 | Slave07 Outlet Port34 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1464 | Slave07 Outlet Port35 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1465 | Slave07 Outlet Port36 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1466 | Slave07 Outlet Port37 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1467 | Slave07 Outlet Port38 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1468 | Slave07 Outlet Port39 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1469 | Slave07 Outlet Port40 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1470 | Slave07 Outlet Port41 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1471 | Slave07 Outlet Port42 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1472 | Slave08 Outlet Port01 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1473 | Slave08 Outlet Port02 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1474 | Slave08 Outlet Port03 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1475 | Slave08 Outlet Port04 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1476 | Slave08 Outlet Port05 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1477 | Slave08 Outlet Port06 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1478 | Slave08 Outlet Port07 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1479 | Slave08 Outlet Port08 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1480 | Slave08 Outlet Port09 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1481 | Slave08 Outlet Port10 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1482 | Slave08 Outlet Port11 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1483 | Slave08 Outlet Port12 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1484 | Slave08 Outlet Port13 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1485 | Slave08 Outlet Port14 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1486 | Slave08 Outlet Port15 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1487 | Slave08 Outlet Port16 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1488 | Slave08 Outlet Port17 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1489 | Slave08 Outlet Port18 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1490 | Slave08 Outlet Port19 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1491 | Slave08 Outlet Port20 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1492 | Slave08 Outlet Port21 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1493 | Slave08 Outlet Port22 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1494 | Slave08 Outlet Port23 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1495 | Slave08 Outlet Port24 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1496 | Slave08 Outlet Port25 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1497 | Slave08 Outlet Port26 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1498 | Slave08 Outlet Port27 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1499 | Slave08 Outlet Port28 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1500 | Slave08 Outlet Port29 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1501 | Slave08 Outlet Port30 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1502 | Slave08 Outlet Port31 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1503 | Slave08 Outlet Port32 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1504 | Slave08 Outlet Port33 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1505 | Slave08 Outlet Port34 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1506 | Slave08 Outlet Port35 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1507 | Slave08 Outlet Port36 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1508 | Slave08 Outlet Port37 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1509 | Slave08 Outlet Port38 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1510 | Slave08 Outlet Port39 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1511 | Slave08 Outlet Port40 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1512 | Slave08 Outlet Port41 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1513 | Slave08 Outlet Port42 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1514 | Slave09 Outlet Port01 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1515 | Slave09 Outlet Port02 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1516 | Slave09 Outlet Port03 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1517 | Slave09 Outlet Port04 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1518 | Slave09 Outlet Port05 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1519 | Slave09 Outlet Port06 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1520 | Slave09 Outlet Port07 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1521 | Slave09 Outlet Port08 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1522 | Slave09 Outlet Port09 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1523 | Slave09 Outlet Port10 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1524 | Slave09 Outlet Port11 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1525 | Slave09 Outlet Port12 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1526 | Slave09 Outlet Port13 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1527 | Slave09 Outlet Port14 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1528 | Slave09 Outlet Port15 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1529 | Slave09 Outlet Port16 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1530 | Slave09 Outlet Port17 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1531 | Slave09 Outlet Port18 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1532 | Slave09 Outlet Port19 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1533 | Slave09 Outlet Port20 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1534 | Slave09 Outlet Port21 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1535 | Slave09 Outlet Port22 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1536 | Slave09 Outlet Port23 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1537 | Slave09 Outlet Port24 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1538 | Slave09 Outlet Port25 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1539 | Slave09 Outlet Port26 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1540 | Slave09 Outlet Port27 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1541 | Slave09 Outlet Port28 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1542 | Slave09 Outlet Port29 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1543 | Slave09 Outlet Port30 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1544 | Slave09 Outlet Port31 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1545 | Slave09 Outlet Port32 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1546 | Slave09 Outlet Port33 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1547 | Slave09 Outlet Port34 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1548 | Slave09 Outlet Port35 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1549 | Slave09 Outlet Port36 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1550 | Slave09 Outlet Port37 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1551 | Slave09 Outlet Port38 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1552 | Slave09 Outlet Port39 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1553 | Slave09 Outlet Port40 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1554 | Slave09 Outlet Port41 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1555 | Slave09 Outlet Port42 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1556 | Slave10 Outlet Port01 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1557 | Slave10 Outlet Port02 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1558 | Slave10 Outlet Port03 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1559 | Slave10 Outlet Port04 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1560 | Slave10 Outlet Port05 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1561 | Slave10 Outlet Port06 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1562 | Slave10 Outlet Port07 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1563 | Slave10 Outlet Port08 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1564 | Slave10 Outlet Port09 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1565 | Slave10 Outlet Port10 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1566 | Slave10 Outlet Port11 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1567 | Slave10 Outlet Port12 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1568 | Slave10 Outlet Port13 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1569 | Slave10 Outlet Port14 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1570 | Slave10 Outlet Port15 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1571 | Slave10 Outlet Port16 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1572 | Slave10 Outlet Port17 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1573 | Slave10 Outlet Port18 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1574 | Slave10 Outlet Port19 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1575 | Slave10 Outlet Port20 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1576 | Slave10 Outlet Port21 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1577 | Slave10 Outlet Port22 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1578 | Slave10 Outlet Port23 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1579 | Slave10 Outlet Port24 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1580 | Slave10 Outlet Port25 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1581 | Slave10 Outlet Port26 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1582 | Slave10 Outlet Port27 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1583 | Slave10 Outlet Port28 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1584 | Slave10 Outlet Port29 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1585 | Slave10 Outlet Port30 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1586 | Slave10 Outlet Port31 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1587 | Slave10 Outlet Port32 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1588 | Slave10 Outlet Port33 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1589 | Slave10 Outlet Port34 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1590 | Slave10 Outlet Port35 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1591 | Slave10 Outlet Port36 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1592 | Slave10 Outlet Port37 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1593 | Slave10 Outlet Port38 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1594 | Slave10 Outlet Port39 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1595 | Slave10 Outlet Port40 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1596 | Slave10 Outlet Port41 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1597 | Slave10 Outlet Port42 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1598 | Slave11 Outlet Port01 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1599 | Slave11 Outlet Port02 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1600 | Slave11 Outlet Port03 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1601 | Slave11 Outlet Port04 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1602 | Slave11 Outlet Port05 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1603 | Slave11 Outlet Port06 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1604 | Slave11 Outlet Port07 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1605 | Slave11 Outlet Port08 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1606 | Slave11 Outlet Port09 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1607 | Slave11 Outlet Port10 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1608 | Slave11 Outlet Port11 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1609 | Slave11 Outlet Port12 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1610 | Slave11 Outlet Port13 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1611 | Slave11 Outlet Port14 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1612 | Slave11 Outlet Port15 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1613 | Slave11 Outlet Port16 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1614 | Slave11 Outlet Port17 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1615 | Slave11 Outlet Port18 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1616 | Slave11 Outlet Port19 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1617 | Slave11 Outlet Port20 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1618 | Slave11 Outlet Port21 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1619 | Slave11 Outlet Port22 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1620 | Slave11 Outlet Port23 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1621 | Slave11 Outlet Port24 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1622 | Slave11 Outlet Port25 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1623 | Slave11 Outlet Port26 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1624 | Slave11 Outlet Port27 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1625 | Slave11 Outlet Port28 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1626 | Slave11 Outlet Port29 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1627 | Slave11 Outlet Port30 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1628 | Slave11 Outlet Port31 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1629 | Slave11 Outlet Port32 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1630 | Slave11 Outlet Port33 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1631 | Slave11 Outlet Port34 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1632 | Slave11 Outlet Port35 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1633 | Slave11 Outlet Port36 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1634 | Slave11 Outlet Port37 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1635 | Slave11 Outlet Port38 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1636 | Slave11 Outlet Port39 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1637 | Slave11 Outlet Port40 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1638 | Slave11 Outlet Port41 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1639 | Slave11 Outlet Port42 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1640 | Slave12 Outlet Port01 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1641 | Slave12 Outlet Port02 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1642 | Slave12 Outlet Port03 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1643 | Slave12 Outlet Port04 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1644 | Slave12 Outlet Port05 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1645 | Slave12 Outlet Port06 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1646 | Slave12 Outlet Port07 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1647 | Slave12 Outlet Port08 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1648 | Slave12 Outlet Port09 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1649 | Slave12 Outlet Port10 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1650 | Slave12 Outlet Port11 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1651 | Slave12 Outlet Port12 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1652 | Slave12 Outlet Port13 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1653 | Slave12 Outlet Port14 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1654 | Slave12 Outlet Port15 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1655 | Slave12 Outlet Port16 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1656 | Slave12 Outlet Port17 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1657 | Slave12 Outlet Port18 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1658 | Slave12 Outlet Port19 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1659 | Slave12 Outlet Port20 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1660 | Slave12 Outlet Port21 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1661 | Slave12 Outlet Port22 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1662 | Slave12 Outlet Port23 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1663 | Slave12 Outlet Port24 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1664 | Slave12 Outlet Port25 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1665 | Slave12 Outlet Port26 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1666 | Slave12 Outlet Port27 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1667 | Slave12 Outlet Port28 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1668 | Slave12 Outlet Port29 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1669 | Slave12 Outlet Port30 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1670 | Slave12 Outlet Port31 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1671 | Slave12 Outlet Port32 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1672 | Slave12 Outlet Port33 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1673 | Slave12 Outlet Port34 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1674 | Slave12 Outlet Port35 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1675 | Slave12 Outlet Port36 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1676 | Slave12 Outlet Port37 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1677 | Slave12 Outlet Port38 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1678 | Slave12 Outlet Port39 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1679 | Slave12 Outlet Port40 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1680 | Slave12 Outlet Port41 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1681 | Slave12 Outlet Port42 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1682 | Slave13 Outlet Port01 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1683 | Slave13 Outlet Port02 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1684 | Slave13 Outlet Port03 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1685 | Slave13 Outlet Port04 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1686 | Slave13 Outlet Port05 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1687 | Slave13 Outlet Port06 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1688 | Slave13 Outlet Port07 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1689 | Slave13 Outlet Port08 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1690 | Slave13 Outlet Port09 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1691 | Slave13 Outlet Port10 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1692 | Slave13 Outlet Port11 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1693 | Slave13 Outlet Port12 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1694 | Slave13 Outlet Port13 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1695 | Slave13 Outlet Port14 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1696 | Slave13 Outlet Port15 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1697 | Slave13 Outlet Port16 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1698 | Slave13 Outlet Port17 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1699 | Slave13 Outlet Port18 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1700 | Slave13 Outlet Port19 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1701 | Slave13 Outlet Port20 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1702 | Slave13 Outlet Port21 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1703 | Slave13 Outlet Port22 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1704 | Slave13 Outlet Port23 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1705 | Slave13 Outlet Port24 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1706 | Slave13 Outlet Port25 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1707 | Slave13 Outlet Port26 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1708 | Slave13 Outlet Port27 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1709 | Slave13 Outlet Port28 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1710 | Slave13 Outlet Port29 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1711 | Slave13 Outlet Port30 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1712 | Slave13 Outlet Port31 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1713 | Slave13 Outlet Port32 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1714 | Slave13 Outlet Port33 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1715 | Slave13 Outlet Port34 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1716 | Slave13 Outlet Port35 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1717 | Slave13 Outlet Port36 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1718 | Slave13 Outlet Port37 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1719 | Slave13 Outlet Port38 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1720 | Slave13 Outlet Port39 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1721 | Slave13 Outlet Port40 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1722 | Slave13 Outlet Port41 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1723 | Slave13 Outlet Port42 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1724 | Slave14 Outlet Port01 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1725 | Slave14 Outlet Port02 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1726 | Slave14 Outlet Port03 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1727 | Slave14 Outlet Port04 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1728 | Slave14 Outlet Port05 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1729 | Slave14 Outlet Port06 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1730 | Slave14 Outlet Port07 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1731 | Slave14 Outlet Port08 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1732 | Slave14 Outlet Port09 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1733 | Slave14 Outlet Port10 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1734 | Slave14 Outlet Port11 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1735 | Slave14 Outlet Port12 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1736 | Slave14 Outlet Port13 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1737 | Slave14 Outlet Port14 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1738 | Slave14 Outlet Port15 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1739 | Slave14 Outlet Port16 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1740 | Slave14 Outlet Port17 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1741 | Slave14 Outlet Port18 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1742 | Slave14 Outlet Port19 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1743 | Slave14 Outlet Port20 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1744 | Slave14 Outlet Port21 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1745 | Slave14 Outlet Port22 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1746 | Slave14 Outlet Port23 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1747 | Slave14 Outlet Port24 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1748 | Slave14 Outlet Port25 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1749 | Slave14 Outlet Port26 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1750 | Slave14 Outlet Port27 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1751 | Slave14 Outlet Port28 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1752 | Slave14 Outlet Port29 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1753 | Slave14 Outlet Port30 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1754 | Slave14 Outlet Port31 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1755 | Slave14 Outlet Port32 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1756 | Slave14 Outlet Port33 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1757 | Slave14 Outlet Port34 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1758 | Slave14 Outlet Port35 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1759 | Slave14 Outlet Port36 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1760 | Slave14 Outlet Port37 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1761 | Slave14 Outlet Port38 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1762 | Slave14 Outlet Port39 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1763 | Slave14 Outlet Port40 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1764 | Slave14 Outlet Port41 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1765 | Slave14 Outlet Port42 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1766 | Slave15 Outlet Port01 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1767 | Slave15 Outlet Port02 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1768 | Slave15 Outlet Port03 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1769 | Slave15 Outlet Port04 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1770 | Slave15 Outlet Port05 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1771 | Slave15 Outlet Port06 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1772 | Slave15 Outlet Port07 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1773 | Slave15 Outlet Port08 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1774 | Slave15 Outlet Port09 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1775 | Slave15 Outlet Port10 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1776 | Slave15 Outlet Port11 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1777 | Slave15 Outlet Port12 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1778 | Slave15 Outlet Port13 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1779 | Slave15 Outlet Port14 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1780 | Slave15 Outlet Port15 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1781 | Slave15 Outlet Port16 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1782 | Slave15 Outlet Port17 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1783 | Slave15 Outlet Port18 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1784 | Slave15 Outlet Port19 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1785 | Slave15 Outlet Port20 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1786 | Slave15 Outlet Port21 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1787 | Slave15 Outlet Port22 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1788 | Slave15 Outlet Port23 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1789 | Slave15 Outlet Port24 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1790 | Slave15 Outlet Port25 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1791 | Slave15 Outlet Port26 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1792 | Slave15 Outlet Port27 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1793 | Slave15 Outlet Port28 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1794 | Slave15 Outlet Port29 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1795 | Slave15 Outlet Port30 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1796 | Slave15 Outlet Port31 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1797 | Slave15 Outlet Port32 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1798 | Slave15 Outlet Port33 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1799 | Slave15 Outlet Port34 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1800 | Slave15 Outlet Port35 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1801 | Slave15 Outlet Port36 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1802 | Slave15 Outlet Port37 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1803 | Slave15 Outlet Port38 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1804 | Slave15 Outlet Port39 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1805 | Slave15 Outlet Port40 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1806 | Slave15 Outlet Port41 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1807 | Slave15 Outlet Port42 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1808 | Master Outlet Port01 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1809 | Master Outlet Port02 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1810 | Master Outlet Port03 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1811 | Master Outlet Port04 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1812 | Master Outlet Port05 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1813 | Master Outlet Port06 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1814 | Master Outlet Port07 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1815 | Master Outlet Port08 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1816 | Master Outlet Port09 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1817 | Master Outlet Port10 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1818 | Master Outlet Port11 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1819 | Master Outlet Port12 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1820 | Master Outlet Port13 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1821 | Master Outlet Port14 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1822 | Master Outlet Port15 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1823 | Master Outlet Port16 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1824 | Master Outlet Port17 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1825 | Master Outlet Port18 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1826 | Master Outlet Port19 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1827 | Master Outlet Port20 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1828 | Master Outlet Port21 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1829 | Master Outlet Port22 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1830 | Master Outlet Port23 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1831 | Master Outlet Port24 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1832 | Master Outlet Port25 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1833 | Master Outlet Port26 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1834 | Master Outlet Port27 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1835 | Master Outlet Port28 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1836 | Master Outlet Port29 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1837 | Master Outlet Port30 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1838 | Master Outlet Port31 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1839 | Master Outlet Port32 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1840 | Master Outlet Port33 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1841 | Master Outlet Port34 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1842 | Master Outlet Port35 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1843 | Master Outlet Port36 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1844 | Master Outlet Port37 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1845 | Master Outlet Port38 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1846 | Master Outlet Port39 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1847 | Master Outlet Port40 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1848 | Master Outlet Port41 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1849 | Master Outlet Port42 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1850 | Slave01 Outlet Port01 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1851 | Slave01 Outlet Port02 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1852 | Slave01 Outlet Port03 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1853 | Slave01 Outlet Port04 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1854 | Slave01 Outlet Port05 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1855 | Slave01 Outlet Port06 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1856 | Slave01 Outlet Port07 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1857 | Slave01 Outlet Port08 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1858 | Slave01 Outlet Port09 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1859 | Slave01 Outlet Port10 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1860 | Slave01 Outlet Port11 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1861 | Slave01 Outlet Port12 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1862 | Slave01 Outlet Port13 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1863 | Slave01 Outlet Port14 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1864 | Slave01 Outlet Port15 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1865 | Slave01 Outlet Port16 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1866 | Slave01 Outlet Port17 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1867 | Slave01 Outlet Port18 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1868 | Slave01 Outlet Port19 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1869 | Slave01 Outlet Port20 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1870 | Slave01 Outlet Port21 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1871 | Slave01 Outlet Port22 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1872 | Slave01 Outlet Port23 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1873 | Slave01 Outlet Port24 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1874 | Slave01 Outlet Port25 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1875 | Slave01 Outlet Port26 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1876 | Slave01 Outlet Port27 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1877 | Slave01 Outlet Port28 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1878 | Slave01 Outlet Port29 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1879 | Slave01 Outlet Port30 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1880 | Slave01 Outlet Port31 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1881 | Slave01 Outlet Port32 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1882 | Slave01 Outlet Port33 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1883 | Slave01 Outlet Port34 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1884 | Slave01 Outlet Port35 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1885 | Slave01 Outlet Port36 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1886 | Slave01 Outlet Port37 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1887 | Slave01 Outlet Port38 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1888 | Slave01 Outlet Port39 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1889 | Slave01 Outlet Port40 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1890 | Slave01 Outlet Port41 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1891 | Slave01 Outlet Port42 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1892 | Slave02 Outlet Port01 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1893 | Slave02 Outlet Port02 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1894 | Slave02 Outlet Port03 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1895 | Slave02 Outlet Port04 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1896 | Slave02 Outlet Port05 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1897 | Slave02 Outlet Port06 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1898 | Slave02 Outlet Port07 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1899 | Slave02 Outlet Port08 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1900 | Slave02 Outlet Port09 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1901 | Slave02 Outlet Port10 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1902 | Slave02 Outlet Port11 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1903 | Slave02 Outlet Port12 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1904 | Slave02 Outlet Port13 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1905 | Slave02 Outlet Port14 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1906 | Slave02 Outlet Port15 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1907 | Slave02 Outlet Port16 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1908 | Slave02 Outlet Port17 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1909 | Slave02 Outlet Port18 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1910 | Slave02 Outlet Port19 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1911 | Slave02 Outlet Port20 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1912 | Slave02 Outlet Port21 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1913 | Slave02 Outlet Port22 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1914 | Slave02 Outlet Port23 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1915 | Slave02 Outlet Port24 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1916 | Slave02 Outlet Port25 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1917 | Slave02 Outlet Port26 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1918 | Slave02 Outlet Port27 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1919 | Slave02 Outlet Port28 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1920 | Slave02 Outlet Port29 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1921 | Slave02 Outlet Port30 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1922 | Slave02 Outlet Port31 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1923 | Slave02 Outlet Port32 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1924 | Slave02 Outlet Port33 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1925 | Slave02 Outlet Port34 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1926 | Slave02 Outlet Port35 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1927 | Slave02 Outlet Port36 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1928 | Slave02 Outlet Port37 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1929 | Slave02 Outlet Port38 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1930 | Slave02 Outlet Port39 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1931 | Slave02 Outlet Port40 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1932 | Slave02 Outlet Port41 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1933 | Slave02 Outlet Port42 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1934 | Slave03 Outlet Port01 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1935 | Slave03 Outlet Port02 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1936 | Slave03 Outlet Port03 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1937 | Slave03 Outlet Port04 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1938 | Slave03 Outlet Port05 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1939 | Slave03 Outlet Port06 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1940 | Slave03 Outlet Port07 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1941 | Slave03 Outlet Port08 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1942 | Slave03 Outlet Port09 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1943 | Slave03 Outlet Port10 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1944 | Slave03 Outlet Port11 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1945 | Slave03 Outlet Port12 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1946 | Slave03 Outlet Port13 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1947 | Slave03 Outlet Port14 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1948 | Slave03 Outlet Port15 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1949 | Slave03 Outlet Port16 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1950 | Slave03 Outlet Port17 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1951 | Slave03 Outlet Port18 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1952 | Slave03 Outlet Port19 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1953 | Slave03 Outlet Port20 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1954 | Slave03 Outlet Port21 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1955 | Slave03 Outlet Port22 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1956 | Slave03 Outlet Port23 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1957 | Slave03 Outlet Port24 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1958 | Slave03 Outlet Port25 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1959 | Slave03 Outlet Port26 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1960 | Slave03 Outlet Port27 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1961 | Slave03 Outlet Port28 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1962 | Slave03 Outlet Port29 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1963 | Slave03 Outlet Port30 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1964 | Slave03 Outlet Port31 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1965 | Slave03 Outlet Port32 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1966 | Slave03 Outlet Port33 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1967 | Slave03 Outlet Port34 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1968 | Slave03 Outlet Port35 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1969 | Slave03 Outlet Port36 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1970 | Slave03 Outlet Port37 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1971 | Slave03 Outlet Port38 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1972 | Slave03 Outlet Port39 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1973 | Slave03 Outlet Port40 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1974 | Slave03 Outlet Port41 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1975 | Slave03 Outlet Port42 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1976 | Slave04 Outlet Port01 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1977 | Slave04 Outlet Port02 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1978 | Slave04 Outlet Port03 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1979 | Slave04 Outlet Port04 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1980 | Slave04 Outlet Port05 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1981 | Slave04 Outlet Port06 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1982 | Slave04 Outlet Port07 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1983 | Slave04 Outlet Port08 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1984 | Slave04 Outlet Port09 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1985 | Slave04 Outlet Port10 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1986 | Slave04 Outlet Port11 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1987 | Slave04 Outlet Port12 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1988 | Slave04 Outlet Port13 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1989 | Slave04 Outlet Port14 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1990 | Slave04 Outlet Port15 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1991 | Slave04 Outlet Port16 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1992 | Slave04 Outlet Port17 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1993 | Slave04 Outlet Port18 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1994 | Slave04 Outlet Port19 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1995 | Slave04 Outlet Port20 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1996 | Slave04 Outlet Port21 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1997 | Slave04 Outlet Port22 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1998 | Slave04 Outlet Port23 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
1999 | Slave04 Outlet Port24 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2000 | Slave04 Outlet Port25 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2001 | Slave04 Outlet Port26 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2002 | Slave04 Outlet Port27 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2003 | Slave04 Outlet Port28 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2004 | Slave04 Outlet Port29 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2005 | Slave04 Outlet Port30 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2006 | Slave04 Outlet Port31 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2007 | Slave04 Outlet Port32 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2008 | Slave04 Outlet Port33 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2009 | Slave04 Outlet Port34 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2010 | Slave04 Outlet Port35 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2011 | Slave04 Outlet Port36 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2012 | Slave04 Outlet Port37 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2013 | Slave04 Outlet Port38 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2014 | Slave04 Outlet Port39 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2015 | Slave04 Outlet Port40 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2016 | Slave04 Outlet Port41 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2017 | Slave04 Outlet Port42 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2018 | Slave05 Outlet Port01 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2019 | Slave05 Outlet Port02 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2020 | Slave05 Outlet Port03 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2021 | Slave05 Outlet Port04 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2022 | Slave05 Outlet Port05 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2023 | Slave05 Outlet Port06 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2024 | Slave05 Outlet Port07 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2025 | Slave05 Outlet Port08 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2026 | Slave05 Outlet Port09 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2027 | Slave05 Outlet Port10 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2028 | Slave05 Outlet Port11 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2029 | Slave05 Outlet Port12 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2030 | Slave05 Outlet Port13 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2031 | Slave05 Outlet Port14 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2032 | Slave05 Outlet Port15 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2033 | Slave05 Outlet Port16 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2034 | Slave05 Outlet Port17 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2035 | Slave05 Outlet Port18 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2036 | Slave05 Outlet Port19 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2037 | Slave05 Outlet Port20 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2038 | Slave05 Outlet Port21 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2039 | Slave05 Outlet Port22 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2040 | Slave05 Outlet Port23 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2041 | Slave05 Outlet Port24 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2042 | Slave05 Outlet Port25 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2043 | Slave05 Outlet Port26 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2044 | Slave05 Outlet Port27 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2045 | Slave05 Outlet Port28 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2046 | Slave05 Outlet Port29 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2047 | Slave05 Outlet Port30 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2048 | Slave05 Outlet Port31 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2049 | Slave05 Outlet Port32 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2050 | Slave05 Outlet Port33 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2051 | Slave05 Outlet Port34 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2052 | Slave05 Outlet Port35 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2053 | Slave05 Outlet Port36 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2054 | Slave05 Outlet Port37 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2055 | Slave05 Outlet Port38 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2056 | Slave05 Outlet Port39 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2057 | Slave05 Outlet Port40 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2058 | Slave05 Outlet Port41 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2059 | Slave05 Outlet Port42 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2060 | Slave06 Outlet Port01 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2061 | Slave06 Outlet Port02 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2062 | Slave06 Outlet Port03 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2063 | Slave06 Outlet Port04 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2064 | Slave06 Outlet Port05 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2065 | Slave06 Outlet Port06 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2066 | Slave06 Outlet Port07 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2067 | Slave06 Outlet Port08 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2068 | Slave06 Outlet Port09 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2069 | Slave06 Outlet Port10 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2070 | Slave06 Outlet Port11 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2071 | Slave06 Outlet Port12 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2072 | Slave06 Outlet Port13 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2073 | Slave06 Outlet Port14 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2074 | Slave06 Outlet Port15 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2075 | Slave06 Outlet Port16 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2076 | Slave06 Outlet Port17 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2077 | Slave06 Outlet Port18 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2078 | Slave06 Outlet Port19 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2079 | Slave06 Outlet Port20 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2080 | Slave06 Outlet Port21 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2081 | Slave06 Outlet Port22 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2082 | Slave06 Outlet Port23 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2083 | Slave06 Outlet Port24 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2084 | Slave06 Outlet Port25 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2085 | Slave06 Outlet Port26 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2086 | Slave06 Outlet Port27 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2087 | Slave06 Outlet Port28 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2088 | Slave06 Outlet Port29 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2089 | Slave06 Outlet Port30 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2090 | Slave06 Outlet Port31 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2091 | Slave06 Outlet Port32 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2092 | Slave06 Outlet Port33 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2093 | Slave06 Outlet Port34 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2094 | Slave06 Outlet Port35 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2095 | Slave06 Outlet Port36 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2096 | Slave06 Outlet Port37 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2097 | Slave06 Outlet Port38 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2098 | Slave06 Outlet Port39 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2099 | Slave06 Outlet Port40 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2100 | Slave06 Outlet Port41 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2101 | Slave06 Outlet Port42 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2102 | Slave07 Outlet Port01 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2103 | Slave07 Outlet Port02 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2104 | Slave07 Outlet Port03 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2105 | Slave07 Outlet Port04 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2106 | Slave07 Outlet Port05 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2107 | Slave07 Outlet Port06 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2108 | Slave07 Outlet Port07 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2109 | Slave07 Outlet Port08 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2110 | Slave07 Outlet Port09 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2111 | Slave07 Outlet Port10 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2112 | Slave07 Outlet Port11 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2113 | Slave07 Outlet Port12 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2114 | Slave07 Outlet Port13 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2115 | Slave07 Outlet Port14 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2116 | Slave07 Outlet Port15 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2117 | Slave07 Outlet Port16 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2118 | Slave07 Outlet Port17 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2119 | Slave07 Outlet Port18 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2120 | Slave07 Outlet Port19 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2121 | Slave07 Outlet Port20 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2122 | Slave07 Outlet Port21 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2123 | Slave07 Outlet Port22 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2124 | Slave07 Outlet Port23 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2125 | Slave07 Outlet Port24 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2126 | Slave07 Outlet Port25 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2127 | Slave07 Outlet Port26 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2128 | Slave07 Outlet Port27 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2129 | Slave07 Outlet Port28 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2130 | Slave07 Outlet Port29 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2131 | Slave07 Outlet Port30 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2132 | Slave07 Outlet Port31 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2133 | Slave07 Outlet Port32 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2134 | Slave07 Outlet Port33 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2135 | Slave07 Outlet Port34 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2136 | Slave07 Outlet Port35 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2137 | Slave07 Outlet Port36 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2138 | Slave07 Outlet Port37 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2139 | Slave07 Outlet Port38 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2140 | Slave07 Outlet Port39 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2141 | Slave07 Outlet Port40 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2142 | Slave07 Outlet Port41 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2143 | Slave07 Outlet Port42 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2144 | Slave08 Outlet Port01 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2145 | Slave08 Outlet Port02 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2146 | Slave08 Outlet Port03 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2147 | Slave08 Outlet Port04 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2148 | Slave08 Outlet Port05 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2149 | Slave08 Outlet Port06 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2150 | Slave08 Outlet Port07 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2151 | Slave08 Outlet Port08 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2152 | Slave08 Outlet Port09 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2153 | Slave08 Outlet Port10 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2154 | Slave08 Outlet Port11 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2155 | Slave08 Outlet Port12 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2156 | Slave08 Outlet Port13 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2157 | Slave08 Outlet Port14 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2158 | Slave08 Outlet Port15 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2159 | Slave08 Outlet Port16 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2160 | Slave08 Outlet Port17 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2161 | Slave08 Outlet Port18 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2162 | Slave08 Outlet Port19 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2163 | Slave08 Outlet Port20 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2164 | Slave08 Outlet Port21 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2165 | Slave08 Outlet Port22 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2166 | Slave08 Outlet Port23 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2167 | Slave08 Outlet Port24 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2168 | Slave08 Outlet Port25 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2169 | Slave08 Outlet Port26 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2170 | Slave08 Outlet Port27 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2171 | Slave08 Outlet Port28 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2172 | Slave08 Outlet Port29 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2173 | Slave08 Outlet Port30 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2174 | Slave08 Outlet Port31 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2175 | Slave08 Outlet Port32 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2176 | Slave08 Outlet Port33 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2177 | Slave08 Outlet Port34 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2178 | Slave08 Outlet Port35 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2179 | Slave08 Outlet Port36 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2180 | Slave08 Outlet Port37 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2181 | Slave08 Outlet Port38 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2182 | Slave08 Outlet Port39 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2183 | Slave08 Outlet Port40 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2184 | Slave08 Outlet Port41 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2185 | Slave08 Outlet Port42 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2186 | Slave09 Outlet Port01 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2187 | Slave09 Outlet Port02 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2188 | Slave09 Outlet Port03 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2189 | Slave09 Outlet Port04 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2190 | Slave09 Outlet Port05 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2191 | Slave09 Outlet Port06 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2192 | Slave09 Outlet Port07 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2193 | Slave09 Outlet Port08 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2194 | Slave09 Outlet Port09 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2195 | Slave09 Outlet Port10 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2196 | Slave09 Outlet Port11 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2197 | Slave09 Outlet Port12 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2198 | Slave09 Outlet Port13 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2199 | Slave09 Outlet Port14 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2200 | Slave09 Outlet Port15 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2201 | Slave09 Outlet Port16 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2202 | Slave09 Outlet Port17 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2203 | Slave09 Outlet Port18 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2204 | Slave09 Outlet Port19 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2205 | Slave09 Outlet Port20 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2206 | Slave09 Outlet Port21 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2207 | Slave09 Outlet Port22 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2208 | Slave09 Outlet Port23 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2209 | Slave09 Outlet Port24 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2210 | Slave09 Outlet Port25 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2211 | Slave09 Outlet Port26 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2212 | Slave09 Outlet Port27 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2213 | Slave09 Outlet Port28 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2214 | Slave09 Outlet Port29 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2215 | Slave09 Outlet Port30 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2216 | Slave09 Outlet Port31 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2217 | Slave09 Outlet Port32 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2218 | Slave09 Outlet Port33 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2219 | Slave09 Outlet Port34 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2220 | Slave09 Outlet Port35 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2221 | Slave09 Outlet Port36 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2222 | Slave09 Outlet Port37 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2223 | Slave09 Outlet Port38 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2224 | Slave09 Outlet Port39 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2225 | Slave09 Outlet Port40 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2226 | Slave09 Outlet Port41 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2227 | Slave09 Outlet Port42 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2228 | Slave10 Outlet Port01 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2229 | Slave10 Outlet Port02 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2230 | Slave10 Outlet Port03 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2231 | Slave10 Outlet Port04 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2232 | Slave10 Outlet Port05 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2233 | Slave10 Outlet Port06 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2234 | Slave10 Outlet Port07 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2235 | Slave10 Outlet Port08 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2236 | Slave10 Outlet Port09 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2237 | Slave10 Outlet Port10 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2238 | Slave10 Outlet Port11 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2239 | Slave10 Outlet Port12 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2240 | Slave10 Outlet Port13 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2241 | Slave10 Outlet Port14 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2242 | Slave10 Outlet Port15 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2243 | Slave10 Outlet Port16 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2244 | Slave10 Outlet Port17 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2245 | Slave10 Outlet Port18 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2246 | Slave10 Outlet Port19 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2247 | Slave10 Outlet Port20 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2248 | Slave10 Outlet Port21 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2249 | Slave10 Outlet Port22 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2250 | Slave10 Outlet Port23 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2251 | Slave10 Outlet Port24 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2252 | Slave10 Outlet Port25 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2253 | Slave10 Outlet Port26 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2254 | Slave10 Outlet Port27 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2255 | Slave10 Outlet Port28 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2256 | Slave10 Outlet Port29 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2257 | Slave10 Outlet Port30 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2258 | Slave10 Outlet Port31 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2259 | Slave10 Outlet Port32 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2260 | Slave10 Outlet Port33 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2261 | Slave10 Outlet Port34 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2262 | Slave10 Outlet Port35 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2263 | Slave10 Outlet Port36 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2264 | Slave10 Outlet Port37 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2265 | Slave10 Outlet Port38 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2266 | Slave10 Outlet Port39 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2267 | Slave10 Outlet Port40 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2268 | Slave10 Outlet Port41 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2269 | Slave10 Outlet Port42 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2270 | Slave11 Outlet Port01 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2271 | Slave11 Outlet Port02 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2272 | Slave11 Outlet Port03 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2273 | Slave11 Outlet Port04 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2274 | Slave11 Outlet Port05 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2275 | Slave11 Outlet Port06 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2276 | Slave11 Outlet Port07 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2277 | Slave11 Outlet Port08 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2278 | Slave11 Outlet Port09 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2279 | Slave11 Outlet Port10 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2280 | Slave11 Outlet Port11 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2281 | Slave11 Outlet Port12 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2282 | Slave11 Outlet Port13 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2283 | Slave11 Outlet Port14 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2284 | Slave11 Outlet Port15 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2285 | Slave11 Outlet Port16 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2286 | Slave11 Outlet Port17 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2287 | Slave11 Outlet Port18 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2288 | Slave11 Outlet Port19 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2289 | Slave11 Outlet Port20 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2290 | Slave11 Outlet Port21 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2291 | Slave11 Outlet Port22 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2292 | Slave11 Outlet Port23 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2293 | Slave11 Outlet Port24 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2294 | Slave11 Outlet Port25 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2295 | Slave11 Outlet Port26 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2296 | Slave11 Outlet Port27 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2297 | Slave11 Outlet Port28 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2298 | Slave11 Outlet Port29 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2299 | Slave11 Outlet Port30 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2300 | Slave11 Outlet Port31 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2301 | Slave11 Outlet Port32 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2302 | Slave11 Outlet Port33 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2303 | Slave11 Outlet Port34 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2304 | Slave11 Outlet Port35 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2305 | Slave11 Outlet Port36 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2306 | Slave11 Outlet Port37 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2307 | Slave11 Outlet Port38 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2308 | Slave11 Outlet Port39 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2309 | Slave11 Outlet Port40 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2310 | Slave11 Outlet Port41 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2311 | Slave11 Outlet Port42 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2312 | Slave12 Outlet Port01 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2313 | Slave12 Outlet Port02 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2314 | Slave12 Outlet Port03 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2315 | Slave12 Outlet Port04 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2316 | Slave12 Outlet Port05 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2317 | Slave12 Outlet Port06 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2318 | Slave12 Outlet Port07 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2319 | Slave12 Outlet Port08 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2320 | Slave12 Outlet Port09 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2321 | Slave12 Outlet Port10 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2322 | Slave12 Outlet Port11 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2323 | Slave12 Outlet Port12 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2324 | Slave12 Outlet Port13 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2325 | Slave12 Outlet Port14 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2326 | Slave12 Outlet Port15 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2327 | Slave12 Outlet Port16 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2328 | Slave12 Outlet Port17 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2329 | Slave12 Outlet Port18 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2330 | Slave12 Outlet Port19 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2331 | Slave12 Outlet Port20 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2332 | Slave12 Outlet Port21 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2333 | Slave12 Outlet Port22 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2334 | Slave12 Outlet Port23 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2335 | Slave12 Outlet Port24 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2336 | Slave12 Outlet Port25 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2337 | Slave12 Outlet Port26 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2338 | Slave12 Outlet Port27 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2339 | Slave12 Outlet Port28 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2340 | Slave12 Outlet Port29 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2341 | Slave12 Outlet Port30 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2342 | Slave12 Outlet Port31 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2343 | Slave12 Outlet Port32 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2344 | Slave12 Outlet Port33 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2345 | Slave12 Outlet Port34 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2346 | Slave12 Outlet Port35 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2347 | Slave12 Outlet Port36 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2348 | Slave12 Outlet Port37 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2349 | Slave12 Outlet Port38 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2350 | Slave12 Outlet Port39 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2351 | Slave12 Outlet Port40 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2352 | Slave12 Outlet Port41 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2353 | Slave12 Outlet Port42 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2354 | Slave13 Outlet Port01 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2355 | Slave13 Outlet Port02 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2356 | Slave13 Outlet Port03 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2357 | Slave13 Outlet Port04 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2358 | Slave13 Outlet Port05 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2359 | Slave13 Outlet Port06 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2360 | Slave13 Outlet Port07 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2361 | Slave13 Outlet Port08 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2362 | Slave13 Outlet Port09 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2363 | Slave13 Outlet Port10 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2364 | Slave13 Outlet Port11 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2365 | Slave13 Outlet Port12 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2366 | Slave13 Outlet Port13 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2367 | Slave13 Outlet Port14 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2368 | Slave13 Outlet Port15 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2369 | Slave13 Outlet Port16 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2370 | Slave13 Outlet Port17 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2371 | Slave13 Outlet Port18 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2372 | Slave13 Outlet Port19 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2373 | Slave13 Outlet Port20 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2374 | Slave13 Outlet Port21 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2375 | Slave13 Outlet Port22 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2376 | Slave13 Outlet Port23 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2377 | Slave13 Outlet Port24 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2378 | Slave13 Outlet Port25 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2379 | Slave13 Outlet Port26 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2380 | Slave13 Outlet Port27 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2381 | Slave13 Outlet Port28 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2382 | Slave13 Outlet Port29 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2383 | Slave13 Outlet Port30 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2384 | Slave13 Outlet Port31 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2385 | Slave13 Outlet Port32 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2386 | Slave13 Outlet Port33 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2387 | Slave13 Outlet Port34 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2388 | Slave13 Outlet Port35 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2389 | Slave13 Outlet Port36 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2390 | Slave13 Outlet Port37 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2391 | Slave13 Outlet Port38 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2392 | Slave13 Outlet Port39 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2393 | Slave13 Outlet Port40 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2394 | Slave13 Outlet Port41 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2395 | Slave13 Outlet Port42 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2396 | Slave14 Outlet Port01 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2397 | Slave14 Outlet Port02 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2398 | Slave14 Outlet Port03 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2399 | Slave14 Outlet Port04 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2400 | Slave14 Outlet Port05 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2401 | Slave14 Outlet Port06 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2402 | Slave14 Outlet Port07 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2403 | Slave14 Outlet Port08 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2404 | Slave14 Outlet Port09 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2405 | Slave14 Outlet Port10 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2406 | Slave14 Outlet Port11 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2407 | Slave14 Outlet Port12 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2408 | Slave14 Outlet Port13 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2409 | Slave14 Outlet Port14 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2410 | Slave14 Outlet Port15 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2411 | Slave14 Outlet Port16 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2412 | Slave14 Outlet Port17 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2413 | Slave14 Outlet Port18 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2414 | Slave14 Outlet Port19 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2415 | Slave14 Outlet Port20 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2416 | Slave14 Outlet Port21 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2417 | Slave14 Outlet Port22 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2418 | Slave14 Outlet Port23 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2419 | Slave14 Outlet Port24 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2420 | Slave14 Outlet Port25 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2421 | Slave14 Outlet Port26 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2422 | Slave14 Outlet Port27 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2423 | Slave14 Outlet Port28 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2424 | Slave14 Outlet Port29 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2425 | Slave14 Outlet Port30 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2426 | Slave14 Outlet Port31 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2427 | Slave14 Outlet Port32 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2428 | Slave14 Outlet Port33 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2429 | Slave14 Outlet Port34 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2430 | Slave14 Outlet Port35 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2431 | Slave14 Outlet Port36 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2432 | Slave14 Outlet Port37 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2433 | Slave14 Outlet Port38 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2434 | Slave14 Outlet Port39 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2435 | Slave14 Outlet Port40 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2436 | Slave14 Outlet Port41 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2437 | Slave14 Outlet Port42 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2438 | Slave15 Outlet Port01 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2439 | Slave15 Outlet Port02 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2440 | Slave15 Outlet Port03 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2441 | Slave15 Outlet Port04 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2442 | Slave15 Outlet Port05 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2443 | Slave15 Outlet Port06 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2444 | Slave15 Outlet Port07 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2445 | Slave15 Outlet Port08 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2446 | Slave15 Outlet Port09 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2447 | Slave15 Outlet Port10 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2448 | Slave15 Outlet Port11 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2449 | Slave15 Outlet Port12 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2450 | Slave15 Outlet Port13 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2451 | Slave15 Outlet Port14 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2452 | Slave15 Outlet Port15 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2453 | Slave15 Outlet Port16 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2454 | Slave15 Outlet Port17 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2455 | Slave15 Outlet Port18 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2456 | Slave15 Outlet Port19 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2457 | Slave15 Outlet Port20 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2458 | Slave15 Outlet Port21 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2459 | Slave15 Outlet Port22 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2460 | Slave15 Outlet Port23 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2461 | Slave15 Outlet Port24 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2462 | Slave15 Outlet Port25 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2463 | Slave15 Outlet Port26 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2464 | Slave15 Outlet Port27 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2465 | Slave15 Outlet Port28 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2466 | Slave15 Outlet Port29 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2467 | Slave15 Outlet Port30 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2468 | Slave15 Outlet Port31 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2469 | Slave15 Outlet Port32 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2470 | Slave15 Outlet Port33 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2471 | Slave15 Outlet Port34 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2472 | Slave15 Outlet Port35 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2473 | Slave15 Outlet Port36 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2474 | Slave15 Outlet Port37 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2475 | Slave15 Outlet Port38 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2476 | Slave15 Outlet Port39 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2477 | Slave15 Outlet Port40 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2478 | Slave15 Outlet Port41 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2479 | Slave15 Outlet Port42 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2480 | Master Outlet Port01 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2481 | Master Outlet Port02 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2482 | Master Outlet Port03 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2483 | Master Outlet Port04 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2484 | Master Outlet Port05 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2485 | Master Outlet Port06 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2486 | Master Outlet Port07 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2487 | Master Outlet Port08 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2488 | Master Outlet Port09 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2489 | Master Outlet Port10 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2490 | Master Outlet Port11 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2491 | Master Outlet Port12 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2492 | Master Outlet Port13 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2493 | Master Outlet Port14 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2494 | Master Outlet Port15 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2495 | Master Outlet Port16 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2496 | Master Outlet Port17 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2497 | Master Outlet Port18 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2498 | Master Outlet Port19 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2499 | Master Outlet Port20 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2500 | Master Outlet Port21 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2501 | Master Outlet Port22 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2502 | Master Outlet Port23 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2503 | Master Outlet Port24 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2504 | Master Outlet Port25 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2505 | Master Outlet Port26 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2506 | Master Outlet Port27 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2507 | Master Outlet Port28 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2508 | Master Outlet Port29 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2509 | Master Outlet Port30 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2510 | Master Outlet Port31 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2511 | Master Outlet Port32 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2512 | Master Outlet Port33 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2513 | Master Outlet Port34 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2514 | Master Outlet Port35 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2515 | Master Outlet Port36 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2516 | Master Outlet Port37 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2517 | Master Outlet Port38 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2518 | Master Outlet Port39 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2519 | Master Outlet Port40 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2520 | Master Outlet Port41 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2521 | Master Outlet Port42 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2522 | Slave01 Outlet Port01 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2523 | Slave01 Outlet Port02 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2524 | Slave01 Outlet Port03 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2525 | Slave01 Outlet Port04 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2526 | Slave01 Outlet Port05 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2527 | Slave01 Outlet Port06 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2528 | Slave01 Outlet Port07 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2529 | Slave01 Outlet Port08 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2530 | Slave01 Outlet Port09 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2531 | Slave01 Outlet Port10 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2532 | Slave01 Outlet Port11 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2533 | Slave01 Outlet Port12 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2534 | Slave01 Outlet Port13 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2535 | Slave01 Outlet Port14 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2536 | Slave01 Outlet Port15 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2537 | Slave01 Outlet Port16 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2538 | Slave01 Outlet Port17 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2539 | Slave01 Outlet Port18 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2540 | Slave01 Outlet Port19 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2541 | Slave01 Outlet Port20 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2542 | Slave01 Outlet Port21 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2543 | Slave01 Outlet Port22 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2544 | Slave01 Outlet Port23 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2545 | Slave01 Outlet Port24 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2546 | Slave01 Outlet Port25 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2547 | Slave01 Outlet Port26 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2548 | Slave01 Outlet Port27 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2549 | Slave01 Outlet Port28 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2550 | Slave01 Outlet Port29 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2551 | Slave01 Outlet Port30 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2552 | Slave01 Outlet Port31 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2553 | Slave01 Outlet Port32 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2554 | Slave01 Outlet Port33 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2555 | Slave01 Outlet Port34 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2556 | Slave01 Outlet Port35 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2557 | Slave01 Outlet Port36 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2558 | Slave01 Outlet Port37 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2559 | Slave01 Outlet Port38 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2560 | Slave01 Outlet Port39 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2561 | Slave01 Outlet Port40 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2562 | Slave01 Outlet Port41 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2563 | Slave01 Outlet Port42 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2564 | Slave02 Outlet Port01 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2565 | Slave02 Outlet Port02 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2566 | Slave02 Outlet Port03 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2567 | Slave02 Outlet Port04 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2568 | Slave02 Outlet Port05 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2569 | Slave02 Outlet Port06 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2570 | Slave02 Outlet Port07 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2571 | Slave02 Outlet Port08 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2572 | Slave02 Outlet Port09 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2573 | Slave02 Outlet Port10 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2574 | Slave02 Outlet Port11 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2575 | Slave02 Outlet Port12 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2576 | Slave02 Outlet Port13 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2577 | Slave02 Outlet Port14 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2578 | Slave02 Outlet Port15 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2579 | Slave02 Outlet Port16 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2580 | Slave02 Outlet Port17 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2581 | Slave02 Outlet Port18 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2582 | Slave02 Outlet Port19 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2583 | Slave02 Outlet Port20 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2584 | Slave02 Outlet Port21 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2585 | Slave02 Outlet Port22 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2586 | Slave02 Outlet Port23 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2587 | Slave02 Outlet Port24 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2588 | Slave02 Outlet Port25 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2589 | Slave02 Outlet Port26 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2590 | Slave02 Outlet Port27 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2591 | Slave02 Outlet Port28 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2592 | Slave02 Outlet Port29 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2593 | Slave02 Outlet Port30 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2594 | Slave02 Outlet Port31 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2595 | Slave02 Outlet Port32 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2596 | Slave02 Outlet Port33 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2597 | Slave02 Outlet Port34 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2598 | Slave02 Outlet Port35 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2599 | Slave02 Outlet Port36 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2600 | Slave02 Outlet Port37 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2601 | Slave02 Outlet Port38 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2602 | Slave02 Outlet Port39 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2603 | Slave02 Outlet Port40 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2604 | Slave02 Outlet Port41 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2605 | Slave02 Outlet Port42 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2606 | Slave03 Outlet Port01 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2607 | Slave03 Outlet Port02 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2608 | Slave03 Outlet Port03 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2609 | Slave03 Outlet Port04 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2610 | Slave03 Outlet Port05 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2611 | Slave03 Outlet Port06 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2612 | Slave03 Outlet Port07 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2613 | Slave03 Outlet Port08 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2614 | Slave03 Outlet Port09 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2615 | Slave03 Outlet Port10 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2616 | Slave03 Outlet Port11 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2617 | Slave03 Outlet Port12 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2618 | Slave03 Outlet Port13 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2619 | Slave03 Outlet Port14 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2620 | Slave03 Outlet Port15 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2621 | Slave03 Outlet Port16 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2622 | Slave03 Outlet Port17 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2623 | Slave03 Outlet Port18 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2624 | Slave03 Outlet Port19 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2625 | Slave03 Outlet Port20 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2626 | Slave03 Outlet Port21 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2627 | Slave03 Outlet Port22 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2628 | Slave03 Outlet Port23 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2629 | Slave03 Outlet Port24 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2630 | Slave03 Outlet Port25 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2631 | Slave03 Outlet Port26 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2632 | Slave03 Outlet Port27 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2633 | Slave03 Outlet Port28 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2634 | Slave03 Outlet Port29 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2635 | Slave03 Outlet Port30 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2636 | Slave03 Outlet Port31 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2637 | Slave03 Outlet Port32 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2638 | Slave03 Outlet Port33 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2639 | Slave03 Outlet Port34 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2640 | Slave03 Outlet Port35 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2641 | Slave03 Outlet Port36 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2642 | Slave03 Outlet Port37 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2643 | Slave03 Outlet Port38 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2644 | Slave03 Outlet Port39 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2645 | Slave03 Outlet Port40 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2646 | Slave03 Outlet Port41 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2647 | Slave03 Outlet Port42 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2648 | Slave04 Outlet Port01 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2649 | Slave04 Outlet Port02 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2650 | Slave04 Outlet Port03 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2651 | Slave04 Outlet Port04 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2652 | Slave04 Outlet Port05 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2653 | Slave04 Outlet Port06 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2654 | Slave04 Outlet Port07 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2655 | Slave04 Outlet Port08 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2656 | Slave04 Outlet Port09 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2657 | Slave04 Outlet Port10 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2658 | Slave04 Outlet Port11 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2659 | Slave04 Outlet Port12 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2660 | Slave04 Outlet Port13 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2661 | Slave04 Outlet Port14 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2662 | Slave04 Outlet Port15 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2663 | Slave04 Outlet Port16 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2664 | Slave04 Outlet Port17 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2665 | Slave04 Outlet Port18 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2666 | Slave04 Outlet Port19 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2667 | Slave04 Outlet Port20 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2668 | Slave04 Outlet Port21 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2669 | Slave04 Outlet Port22 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2670 | Slave04 Outlet Port23 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2671 | Slave04 Outlet Port24 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2672 | Slave04 Outlet Port25 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2673 | Slave04 Outlet Port26 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2674 | Slave04 Outlet Port27 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2675 | Slave04 Outlet Port28 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2676 | Slave04 Outlet Port29 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2677 | Slave04 Outlet Port30 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2678 | Slave04 Outlet Port31 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2679 | Slave04 Outlet Port32 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2680 | Slave04 Outlet Port33 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2681 | Slave04 Outlet Port34 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2682 | Slave04 Outlet Port35 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2683 | Slave04 Outlet Port36 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2684 | Slave04 Outlet Port37 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2685 | Slave04 Outlet Port38 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2686 | Slave04 Outlet Port39 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2687 | Slave04 Outlet Port40 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2688 | Slave04 Outlet Port41 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2689 | Slave04 Outlet Port42 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2690 | Slave05 Outlet Port01 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2691 | Slave05 Outlet Port02 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2692 | Slave05 Outlet Port03 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2693 | Slave05 Outlet Port04 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2694 | Slave05 Outlet Port05 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2695 | Slave05 Outlet Port06 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2696 | Slave05 Outlet Port07 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2697 | Slave05 Outlet Port08 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2698 | Slave05 Outlet Port09 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2699 | Slave05 Outlet Port10 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2700 | Slave05 Outlet Port11 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2701 | Slave05 Outlet Port12 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2702 | Slave05 Outlet Port13 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2703 | Slave05 Outlet Port14 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2704 | Slave05 Outlet Port15 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2705 | Slave05 Outlet Port16 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2706 | Slave05 Outlet Port17 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2707 | Slave05 Outlet Port18 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2708 | Slave05 Outlet Port19 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2709 | Slave05 Outlet Port20 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2710 | Slave05 Outlet Port21 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2711 | Slave05 Outlet Port22 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2712 | Slave05 Outlet Port23 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2713 | Slave05 Outlet Port24 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2714 | Slave05 Outlet Port25 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2715 | Slave05 Outlet Port26 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2716 | Slave05 Outlet Port27 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2717 | Slave05 Outlet Port28 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2718 | Slave05 Outlet Port29 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2719 | Slave05 Outlet Port30 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2720 | Slave05 Outlet Port31 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2721 | Slave05 Outlet Port32 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2722 | Slave05 Outlet Port33 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2723 | Slave05 Outlet Port34 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2724 | Slave05 Outlet Port35 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2725 | Slave05 Outlet Port36 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2726 | Slave05 Outlet Port37 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2727 | Slave05 Outlet Port38 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2728 | Slave05 Outlet Port39 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2729 | Slave05 Outlet Port40 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2730 | Slave05 Outlet Port41 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2731 | Slave05 Outlet Port42 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2732 | Slave06 Outlet Port01 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2733 | Slave06 Outlet Port02 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2734 | Slave06 Outlet Port03 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2735 | Slave06 Outlet Port04 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2736 | Slave06 Outlet Port05 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2737 | Slave06 Outlet Port06 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2738 | Slave06 Outlet Port07 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2739 | Slave06 Outlet Port08 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2740 | Slave06 Outlet Port09 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2741 | Slave06 Outlet Port10 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2742 | Slave06 Outlet Port11 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2743 | Slave06 Outlet Port12 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2744 | Slave06 Outlet Port13 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2745 | Slave06 Outlet Port14 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2746 | Slave06 Outlet Port15 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2747 | Slave06 Outlet Port16 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2748 | Slave06 Outlet Port17 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2749 | Slave06 Outlet Port18 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2750 | Slave06 Outlet Port19 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2751 | Slave06 Outlet Port20 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2752 | Slave06 Outlet Port21 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2753 | Slave06 Outlet Port22 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2754 | Slave06 Outlet Port23 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2755 | Slave06 Outlet Port24 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2756 | Slave06 Outlet Port25 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2757 | Slave06 Outlet Port26 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2758 | Slave06 Outlet Port27 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2759 | Slave06 Outlet Port28 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2760 | Slave06 Outlet Port29 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2761 | Slave06 Outlet Port30 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2762 | Slave06 Outlet Port31 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2763 | Slave06 Outlet Port32 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2764 | Slave06 Outlet Port33 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2765 | Slave06 Outlet Port34 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2766 | Slave06 Outlet Port35 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2767 | Slave06 Outlet Port36 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2768 | Slave06 Outlet Port37 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2769 | Slave06 Outlet Port38 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2770 | Slave06 Outlet Port39 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2771 | Slave06 Outlet Port40 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2772 | Slave06 Outlet Port41 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2773 | Slave06 Outlet Port42 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2774 | Slave07 Outlet Port01 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2775 | Slave07 Outlet Port02 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2776 | Slave07 Outlet Port03 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2777 | Slave07 Outlet Port04 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2778 | Slave07 Outlet Port05 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2779 | Slave07 Outlet Port06 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2780 | Slave07 Outlet Port07 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2781 | Slave07 Outlet Port08 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2782 | Slave07 Outlet Port09 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2783 | Slave07 Outlet Port10 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2784 | Slave07 Outlet Port11 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2785 | Slave07 Outlet Port12 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2786 | Slave07 Outlet Port13 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2787 | Slave07 Outlet Port14 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2788 | Slave07 Outlet Port15 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2789 | Slave07 Outlet Port16 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2790 | Slave07 Outlet Port17 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2791 | Slave07 Outlet Port18 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2792 | Slave07 Outlet Port19 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2793 | Slave07 Outlet Port20 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2794 | Slave07 Outlet Port21 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2795 | Slave07 Outlet Port22 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2796 | Slave07 Outlet Port23 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2797 | Slave07 Outlet Port24 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2798 | Slave07 Outlet Port25 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2799 | Slave07 Outlet Port26 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2800 | Slave07 Outlet Port27 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2801 | Slave07 Outlet Port28 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2802 | Slave07 Outlet Port29 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2803 | Slave07 Outlet Port30 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2804 | Slave07 Outlet Port31 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2805 | Slave07 Outlet Port32 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2806 | Slave07 Outlet Port33 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2807 | Slave07 Outlet Port34 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2808 | Slave07 Outlet Port35 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2809 | Slave07 Outlet Port36 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2810 | Slave07 Outlet Port37 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2811 | Slave07 Outlet Port38 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2812 | Slave07 Outlet Port39 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2813 | Slave07 Outlet Port40 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2814 | Slave07 Outlet Port41 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2815 | Slave07 Outlet Port42 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2816 | Slave08 Outlet Port01 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2817 | Slave08 Outlet Port02 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2818 | Slave08 Outlet Port03 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2819 | Slave08 Outlet Port04 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2820 | Slave08 Outlet Port05 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2821 | Slave08 Outlet Port06 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2822 | Slave08 Outlet Port07 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2823 | Slave08 Outlet Port08 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2824 | Slave08 Outlet Port09 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2825 | Slave08 Outlet Port10 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2826 | Slave08 Outlet Port11 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2827 | Slave08 Outlet Port12 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2828 | Slave08 Outlet Port13 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2829 | Slave08 Outlet Port14 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2830 | Slave08 Outlet Port15 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2831 | Slave08 Outlet Port16 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2832 | Slave08 Outlet Port17 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2833 | Slave08 Outlet Port18 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2834 | Slave08 Outlet Port19 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2835 | Slave08 Outlet Port20 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2836 | Slave08 Outlet Port21 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2837 | Slave08 Outlet Port22 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2838 | Slave08 Outlet Port23 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2839 | Slave08 Outlet Port24 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2840 | Slave08 Outlet Port25 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2841 | Slave08 Outlet Port26 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2842 | Slave08 Outlet Port27 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2843 | Slave08 Outlet Port28 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2844 | Slave08 Outlet Port29 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2845 | Slave08 Outlet Port30 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2846 | Slave08 Outlet Port31 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2847 | Slave08 Outlet Port32 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2848 | Slave08 Outlet Port33 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2849 | Slave08 Outlet Port34 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2850 | Slave08 Outlet Port35 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2851 | Slave08 Outlet Port36 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2852 | Slave08 Outlet Port37 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2853 | Slave08 Outlet Port38 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2854 | Slave08 Outlet Port39 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2855 | Slave08 Outlet Port40 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2856 | Slave08 Outlet Port41 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2857 | Slave08 Outlet Port42 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2858 | Slave09 Outlet Port01 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2859 | Slave09 Outlet Port02 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2860 | Slave09 Outlet Port03 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2861 | Slave09 Outlet Port04 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2862 | Slave09 Outlet Port05 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2863 | Slave09 Outlet Port06 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2864 | Slave09 Outlet Port07 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2865 | Slave09 Outlet Port08 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2866 | Slave09 Outlet Port09 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2867 | Slave09 Outlet Port10 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2868 | Slave09 Outlet Port11 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2869 | Slave09 Outlet Port12 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2870 | Slave09 Outlet Port13 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2871 | Slave09 Outlet Port14 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2872 | Slave09 Outlet Port15 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2873 | Slave09 Outlet Port16 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2874 | Slave09 Outlet Port17 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2875 | Slave09 Outlet Port18 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2876 | Slave09 Outlet Port19 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2877 | Slave09 Outlet Port20 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2878 | Slave09 Outlet Port21 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2879 | Slave09 Outlet Port22 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2880 | Slave09 Outlet Port23 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2881 | Slave09 Outlet Port24 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2882 | Slave09 Outlet Port25 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2883 | Slave09 Outlet Port26 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2884 | Slave09 Outlet Port27 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2885 | Slave09 Outlet Port28 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2886 | Slave09 Outlet Port29 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2887 | Slave09 Outlet Port30 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2888 | Slave09 Outlet Port31 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2889 | Slave09 Outlet Port32 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2890 | Slave09 Outlet Port33 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2891 | Slave09 Outlet Port34 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2892 | Slave09 Outlet Port35 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2893 | Slave09 Outlet Port36 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2894 | Slave09 Outlet Port37 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2895 | Slave09 Outlet Port38 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2896 | Slave09 Outlet Port39 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2897 | Slave09 Outlet Port40 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2898 | Slave09 Outlet Port41 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2899 | Slave09 Outlet Port42 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2900 | Slave10 Outlet Port01 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2901 | Slave10 Outlet Port02 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2902 | Slave10 Outlet Port03 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2903 | Slave10 Outlet Port04 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2904 | Slave10 Outlet Port05 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2905 | Slave10 Outlet Port06 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2906 | Slave10 Outlet Port07 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2907 | Slave10 Outlet Port08 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2908 | Slave10 Outlet Port09 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2909 | Slave10 Outlet Port10 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2910 | Slave10 Outlet Port11 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2911 | Slave10 Outlet Port12 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2912 | Slave10 Outlet Port13 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2913 | Slave10 Outlet Port14 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2914 | Slave10 Outlet Port15 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2915 | Slave10 Outlet Port16 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2916 | Slave10 Outlet Port17 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2917 | Slave10 Outlet Port18 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2918 | Slave10 Outlet Port19 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2919 | Slave10 Outlet Port20 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2920 | Slave10 Outlet Port21 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2921 | Slave10 Outlet Port22 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2922 | Slave10 Outlet Port23 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2923 | Slave10 Outlet Port24 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2924 | Slave10 Outlet Port25 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2925 | Slave10 Outlet Port26 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2926 | Slave10 Outlet Port27 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2927 | Slave10 Outlet Port28 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2928 | Slave10 Outlet Port29 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2929 | Slave10 Outlet Port30 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2930 | Slave10 Outlet Port31 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2931 | Slave10 Outlet Port32 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2932 | Slave10 Outlet Port33 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2933 | Slave10 Outlet Port34 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2934 | Slave10 Outlet Port35 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2935 | Slave10 Outlet Port36 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2936 | Slave10 Outlet Port37 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2937 | Slave10 Outlet Port38 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2938 | Slave10 Outlet Port39 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2939 | Slave10 Outlet Port40 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2940 | Slave10 Outlet Port41 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2941 | Slave10 Outlet Port42 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2942 | Slave11 Outlet Port01 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2943 | Slave11 Outlet Port02 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2944 | Slave11 Outlet Port03 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2945 | Slave11 Outlet Port04 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2946 | Slave11 Outlet Port05 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2947 | Slave11 Outlet Port06 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2948 | Slave11 Outlet Port07 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2949 | Slave11 Outlet Port08 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2950 | Slave11 Outlet Port09 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2951 | Slave11 Outlet Port10 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2952 | Slave11 Outlet Port11 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2953 | Slave11 Outlet Port12 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2954 | Slave11 Outlet Port13 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2955 | Slave11 Outlet Port14 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2956 | Slave11 Outlet Port15 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2957 | Slave11 Outlet Port16 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2958 | Slave11 Outlet Port17 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2959 | Slave11 Outlet Port18 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2960 | Slave11 Outlet Port19 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2961 | Slave11 Outlet Port20 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2962 | Slave11 Outlet Port21 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2963 | Slave11 Outlet Port22 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2964 | Slave11 Outlet Port23 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2965 | Slave11 Outlet Port24 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2966 | Slave11 Outlet Port25 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2967 | Slave11 Outlet Port26 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2968 | Slave11 Outlet Port27 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2969 | Slave11 Outlet Port28 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2970 | Slave11 Outlet Port29 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2971 | Slave11 Outlet Port30 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2972 | Slave11 Outlet Port31 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2973 | Slave11 Outlet Port32 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2974 | Slave11 Outlet Port33 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2975 | Slave11 Outlet Port34 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2976 | Slave11 Outlet Port35 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2977 | Slave11 Outlet Port36 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2978 | Slave11 Outlet Port37 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2979 | Slave11 Outlet Port38 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2980 | Slave11 Outlet Port39 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2981 | Slave11 Outlet Port40 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2982 | Slave11 Outlet Port41 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2983 | Slave11 Outlet Port42 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2984 | Slave12 Outlet Port01 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2985 | Slave12 Outlet Port02 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2986 | Slave12 Outlet Port03 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2987 | Slave12 Outlet Port04 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2988 | Slave12 Outlet Port05 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2989 | Slave12 Outlet Port06 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2990 | Slave12 Outlet Port07 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2991 | Slave12 Outlet Port08 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2992 | Slave12 Outlet Port09 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2993 | Slave12 Outlet Port10 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2994 | Slave12 Outlet Port11 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2995 | Slave12 Outlet Port12 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2996 | Slave12 Outlet Port13 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2997 | Slave12 Outlet Port14 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2998 | Slave12 Outlet Port15 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
2999 | Slave12 Outlet Port16 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3000 | Slave12 Outlet Port17 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3001 | Slave12 Outlet Port18 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3002 | Slave12 Outlet Port19 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3003 | Slave12 Outlet Port20 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3004 | Slave12 Outlet Port21 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3005 | Slave12 Outlet Port22 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3006 | Slave12 Outlet Port23 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3007 | Slave12 Outlet Port24 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3008 | Slave12 Outlet Port25 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3009 | Slave12 Outlet Port26 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3010 | Slave12 Outlet Port27 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3011 | Slave12 Outlet Port28 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3012 | Slave12 Outlet Port29 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3013 | Slave12 Outlet Port30 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3014 | Slave12 Outlet Port31 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3015 | Slave12 Outlet Port32 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3016 | Slave12 Outlet Port33 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3017 | Slave12 Outlet Port34 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3018 | Slave12 Outlet Port35 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3019 | Slave12 Outlet Port36 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3020 | Slave12 Outlet Port37 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3021 | Slave12 Outlet Port38 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3022 | Slave12 Outlet Port39 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3023 | Slave12 Outlet Port40 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3024 | Slave12 Outlet Port41 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3025 | Slave12 Outlet Port42 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3026 | Slave13 Outlet Port01 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3027 | Slave13 Outlet Port02 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3028 | Slave13 Outlet Port03 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3029 | Slave13 Outlet Port04 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3030 | Slave13 Outlet Port05 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3031 | Slave13 Outlet Port06 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3032 | Slave13 Outlet Port07 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3033 | Slave13 Outlet Port08 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3034 | Slave13 Outlet Port09 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3035 | Slave13 Outlet Port10 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3036 | Slave13 Outlet Port11 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3037 | Slave13 Outlet Port12 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3038 | Slave13 Outlet Port13 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3039 | Slave13 Outlet Port14 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3040 | Slave13 Outlet Port15 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3041 | Slave13 Outlet Port16 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3042 | Slave13 Outlet Port17 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3043 | Slave13 Outlet Port18 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3044 | Slave13 Outlet Port19 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3045 | Slave13 Outlet Port20 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3046 | Slave13 Outlet Port21 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3047 | Slave13 Outlet Port22 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3048 | Slave13 Outlet Port23 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3049 | Slave13 Outlet Port24 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3050 | Slave13 Outlet Port25 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3051 | Slave13 Outlet Port26 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3052 | Slave13 Outlet Port27 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3053 | Slave13 Outlet Port28 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3054 | Slave13 Outlet Port29 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3055 | Slave13 Outlet Port30 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3056 | Slave13 Outlet Port31 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3057 | Slave13 Outlet Port32 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3058 | Slave13 Outlet Port33 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3059 | Slave13 Outlet Port34 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3060 | Slave13 Outlet Port35 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3061 | Slave13 Outlet Port36 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3062 | Slave13 Outlet Port37 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3063 | Slave13 Outlet Port38 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3064 | Slave13 Outlet Port39 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3065 | Slave13 Outlet Port40 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3066 | Slave13 Outlet Port41 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3067 | Slave13 Outlet Port42 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3068 | Slave14 Outlet Port01 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3069 | Slave14 Outlet Port02 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3070 | Slave14 Outlet Port03 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3071 | Slave14 Outlet Port04 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3072 | Slave14 Outlet Port05 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3073 | Slave14 Outlet Port06 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3074 | Slave14 Outlet Port07 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3075 | Slave14 Outlet Port08 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3076 | Slave14 Outlet Port09 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3077 | Slave14 Outlet Port10 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3078 | Slave14 Outlet Port11 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3079 | Slave14 Outlet Port12 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3080 | Slave14 Outlet Port13 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3081 | Slave14 Outlet Port14 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3082 | Slave14 Outlet Port15 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3083 | Slave14 Outlet Port16 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3084 | Slave14 Outlet Port17 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3085 | Slave14 Outlet Port18 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3086 | Slave14 Outlet Port19 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3087 | Slave14 Outlet Port20 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3088 | Slave14 Outlet Port21 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3089 | Slave14 Outlet Port22 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3090 | Slave14 Outlet Port23 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3091 | Slave14 Outlet Port24 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3092 | Slave14 Outlet Port25 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3093 | Slave14 Outlet Port26 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3094 | Slave14 Outlet Port27 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3095 | Slave14 Outlet Port28 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3096 | Slave14 Outlet Port29 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3097 | Slave14 Outlet Port30 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3098 | Slave14 Outlet Port31 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3099 | Slave14 Outlet Port32 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3100 | Slave14 Outlet Port33 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3101 | Slave14 Outlet Port34 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3102 | Slave14 Outlet Port35 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3103 | Slave14 Outlet Port36 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3104 | Slave14 Outlet Port37 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3105 | Slave14 Outlet Port38 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3106 | Slave14 Outlet Port39 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3107 | Slave14 Outlet Port40 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3108 | Slave14 Outlet Port41 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3109 | Slave14 Outlet Port42 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3110 | Slave15 Outlet Port01 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3111 | Slave15 Outlet Port02 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3112 | Slave15 Outlet Port03 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3113 | Slave15 Outlet Port04 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3114 | Slave15 Outlet Port05 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3115 | Slave15 Outlet Port06 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3116 | Slave15 Outlet Port07 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3117 | Slave15 Outlet Port08 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3118 | Slave15 Outlet Port09 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3119 | Slave15 Outlet Port10 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3120 | Slave15 Outlet Port11 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3121 | Slave15 Outlet Port12 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3122 | Slave15 Outlet Port13 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3123 | Slave15 Outlet Port14 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3124 | Slave15 Outlet Port15 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3125 | Slave15 Outlet Port16 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3126 | Slave15 Outlet Port17 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3127 | Slave15 Outlet Port18 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3128 | Slave15 Outlet Port19 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3129 | Slave15 Outlet Port20 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3130 | Slave15 Outlet Port21 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3131 | Slave15 Outlet Port22 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3132 | Slave15 Outlet Port23 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3133 | Slave15 Outlet Port24 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3134 | Slave15 Outlet Port25 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3135 | Slave15 Outlet Port26 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3136 | Slave15 Outlet Port27 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3137 | Slave15 Outlet Port28 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3138 | Slave15 Outlet Port29 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3139 | Slave15 Outlet Port30 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3140 | Slave15 Outlet Port31 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3141 | Slave15 Outlet Port32 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3142 | Slave15 Outlet Port33 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3143 | Slave15 Outlet Port34 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3144 | Slave15 Outlet Port35 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3145 | Slave15 Outlet Port36 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3146 | Slave15 Outlet Port37 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3147 | Slave15 Outlet Port38 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3148 | Slave15 Outlet Port39 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3149 | Slave15 Outlet Port40 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3150 | Slave15 Outlet Port41 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3151 | Slave15 Outlet Port42 Status | RO | 2 bytes | Bit0:Event Critical; Bit1:Event Warning; Bit2:Over Current Critical; Bit3:Over Current Warning; Bit4:Over Power Critical; Bit5:Over Power Warning
3152 | Master Outlet Port01 Voltage | RO | 2 bytes | Unit:0.1V
3153 | Master Outlet Port02 Voltage | RO | 2 bytes | Unit:0.1V
3154 | Master Outlet Port03 Voltage | RO | 2 bytes | Unit:0.1V
3155 | Master Outlet Port04 Voltage | RO | 2 bytes | Unit:0.1V
3156 | Master Outlet Port05 Voltage | RO | 2 bytes | Unit:0.1V
3157 | Master Outlet Port06 Voltage | RO | 2 bytes | Unit:0.1V
3158 | Master Outlet Port07 Voltage | RO | 2 bytes | Unit:0.1V
3159 | Master Outlet Port08 Voltage | RO | 2 bytes | Unit:0.1V
3160 | Master Outlet Port09 Voltage | RO | 2 bytes | Unit:0.1V
3161 | Master Outlet Port10 Voltage | RO | 2 bytes | Unit:0.1V
3162 | Master Outlet Port11 Voltage | RO | 2 bytes | Unit:0.1V
3163 | Master Outlet Port12 Voltage | RO | 2 bytes | Unit:0.1V
3164 | Master Outlet Port13 Voltage | RO | 2 bytes | Unit:0.1V
3165 | Master Outlet Port14 Voltage | RO | 2 bytes | Unit:0.1V
3166 | Master Outlet Port15 Voltage | RO | 2 bytes | Unit:0.1V
3167 | Master Outlet Port16 Voltage | RO | 2 bytes | Unit:0.1V
3168 | Master Outlet Port17 Voltage | RO | 2 bytes | Unit:0.1V
3169 | Master Outlet Port18 Voltage | RO | 2 bytes | Unit:0.1V
3170 | Master Outlet Port19 Voltage | RO | 2 bytes | Unit:0.1V
3171 | Master Outlet Port20 Voltage | RO | 2 bytes | Unit:0.1V
3172 | Master Outlet Port21 Voltage | RO | 2 bytes | Unit:0.1V
3173 | Master Outlet Port22 Voltage | RO | 2 bytes | Unit:0.1V
3174 | Master Outlet Port23 Voltage | RO | 2 bytes | Unit:0.1V
3175 | Master Outlet Port24 Voltage | RO | 2 bytes | Unit:0.1V
3176 | Master Outlet Port25 Voltage | RO | 2 bytes | Unit:0.1V
3177 | Master Outlet Port26 Voltage | RO | 2 bytes | Unit:0.1V
3178 | Master Outlet Port27 Voltage | RO | 2 bytes | Unit:0.1V
3179 | Master Outlet Port28 Voltage | RO | 2 bytes | Unit:0.1V
3180 | Master Outlet Port29 Voltage | RO | 2 bytes | Unit:0.1V
3181 | Master Outlet Port30 Voltage | RO | 2 bytes | Unit:0.1V
3182 | Master Outlet Port31 Voltage | RO | 2 bytes | Unit:0.1V
3183 | Master Outlet Port32 Voltage | RO | 2 bytes | Unit:0.1V
3184 | Master Outlet Port33 Voltage | RO | 2 bytes | Unit:0.1V
3185 | Master Outlet Port34 Voltage | RO | 2 bytes | Unit:0.1V
3186 | Master Outlet Port35 Voltage | RO | 2 bytes | Unit:0.1V
3187 | Master Outlet Port36 Voltage | RO | 2 bytes | Unit:0.1V
3188 | Master Outlet Port37 Voltage | RO | 2 bytes | Unit:0.1V
3189 | Master Outlet Port38 Voltage | RO | 2 bytes | Unit:0.1V
3190 | Master Outlet Port39 Voltage | RO | 2 bytes | Unit:0.1V
3191 | Master Outlet Port40 Voltage | RO | 2 bytes | Unit:0.1V
3192 | Master Outlet Port41 Voltage | RO | 2 bytes | Unit:0.1V
3193 | Master Outlet Port42 Voltage | RO | 2 bytes | Unit:0.1V
3194 | Slave01 Outlet Port01 Voltage | RO | 2 bytes | Unit:0.1V
3195 | Slave01 Outlet Port02 Voltage | RO | 2 bytes | Unit:0.1V
3196 | Slave01 Outlet Port03 Voltage | RO | 2 bytes | Unit:0.1V
3197 | Slave01 Outlet Port04 Voltage | RO | 2 bytes | Unit:0.1V
3198 | Slave01 Outlet Port05 Voltage | RO | 2 bytes | Unit:0.1V
3199 | Slave01 Outlet Port06 Voltage | RO | 2 bytes | Unit:0.1V
3200 | Slave01 Outlet Port07 Voltage | RO | 2 bytes | Unit:0.1V
3201 | Slave01 Outlet Port08 Voltage | RO | 2 bytes | Unit:0.1V
3202 | Slave01 Outlet Port09 Voltage | RO | 2 bytes | Unit:0.1V
3203 | Slave01 Outlet Port10 Voltage | RO | 2 bytes | Unit:0.1V
3204 | Slave01 Outlet Port11 Voltage | RO | 2 bytes | Unit:0.1V
3205 | Slave01 Outlet Port12 Voltage | RO | 2 bytes | Unit:0.1V
3206 | Slave01 Outlet Port13 Voltage | RO | 2 bytes | Unit:0.1V
3207 | Slave01 Outlet Port14 Voltage | RO | 2 bytes | Unit:0.1V
3208 | Slave01 Outlet Port15 Voltage | RO | 2 bytes | Unit:0.1V
3209 | Slave01 Outlet Port16 Voltage | RO | 2 bytes | Unit:0.1V
3210 | Slave01 Outlet Port17 Voltage | RO | 2 bytes | Unit:0.1V
3211 | Slave01 Outlet Port18 Voltage | RO | 2 bytes | Unit:0.1V
3212 | Slave01 Outlet Port19 Voltage | RO | 2 bytes | Unit:0.1V
3213 | Slave01 Outlet Port20 Voltage | RO | 2 bytes | Unit:0.1V
3214 | Slave01 Outlet Port21 Voltage | RO | 2 bytes | Unit:0.1V
3215 | Slave01 Outlet Port22 Voltage | RO | 2 bytes | Unit:0.1V
3216 | Slave01 Outlet Port23 Voltage | RO | 2 bytes | Unit:0.1V
3217 | Slave01 Outlet Port24 Voltage | RO | 2 bytes | Unit:0.1V
3218 | Slave01 Outlet Port25 Voltage | RO | 2 bytes | Unit:0.1V
3219 | Slave01 Outlet Port26 Voltage | RO | 2 bytes | Unit:0.1V
3220 | Slave01 Outlet Port27 Voltage | RO | 2 bytes | Unit:0.1V
3221 | Slave01 Outlet Port28 Voltage | RO | 2 bytes | Unit:0.1V
3222 | Slave01 Outlet Port29 Voltage | RO | 2 bytes | Unit:0.1V
3223 | Slave01 Outlet Port30 Voltage | RO | 2 bytes | Unit:0.1V
3224 | Slave01 Outlet Port31 Voltage | RO | 2 bytes | Unit:0.1V
3225 | Slave01 Outlet Port32 Voltage | RO | 2 bytes | Unit:0.1V
3226 | Slave01 Outlet Port33 Voltage | RO | 2 bytes | Unit:0.1V
3227 | Slave01 Outlet Port34 Voltage | RO | 2 bytes | Unit:0.1V
3228 | Slave01 Outlet Port35 Voltage | RO | 2 bytes | Unit:0.1V
3229 | Slave01 Outlet Port36 Voltage | RO | 2 bytes | Unit:0.1V
3230 | Slave01 Outlet Port37 Voltage | RO | 2 bytes | Unit:0.1V
3231 | Slave01 Outlet Port38 Voltage | RO | 2 bytes | Unit:0.1V
3232 | Slave01 Outlet Port39 Voltage | RO | 2 bytes | Unit:0.1V
3233 | Slave01 Outlet Port40 Voltage | RO | 2 bytes | Unit:0.1V
3234 | Slave01 Outlet Port41 Voltage | RO | 2 bytes | Unit:0.1V
3235 | Slave01 Outlet Port42 Voltage | RO | 2 bytes | Unit:0.1V
3236 | Slave02 Outlet Port01 Voltage | RO | 2 bytes | Unit:0.1V
3237 | Slave02 Outlet Port02 Voltage | RO | 2 bytes | Unit:0.1V
3238 | Slave02 Outlet Port03 Voltage | RO | 2 bytes | Unit:0.1V
3239 | Slave02 Outlet Port04 Voltage | RO | 2 bytes | Unit:0.1V
3240 | Slave02 Outlet Port05 Voltage | RO | 2 bytes | Unit:0.1V
3241 | Slave02 Outlet Port06 Voltage | RO | 2 bytes | Unit:0.1V
3242 | Slave02 Outlet Port07 Voltage | RO | 2 bytes | Unit:0.1V
3243 | Slave02 Outlet Port08 Voltage | RO | 2 bytes | Unit:0.1V
3244 | Slave02 Outlet Port09 Voltage | RO | 2 bytes | Unit:0.1V
3245 | Slave02 Outlet Port10 Voltage | RO | 2 bytes | Unit:0.1V
3246 | Slave02 Outlet Port11 Voltage | RO | 2 bytes | Unit:0.1V
3247 | Slave02 Outlet Port12 Voltage | RO | 2 bytes | Unit:0.1V
3248 | Slave02 Outlet Port13 Voltage | RO | 2 bytes | Unit:0.1V
3249 | Slave02 Outlet Port14 Voltage | RO | 2 bytes | Unit:0.1V
3250 | Slave02 Outlet Port15 Voltage | RO | 2 bytes | Unit:0.1V
3251 | Slave02 Outlet Port16 Voltage | RO | 2 bytes | Unit:0.1V
3252 | Slave02 Outlet Port17 Voltage | RO | 2 bytes | Unit:0.1V
3253 | Slave02 Outlet Port18 Voltage | RO | 2 bytes | Unit:0.1V
3254 | Slave02 Outlet Port19 Voltage | RO | 2 bytes | Unit:0.1V
3255 | Slave02 Outlet Port20 Voltage | RO | 2 bytes | Unit:0.1V
3256 | Slave02 Outlet Port21 Voltage | RO | 2 bytes | Unit:0.1V
3257 | Slave02 Outlet Port22 Voltage | RO | 2 bytes | Unit:0.1V
3258 | Slave02 Outlet Port23 Voltage | RO | 2 bytes | Unit:0.1V
3259 | Slave02 Outlet Port24 Voltage | RO | 2 bytes | Unit:0.1V
3260 | Slave02 Outlet Port25 Voltage | RO | 2 bytes | Unit:0.1V
3261 | Slave02 Outlet Port26 Voltage | RO | 2 bytes | Unit:0.1V
3262 | Slave02 Outlet Port27 Voltage | RO | 2 bytes | Unit:0.1V
3263 | Slave02 Outlet Port28 Voltage | RO | 2 bytes | Unit:0.1V
3264 | Slave02 Outlet Port29 Voltage | RO | 2 bytes | Unit:0.1V
3265 | Slave02 Outlet Port30 Voltage | RO | 2 bytes | Unit:0.1V
3266 | Slave02 Outlet Port31 Voltage | RO | 2 bytes | Unit:0.1V
3267 | Slave02 Outlet Port32 Voltage | RO | 2 bytes | Unit:0.1V
3268 | Slave02 Outlet Port33 Voltage | RO | 2 bytes | Unit:0.1V
3269 | Slave02 Outlet Port34 Voltage | RO | 2 bytes | Unit:0.1V
3270 | Slave02 Outlet Port35 Voltage | RO | 2 bytes | Unit:0.1V
3271 | Slave02 Outlet Port36 Voltage | RO | 2 bytes | Unit:0.1V
3272 | Slave02 Outlet Port37 Voltage | RO | 2 bytes | Unit:0.1V
3273 | Slave02 Outlet Port38 Voltage | RO | 2 bytes | Unit:0.1V
3274 | Slave02 Outlet Port39 Voltage | RO | 2 bytes | Unit:0.1V
3275 | Slave02 Outlet Port40 Voltage | RO | 2 bytes | Unit:0.1V
3276 | Slave02 Outlet Port41 Voltage | RO | 2 bytes | Unit:0.1V
3277 | Slave02 Outlet Port42 Voltage | RO | 2 bytes | Unit:0.1V
3278 | Slave03 Outlet Port01 Voltage | RO | 2 bytes | Unit:0.1V
3279 | Slave03 Outlet Port02 Voltage | RO | 2 bytes | Unit:0.1V
3280 | Slave03 Outlet Port03 Voltage | RO | 2 bytes | Unit:0.1V
3281 | Slave03 Outlet Port04 Voltage | RO | 2 bytes | Unit:0.1V
3282 | Slave03 Outlet Port05 Voltage | RO | 2 bytes | Unit:0.1V
3283 | Slave03 Outlet Port06 Voltage | RO | 2 bytes | Unit:0.1V
3284 | Slave03 Outlet Port07 Voltage | RO | 2 bytes | Unit:0.1V
3285 | Slave03 Outlet Port08 Voltage | RO | 2 bytes | Unit:0.1V
3286 | Slave03 Outlet Port09 Voltage | RO | 2 bytes | Unit:0.1V
3287 | Slave03 Outlet Port10 Voltage | RO | 2 bytes | Unit:0.1V
3288 | Slave03 Outlet Port11 Voltage | RO | 2 bytes | Unit:0.1V
3289 | Slave03 Outlet Port12 Voltage | RO | 2 bytes | Unit:0.1V
3290 | Slave03 Outlet Port13 Voltage | RO | 2 bytes | Unit:0.1V
3291 | Slave03 Outlet Port14 Voltage | RO | 2 bytes | Unit:0.1V
3292 | Slave03 Outlet Port15 Voltage | RO | 2 bytes | Unit:0.1V
3293 | Slave03 Outlet Port16 Voltage | RO | 2 bytes | Unit:0.1V
3294 | Slave03 Outlet Port17 Voltage | RO | 2 bytes | Unit:0.1V
3295 | Slave03 Outlet Port18 Voltage | RO | 2 bytes | Unit:0.1V
3296 | Slave03 Outlet Port19 Voltage | RO | 2 bytes | Unit:0.1V
3297 | Slave03 Outlet Port20 Voltage | RO | 2 bytes | Unit:0.1V
3298 | Slave03 Outlet Port21 Voltage | RO | 2 bytes | Unit:0.1V
3299 | Slave03 Outlet Port22 Voltage | RO | 2 bytes | Unit:0.1V
3300 | Slave03 Outlet Port23 Voltage | RO | 2 bytes | Unit:0.1V
3301 | Slave03 Outlet Port24 Voltage | RO | 2 bytes | Unit:0.1V
3302 | Slave03 Outlet Port25 Voltage | RO | 2 bytes | Unit:0.1V
3303 | Slave03 Outlet Port26 Voltage | RO | 2 bytes | Unit:0.1V
3304 | Slave03 Outlet Port27 Voltage | RO | 2 bytes | Unit:0.1V
3305 | Slave03 Outlet Port28 Voltage | RO | 2 bytes | Unit:0.1V
3306 | Slave03 Outlet Port29 Voltage | RO | 2 bytes | Unit:0.1V
3307 | Slave03 Outlet Port30 Voltage | RO | 2 bytes | Unit:0.1V
3308 | Slave03 Outlet Port31 Voltage | RO | 2 bytes | Unit:0.1V
3309 | Slave03 Outlet Port32 Voltage | RO | 2 bytes | Unit:0.1V
3310 | Slave03 Outlet Port33 Voltage | RO | 2 bytes | Unit:0.1V
3311 | Slave03 Outlet Port34 Voltage | RO | 2 bytes | Unit:0.1V
3312 | Slave03 Outlet Port35 Voltage | RO | 2 bytes | Unit:0.1V
3313 | Slave03 Outlet Port36 Voltage | RO | 2 bytes | Unit:0.1V
3314 | Slave03 Outlet Port37 Voltage | RO | 2 bytes | Unit:0.1V
3315 | Slave03 Outlet Port38 Voltage | RO | 2 bytes | Unit:0.1V
3316 | Slave03 Outlet Port39 Voltage | RO | 2 bytes | Unit:0.1V
3317 | Slave03 Outlet Port40 Voltage | RO | 2 bytes | Unit:0.1V
3318 | Slave03 Outlet Port41 Voltage | RO | 2 bytes | Unit:0.1V
3319 | Slave03 Outlet Port42 Voltage | RO | 2 bytes | Unit:0.1V
3320 | Slave04 Outlet Port01 Voltage | RO | 2 bytes | Unit:0.1V
3321 | Slave04 Outlet Port02 Voltage | RO | 2 bytes | Unit:0.1V
3322 | Slave04 Outlet Port03 Voltage | RO | 2 bytes | Unit:0.1V
3323 | Slave04 Outlet Port04 Voltage | RO | 2 bytes | Unit:0.1V
3324 | Slave04 Outlet Port05 Voltage | RO | 2 bytes | Unit:0.1V
3325 | Slave04 Outlet Port06 Voltage | RO | 2 bytes | Unit:0.1V
3326 | Slave04 Outlet Port07 Voltage | RO | 2 bytes | Unit:0.1V
3327 | Slave04 Outlet Port08 Voltage | RO | 2 bytes | Unit:0.1V
3328 | Slave04 Outlet Port09 Voltage | RO | 2 bytes | Unit:0.1V
3329 | Slave04 Outlet Port10 Voltage | RO | 2 bytes | Unit:0.1V
3330 | Slave04 Outlet Port11 Voltage | RO | 2 bytes | Unit:0.1V
3331 | Slave04 Outlet Port12 Voltage | RO | 2 bytes | Unit:0.1V
3332 | Slave04 Outlet Port13 Voltage | RO | 2 bytes | Unit:0.1V
3333 | Slave04 Outlet Port14 Voltage | RO | 2 bytes | Unit:0.1V
3334 | Slave04 Outlet Port15 Voltage | RO | 2 bytes | Unit:0.1V
3335 | Slave04 Outlet Port16 Voltage | RO | 2 bytes | Unit:0.1V
3336 | Slave04 Outlet Port17 Voltage | RO | 2 bytes | Unit:0.1V
3337 | Slave04 Outlet Port18 Voltage | RO | 2 bytes | Unit:0.1V
3338 | Slave04 Outlet Port19 Voltage | RO | 2 bytes | Unit:0.1V
3339 | Slave04 Outlet Port20 Voltage | RO | 2 bytes | Unit:0.1V
3340 | Slave04 Outlet Port21 Voltage | RO | 2 bytes | Unit:0.1V
3341 | Slave04 Outlet Port22 Voltage | RO | 2 bytes | Unit:0.1V
3342 | Slave04 Outlet Port23 Voltage | RO | 2 bytes | Unit:0.1V
3343 | Slave04 Outlet Port24 Voltage | RO | 2 bytes | Unit:0.1V
3344 | Slave04 Outlet Port25 Voltage | RO | 2 bytes | Unit:0.1V
3345 | Slave04 Outlet Port26 Voltage | RO | 2 bytes | Unit:0.1V
3346 | Slave04 Outlet Port27 Voltage | RO | 2 bytes | Unit:0.1V
3347 | Slave04 Outlet Port28 Voltage | RO | 2 bytes | Unit:0.1V
3348 | Slave04 Outlet Port29 Voltage | RO | 2 bytes | Unit:0.1V
3349 | Slave04 Outlet Port30 Voltage | RO | 2 bytes | Unit:0.1V
3350 | Slave04 Outlet Port31 Voltage | RO | 2 bytes | Unit:0.1V
3351 | Slave04 Outlet Port32 Voltage | RO | 2 bytes | Unit:0.1V
3352 | Slave04 Outlet Port33 Voltage | RO | 2 bytes | Unit:0.1V
3353 | Slave04 Outlet Port34 Voltage | RO | 2 bytes | Unit:0.1V
3354 | Slave04 Outlet Port35 Voltage | RO | 2 bytes | Unit:0.1V
3355 | Slave04 Outlet Port36 Voltage | RO | 2 bytes | Unit:0.1V
3356 | Slave04 Outlet Port37 Voltage | RO | 2 bytes | Unit:0.1V
3357 | Slave04 Outlet Port38 Voltage | RO | 2 bytes | Unit:0.1V
3358 | Slave04 Outlet Port39 Voltage | RO | 2 bytes | Unit:0.1V
3359 | Slave04 Outlet Port40 Voltage | RO | 2 bytes | Unit:0.1V
3360 | Slave04 Outlet Port41 Voltage | RO | 2 bytes | Unit:0.1V
3361 | Slave04 Outlet Port42 Voltage | RO | 2 bytes | Unit:0.1V
3362 | Slave05 Outlet Port01 Voltage | RO | 2 bytes | Unit:0.1V
3363 | Slave05 Outlet Port02 Voltage | RO | 2 bytes | Unit:0.1V
3364 | Slave05 Outlet Port03 Voltage | RO | 2 bytes | Unit:0.1V
3365 | Slave05 Outlet Port04 Voltage | RO | 2 bytes | Unit:0.1V
3366 | Slave05 Outlet Port05 Voltage | RO | 2 bytes | Unit:0.1V
3367 | Slave05 Outlet Port06 Voltage | RO | 2 bytes | Unit:0.1V
3368 | Slave05 Outlet Port07 Voltage | RO | 2 bytes | Unit:0.1V
3369 | Slave05 Outlet Port08 Voltage | RO | 2 bytes | Unit:0.1V
3370 | Slave05 Outlet Port09 Voltage | RO | 2 bytes | Unit:0.1V
3371 | Slave05 Outlet Port10 Voltage | RO | 2 bytes | Unit:0.1V
3372 | Slave05 Outlet Port11 Voltage | RO | 2 bytes | Unit:0.1V
3373 | Slave05 Outlet Port12 Voltage | RO | 2 bytes | Unit:0.1V
3374 | Slave05 Outlet Port13 Voltage | RO | 2 bytes | Unit:0.1V
3375 | Slave05 Outlet Port14 Voltage | RO | 2 bytes | Unit:0.1V
3376 | Slave05 Outlet Port15 Voltage | RO | 2 bytes | Unit:0.1V
3377 | Slave05 Outlet Port16 Voltage | RO | 2 bytes | Unit:0.1V
3378 | Slave05 Outlet Port17 Voltage | RO | 2 bytes | Unit:0.1V
3379 | Slave05 Outlet Port18 Voltage | RO | 2 bytes | Unit:0.1V
3380 | Slave05 Outlet Port19 Voltage | RO | 2 bytes | Unit:0.1V
3381 | Slave05 Outlet Port20 Voltage | RO | 2 bytes | Unit:0.1V
3382 | Slave05 Outlet Port21 Voltage | RO | 2 bytes | Unit:0.1V
3383 | Slave05 Outlet Port22 Voltage | RO | 2 bytes | Unit:0.1V
3384 | Slave05 Outlet Port23 Voltage | RO | 2 bytes | Unit:0.1V
3385 | Slave05 Outlet Port24 Voltage | RO | 2 bytes | Unit:0.1V
3386 | Slave05 Outlet Port25 Voltage | RO | 2 bytes | Unit:0.1V
3387 | Slave05 Outlet Port26 Voltage | RO | 2 bytes | Unit:0.1V
3388 | Slave05 Outlet Port27 Voltage | RO | 2 bytes | Unit:0.1V
3389 | Slave05 Outlet Port28 Voltage | RO | 2 bytes | Unit:0.1V
3390 | Slave05 Outlet Port29 Voltage | RO | 2 bytes | Unit:0.1V
3391 | Slave05 Outlet Port30 Voltage | RO | 2 bytes | Unit:0.1V
3392 | Slave05 Outlet Port31 Voltage | RO | 2 bytes | Unit:0.1V
3393 | Slave05 Outlet Port32 Voltage | RO | 2 bytes | Unit:0.1V
3394 | Slave05 Outlet Port33 Voltage | RO | 2 bytes | Unit:0.1V
3395 | Slave05 Outlet Port34 Voltage | RO | 2 bytes | Unit:0.1V
3396 | Slave05 Outlet Port35 Voltage | RO | 2 bytes | Unit:0.1V
3397 | Slave05 Outlet Port36 Voltage | RO | 2 bytes | Unit:0.1V
3398 | Slave05 Outlet Port37 Voltage | RO | 2 bytes | Unit:0.1V
3399 | Slave05 Outlet Port38 Voltage | RO | 2 bytes | Unit:0.1V
3400 | Slave05 Outlet Port39 Voltage | RO | 2 bytes | Unit:0.1V
3401 | Slave05 Outlet Port40 Voltage | RO | 2 bytes | Unit:0.1V
3402 | Slave05 Outlet Port41 Voltage | RO | 2 bytes | Unit:0.1V
3403 | Slave05 Outlet Port42 Voltage | RO | 2 bytes | Unit:0.1V
3404 | Slave06 Outlet Port01 Voltage | RO | 2 bytes | Unit:0.1V
3405 | Slave06 Outlet Port02 Voltage | RO | 2 bytes | Unit:0.1V
3406 | Slave06 Outlet Port03 Voltage | RO | 2 bytes | Unit:0.1V
3407 | Slave06 Outlet Port04 Voltage | RO | 2 bytes | Unit:0.1V
3408 | Slave06 Outlet Port05 Voltage | RO | 2 bytes | Unit:0.1V
3409 | Slave06 Outlet Port06 Voltage | RO | 2 bytes | Unit:0.1V
3410 | Slave06 Outlet Port07 Voltage | RO | 2 bytes | Unit:0.1V
3411 | Slave06 Outlet Port08 Voltage | RO | 2 bytes | Unit:0.1V
3412 | Slave06 Outlet Port09 Voltage | RO | 2 bytes | Unit:0.1V
3413 | Slave06 Outlet Port10 Voltage | RO | 2 bytes | Unit:0.1V
3414 | Slave06 Outlet Port11 Voltage | RO | 2 bytes | Unit:0.1V
3415 | Slave06 Outlet Port12 Voltage | RO | 2 bytes | Unit:0.1V
3416 | Slave06 Outlet Port13 Voltage | RO | 2 bytes | Unit:0.1V
3417 | Slave06 Outlet Port14 Voltage | RO | 2 bytes | Unit:0.1V
3418 | Slave06 Outlet Port15 Voltage | RO | 2 bytes | Unit:0.1V
3419 | Slave06 Outlet Port16 Voltage | RO | 2 bytes | Unit:0.1V
3420 | Slave06 Outlet Port17 Voltage | RO | 2 bytes | Unit:0.1V
3421 | Slave06 Outlet Port18 Voltage | RO | 2 bytes | Unit:0.1V
3422 | Slave06 Outlet Port19 Voltage | RO | 2 bytes | Unit:0.1V
3423 | Slave06 Outlet Port20 Voltage | RO | 2 bytes | Unit:0.1V
3424 | Slave06 Outlet Port21 Voltage | RO | 2 bytes | Unit:0.1V
3425 | Slave06 Outlet Port22 Voltage | RO | 2 bytes | Unit:0.1V
3426 | Slave06 Outlet Port23 Voltage | RO | 2 bytes | Unit:0.1V
3427 | Slave06 Outlet Port24 Voltage | RO | 2 bytes | Unit:0.1V
3428 | Slave06 Outlet Port25 Voltage | RO | 2 bytes | Unit:0.1V
3429 | Slave06 Outlet Port26 Voltage | RO | 2 bytes | Unit:0.1V
3430 | Slave06 Outlet Port27 Voltage | RO | 2 bytes | Unit:0.1V
3431 | Slave06 Outlet Port28 Voltage | RO | 2 bytes | Unit:0.1V
3432 | Slave06 Outlet Port29 Voltage | RO | 2 bytes | Unit:0.1V
3433 | Slave06 Outlet Port30 Voltage | RO | 2 bytes | Unit:0.1V
3434 | Slave06 Outlet Port31 Voltage | RO | 2 bytes | Unit:0.1V
3435 | Slave06 Outlet Port32 Voltage | RO | 2 bytes | Unit:0.1V
3436 | Slave06 Outlet Port33 Voltage | RO | 2 bytes | Unit:0.1V
3437 | Slave06 Outlet Port34 Voltage | RO | 2 bytes | Unit:0.1V
3438 | Slave06 Outlet Port35 Voltage | RO | 2 bytes | Unit:0.1V
3439 | Slave06 Outlet Port36 Voltage | RO | 2 bytes | Unit:0.1V
3440 | Slave06 Outlet Port37 Voltage | RO | 2 bytes | Unit:0.1V
3441 | Slave06 Outlet Port38 Voltage | RO | 2 bytes | Unit:0.1V
3442 | Slave06 Outlet Port39 Voltage | RO | 2 bytes | Unit:0.1V
3443 | Slave06 Outlet Port40 Voltage | RO | 2 bytes | Unit:0.1V
3444 | Slave06 Outlet Port41 Voltage | RO | 2 bytes | Unit:0.1V
3445 | Slave06 Outlet Port42 Voltage | RO | 2 bytes | Unit:0.1V
3446 | Slave07 Outlet Port01 Voltage | RO | 2 bytes | Unit:0.1V
3447 | Slave07 Outlet Port02 Voltage | RO | 2 bytes | Unit:0.1V
3448 | Slave07 Outlet Port03 Voltage | RO | 2 bytes | Unit:0.1V
3449 | Slave07 Outlet Port04 Voltage | RO | 2 bytes | Unit:0.1V
3450 | Slave07 Outlet Port05 Voltage | RO | 2 bytes | Unit:0.1V
3451 | Slave07 Outlet Port06 Voltage | RO | 2 bytes | Unit:0.1V
3452 | Slave07 Outlet Port07 Voltage | RO | 2 bytes | Unit:0.1V
3453 | Slave07 Outlet Port08 Voltage | RO | 2 bytes | Unit:0.1V
3454 | Slave07 Outlet Port09 Voltage | RO | 2 bytes | Unit:0.1V
3455 | Slave07 Outlet Port10 Voltage | RO | 2 bytes | Unit:0.1V
3456 | Slave07 Outlet Port11 Voltage | RO | 2 bytes | Unit:0.1V
3457 | Slave07 Outlet Port12 Voltage | RO | 2 bytes | Unit:0.1V
3458 | Slave07 Outlet Port13 Voltage | RO | 2 bytes | Unit:0.1V
3459 | Slave07 Outlet Port14 Voltage | RO | 2 bytes | Unit:0.1V
3460 | Slave07 Outlet Port15 Voltage | RO | 2 bytes | Unit:0.1V
3461 | Slave07 Outlet Port16 Voltage | RO | 2 bytes | Unit:0.1V
3462 | Slave07 Outlet Port17 Voltage | RO | 2 bytes | Unit:0.1V
3463 | Slave07 Outlet Port18 Voltage | RO | 2 bytes | Unit:0.1V
3464 | Slave07 Outlet Port19 Voltage | RO | 2 bytes | Unit:0.1V
3465 | Slave07 Outlet Port20 Voltage | RO | 2 bytes | Unit:0.1V
3466 | Slave07 Outlet Port21 Voltage | RO | 2 bytes | Unit:0.1V
3467 | Slave07 Outlet Port22 Voltage | RO | 2 bytes | Unit:0.1V
3468 | Slave07 Outlet Port23 Voltage | RO | 2 bytes | Unit:0.1V
3469 | Slave07 Outlet Port24 Voltage | RO | 2 bytes | Unit:0.1V
3470 | Slave07 Outlet Port25 Voltage | RO | 2 bytes | Unit:0.1V
3471 | Slave07 Outlet Port26 Voltage | RO | 2 bytes | Unit:0.1V
3472 | Slave07 Outlet Port27 Voltage | RO | 2 bytes | Unit:0.1V
3473 | Slave07 Outlet Port28 Voltage | RO | 2 bytes | Unit:0.1V
3474 | Slave07 Outlet Port29 Voltage | RO | 2 bytes | Unit:0.1V
3475 | Slave07 Outlet Port30 Voltage | RO | 2 bytes | Unit:0.1V
3476 | Slave07 Outlet Port31 Voltage | RO | 2 bytes | Unit:0.1V
3477 | Slave07 Outlet Port32 Voltage | RO | 2 bytes | Unit:0.1V
3478 | Slave07 Outlet Port33 Voltage | RO | 2 bytes | Unit:0.1V
3479 | Slave07 Outlet Port34 Voltage | RO | 2 bytes | Unit:0.1V
3480 | Slave07 Outlet Port35 Voltage | RO | 2 bytes | Unit:0.1V
3481 | Slave07 Outlet Port36 Voltage | RO | 2 bytes | Unit:0.1V
3482 | Slave07 Outlet Port37 Voltage | RO | 2 bytes | Unit:0.1V
3483 | Slave07 Outlet Port38 Voltage | RO | 2 bytes | Unit:0.1V
3484 | Slave07 Outlet Port39 Voltage | RO | 2 bytes | Unit:0.1V
3485 | Slave07 Outlet Port40 Voltage | RO | 2 bytes | Unit:0.1V
3486 | Slave07 Outlet Port41 Voltage | RO | 2 bytes | Unit:0.1V
3487 | Slave07 Outlet Port42 Voltage | RO | 2 bytes | Unit:0.1V
3488 | Slave08 Outlet Port01 Voltage | RO | 2 bytes | Unit:0.1V
3489 | Slave08 Outlet Port02 Voltage | RO | 2 bytes | Unit:0.1V
3490 | Slave08 Outlet Port03 Voltage | RO | 2 bytes | Unit:0.1V
3491 | Slave08 Outlet Port04 Voltage | RO | 2 bytes | Unit:0.1V
3492 | Slave08 Outlet Port05 Voltage | RO | 2 bytes | Unit:0.1V
3493 | Slave08 Outlet Port06 Voltage | RO | 2 bytes | Unit:0.1V
3494 | Slave08 Outlet Port07 Voltage | RO | 2 bytes | Unit:0.1V
3495 | Slave08 Outlet Port08 Voltage | RO | 2 bytes | Unit:0.1V
3496 | Slave08 Outlet Port09 Voltage | RO | 2 bytes | Unit:0.1V
3497 | Slave08 Outlet Port10 Voltage | RO | 2 bytes | Unit:0.1V
3498 | Slave08 Outlet Port11 Voltage | RO | 2 bytes | Unit:0.1V
3499 | Slave08 Outlet Port12 Voltage | RO | 2 bytes | Unit:0.1V
3500 | Slave08 Outlet Port13 Voltage | RO | 2 bytes | Unit:0.1V
3501 | Slave08 Outlet Port14 Voltage | RO | 2 bytes | Unit:0.1V
3502 | Slave08 Outlet Port15 Voltage | RO | 2 bytes | Unit:0.1V
3503 | Slave08 Outlet Port16 Voltage | RO | 2 bytes | Unit:0.1V
3504 | Slave08 Outlet Port17 Voltage | RO | 2 bytes | Unit:0.1V
3505 | Slave08 Outlet Port18 Voltage | RO | 2 bytes | Unit:0.1V
3506 | Slave08 Outlet Port19 Voltage | RO | 2 bytes | Unit:0.1V
3507 | Slave08 Outlet Port20 Voltage | RO | 2 bytes | Unit:0.1V
3508 | Slave08 Outlet Port21 Voltage | RO | 2 bytes | Unit:0.1V
3509 | Slave08 Outlet Port22 Voltage | RO | 2 bytes | Unit:0.1V
3510 | Slave08 Outlet Port23 Voltage | RO | 2 bytes | Unit:0.1V
3511 | Slave08 Outlet Port24 Voltage | RO | 2 bytes | Unit:0.1V
3512 | Slave08 Outlet Port25 Voltage | RO | 2 bytes | Unit:0.1V
3513 | Slave08 Outlet Port26 Voltage | RO | 2 bytes | Unit:0.1V
3514 | Slave08 Outlet Port27 Voltage | RO | 2 bytes | Unit:0.1V
3515 | Slave08 Outlet Port28 Voltage | RO | 2 bytes | Unit:0.1V
3516 | Slave08 Outlet Port29 Voltage | RO | 2 bytes | Unit:0.1V
3517 | Slave08 Outlet Port30 Voltage | RO | 2 bytes | Unit:0.1V
3518 | Slave08 Outlet Port31 Voltage | RO | 2 bytes | Unit:0.1V
3519 | Slave08 Outlet Port32 Voltage | RO | 2 bytes | Unit:0.1V
3520 | Slave08 Outlet Port33 Voltage | RO | 2 bytes | Unit:0.1V
3521 | Slave08 Outlet Port34 Voltage | RO | 2 bytes | Unit:0.1V
3522 | Slave08 Outlet Port35 Voltage | RO | 2 bytes | Unit:0.1V
3523 | Slave08 Outlet Port36 Voltage | RO | 2 bytes | Unit:0.1V
3524 | Slave08 Outlet Port37 Voltage | RO | 2 bytes | Unit:0.1V
3525 | Slave08 Outlet Port38 Voltage | RO | 2 bytes | Unit:0.1V
3526 | Slave08 Outlet Port39 Voltage | RO | 2 bytes | Unit:0.1V
3527 | Slave08 Outlet Port40 Voltage | RO | 2 bytes | Unit:0.1V
3528 | Slave08 Outlet Port41 Voltage | RO | 2 bytes | Unit:0.1V
3529 | Slave08 Outlet Port42 Voltage | RO | 2 bytes | Unit:0.1V
3530 | Slave09 Outlet Port01 Voltage | RO | 2 bytes | Unit:0.1V
3531 | Slave09 Outlet Port02 Voltage | RO | 2 bytes | Unit:0.1V
3532 | Slave09 Outlet Port03 Voltage | RO | 2 bytes | Unit:0.1V
3533 | Slave09 Outlet Port04 Voltage | RO | 2 bytes | Unit:0.1V
3534 | Slave09 Outlet Port05 Voltage | RO | 2 bytes | Unit:0.1V
3535 | Slave09 Outlet Port06 Voltage | RO | 2 bytes | Unit:0.1V
3536 | Slave09 Outlet Port07 Voltage | RO | 2 bytes | Unit:0.1V
3537 | Slave09 Outlet Port08 Voltage | RO | 2 bytes | Unit:0.1V
3538 | Slave09 Outlet Port09 Voltage | RO | 2 bytes | Unit:0.1V
3539 | Slave09 Outlet Port10 Voltage | RO | 2 bytes | Unit:0.1V
3540 | Slave09 Outlet Port11 Voltage | RO | 2 bytes | Unit:0.1V
3541 | Slave09 Outlet Port12 Voltage | RO | 2 bytes | Unit:0.1V
3542 | Slave09 Outlet Port13 Voltage | RO | 2 bytes | Unit:0.1V
3543 | Slave09 Outlet Port14 Voltage | RO | 2 bytes | Unit:0.1V
3544 | Slave09 Outlet Port15 Voltage | RO | 2 bytes | Unit:0.1V
3545 | Slave09 Outlet Port16 Voltage | RO | 2 bytes | Unit:0.1V
3546 | Slave09 Outlet Port17 Voltage | RO | 2 bytes | Unit:0.1V
3547 | Slave09 Outlet Port18 Voltage | RO | 2 bytes | Unit:0.1V
3548 | Slave09 Outlet Port19 Voltage | RO | 2 bytes | Unit:0.1V
3549 | Slave09 Outlet Port20 Voltage | RO | 2 bytes | Unit:0.1V
3550 | Slave09 Outlet Port21 Voltage | RO | 2 bytes | Unit:0.1V
3551 | Slave09 Outlet Port22 Voltage | RO | 2 bytes | Unit:0.1V
3552 | Slave09 Outlet Port23 Voltage | RO | 2 bytes | Unit:0.1V
3553 | Slave09 Outlet Port24 Voltage | RO | 2 bytes | Unit:0.1V
3554 | Slave09 Outlet Port25 Voltage | RO | 2 bytes | Unit:0.1V
3555 | Slave09 Outlet Port26 Voltage | RO | 2 bytes | Unit:0.1V
3556 | Slave09 Outlet Port27 Voltage | RO | 2 bytes | Unit:0.1V
3557 | Slave09 Outlet Port28 Voltage | RO | 2 bytes | Unit:0.1V
3558 | Slave09 Outlet Port29 Voltage | RO | 2 bytes | Unit:0.1V
3559 | Slave09 Outlet Port30 Voltage | RO | 2 bytes | Unit:0.1V
3560 | Slave09 Outlet Port31 Voltage | RO | 2 bytes | Unit:0.1V
3561 | Slave09 Outlet Port32 Voltage | RO | 2 bytes | Unit:0.1V
3562 | Slave09 Outlet Port33 Voltage | RO | 2 bytes | Unit:0.1V
3563 | Slave09 Outlet Port34 Voltage | RO | 2 bytes | Unit:0.1V
3564 | Slave09 Outlet Port35 Voltage | RO | 2 bytes | Unit:0.1V
3565 | Slave09 Outlet Port36 Voltage | RO | 2 bytes | Unit:0.1V
3566 | Slave09 Outlet Port37 Voltage | RO | 2 bytes | Unit:0.1V
3567 | Slave09 Outlet Port38 Voltage | RO | 2 bytes | Unit:0.1V
3568 | Slave09 Outlet Port39 Voltage | RO | 2 bytes | Unit:0.1V
3569 | Slave09 Outlet Port40 Voltage | RO | 2 bytes | Unit:0.1V
3570 | Slave09 Outlet Port41 Voltage | RO | 2 bytes | Unit:0.1V
3571 | Slave09 Outlet Port42 Voltage | RO | 2 bytes | Unit:0.1V
3572 | Slave10 Outlet Port01 Voltage | RO | 2 bytes | Unit:0.1V
3573 | Slave10 Outlet Port02 Voltage | RO | 2 bytes | Unit:0.1V
3574 | Slave10 Outlet Port03 Voltage | RO | 2 bytes | Unit:0.1V
3575 | Slave10 Outlet Port04 Voltage | RO | 2 bytes | Unit:0.1V
3576 | Slave10 Outlet Port05 Voltage | RO | 2 bytes | Unit:0.1V
3577 | Slave10 Outlet Port06 Voltage | RO | 2 bytes | Unit:0.1V
3578 | Slave10 Outlet Port07 Voltage | RO | 2 bytes | Unit:0.1V
3579 | Slave10 Outlet Port08 Voltage | RO | 2 bytes | Unit:0.1V
3580 | Slave10 Outlet Port09 Voltage | RO | 2 bytes | Unit:0.1V
3581 | Slave10 Outlet Port10 Voltage | RO | 2 bytes | Unit:0.1V
3582 | Slave10 Outlet Port11 Voltage | RO | 2 bytes | Unit:0.1V
3583 | Slave10 Outlet Port12 Voltage | RO | 2 bytes | Unit:0.1V
3584 | Slave10 Outlet Port13 Voltage | RO | 2 bytes | Unit:0.1V
3585 | Slave10 Outlet Port14 Voltage | RO | 2 bytes | Unit:0.1V
3586 | Slave10 Outlet Port15 Voltage | RO | 2 bytes | Unit:0.1V
3587 | Slave10 Outlet Port16 Voltage | RO | 2 bytes | Unit:0.1V
3588 | Slave10 Outlet Port17 Voltage | RO | 2 bytes | Unit:0.1V
3589 | Slave10 Outlet Port18 Voltage | RO | 2 bytes | Unit:0.1V
3590 | Slave10 Outlet Port19 Voltage | RO | 2 bytes | Unit:0.1V
3591 | Slave10 Outlet Port20 Voltage | RO | 2 bytes | Unit:0.1V
3592 | Slave10 Outlet Port21 Voltage | RO | 2 bytes | Unit:0.1V
3593 | Slave10 Outlet Port22 Voltage | RO | 2 bytes | Unit:0.1V
3594 | Slave10 Outlet Port23 Voltage | RO | 2 bytes | Unit:0.1V
3595 | Slave10 Outlet Port24 Voltage | RO | 2 bytes | Unit:0.1V
3596 | Slave10 Outlet Port25 Voltage | RO | 2 bytes | Unit:0.1V
3597 | Slave10 Outlet Port26 Voltage | RO | 2 bytes | Unit:0.1V
3598 | Slave10 Outlet Port27 Voltage | RO | 2 bytes | Unit:0.1V
3599 | Slave10 Outlet Port28 Voltage | RO | 2 bytes | Unit:0.1V
3600 | Slave10 Outlet Port29 Voltage | RO | 2 bytes | Unit:0.1V
3601 | Slave10 Outlet Port30 Voltage | RO | 2 bytes | Unit:0.1V
3602 | Slave10 Outlet Port31 Voltage | RO | 2 bytes | Unit:0.1V
3603 | Slave10 Outlet Port32 Voltage | RO | 2 bytes | Unit:0.1V
3604 | Slave10 Outlet Port33 Voltage | RO | 2 bytes | Unit:0.1V
3605 | Slave10 Outlet Port34 Voltage | RO | 2 bytes | Unit:0.1V
3606 | Slave10 Outlet Port35 Voltage | RO | 2 bytes | Unit:0.1V
3607 | Slave10 Outlet Port36 Voltage | RO | 2 bytes | Unit:0.1V
3608 | Slave10 Outlet Port37 Voltage | RO | 2 bytes | Unit:0.1V
3609 | Slave10 Outlet Port38 Voltage | RO | 2 bytes | Unit:0.1V
3610 | Slave10 Outlet Port39 Voltage | RO | 2 bytes | Unit:0.1V
3611 | Slave10 Outlet Port40 Voltage | RO | 2 bytes | Unit:0.1V
3612 | Slave10 Outlet Port41 Voltage | RO | 2 bytes | Unit:0.1V
3613 | Slave10 Outlet Port42 Voltage | RO | 2 bytes | Unit:0.1V
3614 | Slave11 Outlet Port01 Voltage | RO | 2 bytes | Unit:0.1V
3615 | Slave11 Outlet Port02 Voltage | RO | 2 bytes | Unit:0.1V
3616 | Slave11 Outlet Port03 Voltage | RO | 2 bytes | Unit:0.1V
3617 | Slave11 Outlet Port04 Voltage | RO | 2 bytes | Unit:0.1V
3618 | Slave11 Outlet Port05 Voltage | RO | 2 bytes | Unit:0.1V
3619 | Slave11 Outlet Port06 Voltage | RO | 2 bytes | Unit:0.1V
3620 | Slave11 Outlet Port07 Voltage | RO | 2 bytes | Unit:0.1V
3621 | Slave11 Outlet Port08 Voltage | RO | 2 bytes | Unit:0.1V
3622 | Slave11 Outlet Port09 Voltage | RO | 2 bytes | Unit:0.1V
3623 | Slave11 Outlet Port10 Voltage | RO | 2 bytes | Unit:0.1V
3624 | Slave11 Outlet Port11 Voltage | RO | 2 bytes | Unit:0.1V
3625 | Slave11 Outlet Port12 Voltage | RO | 2 bytes | Unit:0.1V
3626 | Slave11 Outlet Port13 Voltage | RO | 2 bytes | Unit:0.1V
3627 | Slave11 Outlet Port14 Voltage | RO | 2 bytes | Unit:0.1V
3628 | Slave11 Outlet Port15 Voltage | RO | 2 bytes | Unit:0.1V
3629 | Slave11 Outlet Port16 Voltage | RO | 2 bytes | Unit:0.1V
3630 | Slave11 Outlet Port17 Voltage | RO | 2 bytes | Unit:0.1V
3631 | Slave11 Outlet Port18 Voltage | RO | 2 bytes | Unit:0.1V
3632 | Slave11 Outlet Port19 Voltage | RO | 2 bytes | Unit:0.1V
3633 | Slave11 Outlet Port20 Voltage | RO | 2 bytes | Unit:0.1V
3634 | Slave11 Outlet Port21 Voltage | RO | 2 bytes | Unit:0.1V
3635 | Slave11 Outlet Port22 Voltage | RO | 2 bytes | Unit:0.1V
3636 | Slave11 Outlet Port23 Voltage | RO | 2 bytes | Unit:0.1V
3637 | Slave11 Outlet Port24 Voltage | RO | 2 bytes | Unit:0.1V
3638 | Slave11 Outlet Port25 Voltage | RO | 2 bytes | Unit:0.1V
3639 | Slave11 Outlet Port26 Voltage | RO | 2 bytes | Unit:0.1V
3640 | Slave11 Outlet Port27 Voltage | RO | 2 bytes | Unit:0.1V
3641 | Slave11 Outlet Port28 Voltage | RO | 2 bytes | Unit:0.1V
3642 | Slave11 Outlet Port29 Voltage | RO | 2 bytes | Unit:0.1V
3643 | Slave11 Outlet Port30 Voltage | RO | 2 bytes | Unit:0.1V
3644 | Slave11 Outlet Port31 Voltage | RO | 2 bytes | Unit:0.1V
3645 | Slave11 Outlet Port32 Voltage | RO | 2 bytes | Unit:0.1V
3646 | Slave11 Outlet Port33 Voltage | RO | 2 bytes | Unit:0.1V
3647 | Slave11 Outlet Port34 Voltage | RO | 2 bytes | Unit:0.1V
3648 | Slave11 Outlet Port35 Voltage | RO | 2 bytes | Unit:0.1V
3649 | Slave11 Outlet Port36 Voltage | RO | 2 bytes | Unit:0.1V
3650 | Slave11 Outlet Port37 Voltage | RO | 2 bytes | Unit:0.1V
3651 | Slave11 Outlet Port38 Voltage | RO | 2 bytes | Unit:0.1V
3652 | Slave11 Outlet Port39 Voltage | RO | 2 bytes | Unit:0.1V
3653 | Slave11 Outlet Port40 Voltage | RO | 2 bytes | Unit:0.1V
3654 | Slave11 Outlet Port41 Voltage | RO | 2 bytes | Unit:0.1V
3655 | Slave11 Outlet Port42 Voltage | RO | 2 bytes | Unit:0.1V
3656 | Slave12 Outlet Port01 Voltage | RO | 2 bytes | Unit:0.1V
3657 | Slave12 Outlet Port02 Voltage | RO | 2 bytes | Unit:0.1V
3658 | Slave12 Outlet Port03 Voltage | RO | 2 bytes | Unit:0.1V
3659 | Slave12 Outlet Port04 Voltage | RO | 2 bytes | Unit:0.1V
3660 | Slave12 Outlet Port05 Voltage | RO | 2 bytes | Unit:0.1V
3661 | Slave12 Outlet Port06 Voltage | RO | 2 bytes | Unit:0.1V
3662 | Slave12 Outlet Port07 Voltage | RO | 2 bytes | Unit:0.1V
3663 | Slave12 Outlet Port08 Voltage | RO | 2 bytes | Unit:0.1V
3664 | Slave12 Outlet Port09 Voltage | RO | 2 bytes | Unit:0.1V
3665 | Slave12 Outlet Port10 Voltage | RO | 2 bytes | Unit:0.1V
3666 | Slave12 Outlet Port11 Voltage | RO | 2 bytes | Unit:0.1V
3667 | Slave12 Outlet Port12 Voltage | RO | 2 bytes | Unit:0.1V
3668 | Slave12 Outlet Port13 Voltage | RO | 2 bytes | Unit:0.1V
3669 | Slave12 Outlet Port14 Voltage | RO | 2 bytes | Unit:0.1V
3670 | Slave12 Outlet Port15 Voltage | RO | 2 bytes | Unit:0.1V
3671 | Slave12 Outlet Port16 Voltage | RO | 2 bytes | Unit:0.1V
3672 | Slave12 Outlet Port17 Voltage | RO | 2 bytes | Unit:0.1V
3673 | Slave12 Outlet Port18 Voltage | RO | 2 bytes | Unit:0.1V
3674 | Slave12 Outlet Port19 Voltage | RO | 2 bytes | Unit:0.1V
3675 | Slave12 Outlet Port20 Voltage | RO | 2 bytes | Unit:0.1V
3676 | Slave12 Outlet Port21 Voltage | RO | 2 bytes | Unit:0.1V
3677 | Slave12 Outlet Port22 Voltage | RO | 2 bytes | Unit:0.1V
3678 | Slave12 Outlet Port23 Voltage | RO | 2 bytes | Unit:0.1V
3679 | Slave12 Outlet Port24 Voltage | RO | 2 bytes | Unit:0.1V
3680 | Slave12 Outlet Port25 Voltage | RO | 2 bytes | Unit:0.1V
3681 | Slave12 Outlet Port26 Voltage | RO | 2 bytes | Unit:0.1V
3682 | Slave12 Outlet Port27 Voltage | RO | 2 bytes | Unit:0.1V
3683 | Slave12 Outlet Port28 Voltage | RO | 2 bytes | Unit:0.1V
3684 | Slave12 Outlet Port29 Voltage | RO | 2 bytes | Unit:0.1V
3685 | Slave12 Outlet Port30 Voltage | RO | 2 bytes | Unit:0.1V
3686 | Slave12 Outlet Port31 Voltage | RO | 2 bytes | Unit:0.1V
3687 | Slave12 Outlet Port32 Voltage | RO | 2 bytes | Unit:0.1V
3688 | Slave12 Outlet Port33 Voltage | RO | 2 bytes | Unit:0.1V
3689 | Slave12 Outlet Port34 Voltage | RO | 2 bytes | Unit:0.1V
3690 | Slave12 Outlet Port35 Voltage | RO | 2 bytes | Unit:0.1V
3691 | Slave12 Outlet Port36 Voltage | RO | 2 bytes | Unit:0.1V
3692 | Slave12 Outlet Port37 Voltage | RO | 2 bytes | Unit:0.1V
3693 | Slave12 Outlet Port38 Voltage | RO | 2 bytes | Unit:0.1V
3694 | Slave12 Outlet Port39 Voltage | RO | 2 bytes | Unit:0.1V
3695 | Slave12 Outlet Port40 Voltage | RO | 2 bytes | Unit:0.1V
3696 | Slave12 Outlet Port41 Voltage | RO | 2 bytes | Unit:0.1V
3697 | Slave12 Outlet Port42 Voltage | RO | 2 bytes | Unit:0.1V
3698 | Slave13 Outlet Port01 Voltage | RO | 2 bytes | Unit:0.1V
3699 | Slave13 Outlet Port02 Voltage | RO | 2 bytes | Unit:0.1V
3700 | Slave13 Outlet Port03 Voltage | RO | 2 bytes | Unit:0.1V
3701 | Slave13 Outlet Port04 Voltage | RO | 2 bytes | Unit:0.1V
3702 | Slave13 Outlet Port05 Voltage | RO | 2 bytes | Unit:0.1V
3703 | Slave13 Outlet Port06 Voltage | RO | 2 bytes | Unit:0.1V
3704 | Slave13 Outlet Port07 Voltage | RO | 2 bytes | Unit:0.1V
3705 | Slave13 Outlet Port08 Voltage | RO | 2 bytes | Unit:0.1V
3706 | Slave13 Outlet Port09 Voltage | RO | 2 bytes | Unit:0.1V
3707 | Slave13 Outlet Port10 Voltage | RO | 2 bytes | Unit:0.1V
3708 | Slave13 Outlet Port11 Voltage | RO | 2 bytes | Unit:0.1V
3709 | Slave13 Outlet Port12 Voltage | RO | 2 bytes | Unit:0.1V
3710 | Slave13 Outlet Port13 Voltage | RO | 2 bytes | Unit:0.1V
3711 | Slave13 Outlet Port14 Voltage | RO | 2 bytes | Unit:0.1V
3712 | Slave13 Outlet Port15 Voltage | RO | 2 bytes | Unit:0.1V
3713 | Slave13 Outlet Port16 Voltage | RO | 2 bytes | Unit:0.1V
3714 | Slave13 Outlet Port17 Voltage | RO | 2 bytes | Unit:0.1V
3715 | Slave13 Outlet Port18 Voltage | RO | 2 bytes | Unit:0.1V
3716 | Slave13 Outlet Port19 Voltage | RO | 2 bytes | Unit:0.1V
3717 | Slave13 Outlet Port20 Voltage | RO | 2 bytes | Unit:0.1V
3718 | Slave13 Outlet Port21 Voltage | RO | 2 bytes | Unit:0.1V
3719 | Slave13 Outlet Port22 Voltage | RO | 2 bytes | Unit:0.1V
3720 | Slave13 Outlet Port23 Voltage | RO | 2 bytes | Unit:0.1V
3721 | Slave13 Outlet Port24 Voltage | RO | 2 bytes | Unit:0.1V
3722 | Slave13 Outlet Port25 Voltage | RO | 2 bytes | Unit:0.1V
3723 | Slave13 Outlet Port26 Voltage | RO | 2 bytes | Unit:0.1V
3724 | Slave13 Outlet Port27 Voltage | RO | 2 bytes | Unit:0.1V
3725 | Slave13 Outlet Port28 Voltage | RO | 2 bytes | Unit:0.1V
3726 | Slave13 Outlet Port29 Voltage | RO | 2 bytes | Unit:0.1V
3727 | Slave13 Outlet Port30 Voltage | RO | 2 bytes | Unit:0.1V
3728 | Slave13 Outlet Port31 Voltage | RO | 2 bytes | Unit:0.1V
3729 | Slave13 Outlet Port32 Voltage | RO | 2 bytes | Unit:0.1V
3730 | Slave13 Outlet Port33 Voltage | RO | 2 bytes | Unit:0.1V
3731 | Slave13 Outlet Port34 Voltage | RO | 2 bytes | Unit:0.1V
3732 | Slave13 Outlet Port35 Voltage | RO | 2 bytes | Unit:0.1V
3733 | Slave13 Outlet Port36 Voltage | RO | 2 bytes | Unit:0.1V
3734 | Slave13 Outlet Port37 Voltage | RO | 2 bytes | Unit:0.1V
3735 | Slave13 Outlet Port38 Voltage | RO | 2 bytes | Unit:0.1V
3736 | Slave13 Outlet Port39 Voltage | RO | 2 bytes | Unit:0.1V
3737 | Slave13 Outlet Port40 Voltage | RO | 2 bytes | Unit:0.1V
3738 | Slave13 Outlet Port41 Voltage | RO | 2 bytes | Unit:0.1V
3739 | Slave13 Outlet Port42 Voltage | RO | 2 bytes | Unit:0.1V
3740 | Slave14 Outlet Port01 Voltage | RO | 2 bytes | Unit:0.1V
3741 | Slave14 Outlet Port02 Voltage | RO | 2 bytes | Unit:0.1V
3742 | Slave14 Outlet Port03 Voltage | RO | 2 bytes | Unit:0.1V
3743 | Slave14 Outlet Port04 Voltage | RO | 2 bytes | Unit:0.1V
3744 | Slave14 Outlet Port05 Voltage | RO | 2 bytes | Unit:0.1V
3745 | Slave14 Outlet Port06 Voltage | RO | 2 bytes | Unit:0.1V
3746 | Slave14 Outlet Port07 Voltage | RO | 2 bytes | Unit:0.1V
3747 | Slave14 Outlet Port08 Voltage | RO | 2 bytes | Unit:0.1V
3748 | Slave14 Outlet Port09 Voltage | RO | 2 bytes | Unit:0.1V
3749 | Slave14 Outlet Port10 Voltage | RO | 2 bytes | Unit:0.1V
3750 | Slave14 Outlet Port11 Voltage | RO | 2 bytes | Unit:0.1V
3751 | Slave14 Outlet Port12 Voltage | RO | 2 bytes | Unit:0.1V
3752 | Slave14 Outlet Port13 Voltage | RO | 2 bytes | Unit:0.1V
3753 | Slave14 Outlet Port14 Voltage | RO | 2 bytes | Unit:0.1V
3754 | Slave14 Outlet Port15 Voltage | RO | 2 bytes | Unit:0.1V
3755 | Slave14 Outlet Port16 Voltage | RO | 2 bytes | Unit:0.1V
3756 | Slave14 Outlet Port17 Voltage | RO | 2 bytes | Unit:0.1V
3757 | Slave14 Outlet Port18 Voltage | RO | 2 bytes | Unit:0.1V
3758 | Slave14 Outlet Port19 Voltage | RO | 2 bytes | Unit:0.1V
3759 | Slave14 Outlet Port20 Voltage | RO | 2 bytes | Unit:0.1V
3760 | Slave14 Outlet Port21 Voltage | RO | 2 bytes | Unit:0.1V
3761 | Slave14 Outlet Port22 Voltage | RO | 2 bytes | Unit:0.1V
3762 | Slave14 Outlet Port23 Voltage | RO | 2 bytes | Unit:0.1V
3763 | Slave14 Outlet Port24 Voltage | RO | 2 bytes | Unit:0.1V
3764 | Slave14 Outlet Port25 Voltage | RO | 2 bytes | Unit:0.1V
3765 | Slave14 Outlet Port26 Voltage | RO | 2 bytes | Unit:0.1V
3766 | Slave14 Outlet Port27 Voltage | RO | 2 bytes | Unit:0.1V
3767 | Slave14 Outlet Port28 Voltage | RO | 2 bytes | Unit:0.1V
3768 | Slave14 Outlet Port29 Voltage | RO | 2 bytes | Unit:0.1V
3769 | Slave14 Outlet Port30 Voltage | RO | 2 bytes | Unit:0.1V
3770 | Slave14 Outlet Port31 Voltage | RO | 2 bytes | Unit:0.1V
3771 | Slave14 Outlet Port32 Voltage | RO | 2 bytes | Unit:0.1V
3772 | Slave14 Outlet Port33 Voltage | RO | 2 bytes | Unit:0.1V
3773 | Slave14 Outlet Port34 Voltage | RO | 2 bytes | Unit:0.1V
3774 | Slave14 Outlet Port35 Voltage | RO | 2 bytes | Unit:0.1V
3775 | Slave14 Outlet Port36 Voltage | RO | 2 bytes | Unit:0.1V
3776 | Slave14 Outlet Port37 Voltage | RO | 2 bytes | Unit:0.1V
3777 | Slave14 Outlet Port38 Voltage | RO | 2 bytes | Unit:0.1V
3778 | Slave14 Outlet Port39 Voltage | RO | 2 bytes | Unit:0.1V
3779 | Slave14 Outlet Port40 Voltage | RO | 2 bytes | Unit:0.1V
3780 | Slave14 Outlet Port41 Voltage | RO | 2 bytes | Unit:0.1V
3781 | Slave14 Outlet Port42 Voltage | RO | 2 bytes | Unit:0.1V
3782 | Slave15 Outlet Port01 Voltage | RO | 2 bytes | Unit:0.1V
3783 | Slave15 Outlet Port02 Voltage | RO | 2 bytes | Unit:0.1V
3784 | Slave15 Outlet Port03 Voltage | RO | 2 bytes | Unit:0.1V
3785 | Slave15 Outlet Port04 Voltage | RO | 2 bytes | Unit:0.1V
3786 | Slave15 Outlet Port05 Voltage | RO | 2 bytes | Unit:0.1V
3787 | Slave15 Outlet Port06 Voltage | RO | 2 bytes | Unit:0.1V
3788 | Slave15 Outlet Port07 Voltage | RO | 2 bytes | Unit:0.1V
3789 | Slave15 Outlet Port08 Voltage | RO | 2 bytes | Unit:0.1V
3790 | Slave15 Outlet Port09 Voltage | RO | 2 bytes | Unit:0.1V
3791 | Slave15 Outlet Port10 Voltage | RO | 2 bytes | Unit:0.1V
3792 | Slave15 Outlet Port11 Voltage | RO | 2 bytes | Unit:0.1V
3793 | Slave15 Outlet Port12 Voltage | RO | 2 bytes | Unit:0.1V
3794 | Slave15 Outlet Port13 Voltage | RO | 2 bytes | Unit:0.1V
3795 | Slave15 Outlet Port14 Voltage | RO | 2 bytes | Unit:0.1V
3796 | Slave15 Outlet Port15 Voltage | RO | 2 bytes | Unit:0.1V
3797 | Slave15 Outlet Port16 Voltage | RO | 2 bytes | Unit:0.1V
3798 | Slave15 Outlet Port17 Voltage | RO | 2 bytes | Unit:0.1V
3799 | Slave15 Outlet Port18 Voltage | RO | 2 bytes | Unit:0.1V
3800 | Slave15 Outlet Port19 Voltage | RO | 2 bytes | Unit:0.1V
3801 | Slave15 Outlet Port20 Voltage | RO | 2 bytes | Unit:0.1V
3802 | Slave15 Outlet Port21 Voltage | RO | 2 bytes | Unit:0.1V
3803 | Slave15 Outlet Port22 Voltage | RO | 2 bytes | Unit:0.1V
3804 | Slave15 Outlet Port23 Voltage | RO | 2 bytes | Unit:0.1V
3805 | Slave15 Outlet Port24 Voltage | RO | 2 bytes | Unit:0.1V
3806 | Slave15 Outlet Port25 Voltage | RO | 2 bytes | Unit:0.1V
3807 | Slave15 Outlet Port26 Voltage | RO | 2 bytes | Unit:0.1V
3808 | Slave15 Outlet Port27 Voltage | RO | 2 bytes | Unit:0.1V
3809 | Slave15 Outlet Port28 Voltage | RO | 2 bytes | Unit:0.1V
3810 | Slave15 Outlet Port29 Voltage | RO | 2 bytes | Unit:0.1V
3811 | Slave15 Outlet Port30 Voltage | RO | 2 bytes | Unit:0.1V
3812 | Slave15 Outlet Port31 Voltage | RO | 2 bytes | Unit:0.1V
3813 | Slave15 Outlet Port32 Voltage | RO | 2 bytes | Unit:0.1V
3814 | Slave15 Outlet Port33 Voltage | RO | 2 bytes | Unit:0.1V
3815 | Slave15 Outlet Port34 Voltage | RO | 2 bytes | Unit:0.1V
3816 | Slave15 Outlet Port35 Voltage | RO | 2 bytes | Unit:0.1V
3817 | Slave15 Outlet Port36 Voltage | RO | 2 bytes | Unit:0.1V
3818 | Slave15 Outlet Port37 Voltage | RO | 2 bytes | Unit:0.1V
3819 | Slave15 Outlet Port38 Voltage | RO | 2 bytes | Unit:0.1V
3820 | Slave15 Outlet Port39 Voltage | RO | 2 bytes | Unit:0.1V
3821 | Slave15 Outlet Port40 Voltage | RO | 2 bytes | Unit:0.1V
3822 | Slave15 Outlet Port41 Voltage | RO | 2 bytes | Unit:0.1V
3823 | Slave15 Outlet Port42 Voltage | RO | 2 bytes | Unit:0.1V
3824 | Master Outlet Port01 Current | RO | 2 bytes | Unit:0.01A
3825 | Master Outlet Port02 Current | RO | 2 bytes | Unit:0.01A
3826 | Master Outlet Port03 Current | RO | 2 bytes | Unit:0.01A
3827 | Master Outlet Port04 Current | RO | 2 bytes | Unit:0.01A
3828 | Master Outlet Port05 Current | RO | 2 bytes | Unit:0.01A
3829 | Master Outlet Port06 Current | RO | 2 bytes | Unit:0.01A
3830 | Master Outlet Port07 Current | RO | 2 bytes | Unit:0.01A
3831 | Master Outlet Port08 Current | RO | 2 bytes | Unit:0.01A
3832 | Master Outlet Port09 Current | RO | 2 bytes | Unit:0.01A
3833 | Master Outlet Port10 Current | RO | 2 bytes | Unit:0.01A
3834 | Master Outlet Port11 Current | RO | 2 bytes | Unit:0.01A
3835 | Master Outlet Port12 Current | RO | 2 bytes | Unit:0.01A
3836 | Master Outlet Port13 Current | RO | 2 bytes | Unit:0.01A
3837 | Master Outlet Port14 Current | RO | 2 bytes | Unit:0.01A
3838 | Master Outlet Port15 Current | RO | 2 bytes | Unit:0.01A
3839 | Master Outlet Port16 Current | RO | 2 bytes | Unit:0.01A
3840 | Master Outlet Port17 Current | RO | 2 bytes | Unit:0.01A
3841 | Master Outlet Port18 Current | RO | 2 bytes | Unit:0.01A
3842 | Master Outlet Port19 Current | RO | 2 bytes | Unit:0.01A
3843 | Master Outlet Port20 Current | RO | 2 bytes | Unit:0.01A
3844 | Master Outlet Port21 Current | RO | 2 bytes | Unit:0.01A
3845 | Master Outlet Port22 Current | RO | 2 bytes | Unit:0.01A
3846 | Master Outlet Port23 Current | RO | 2 bytes | Unit:0.01A
3847 | Master Outlet Port24 Current | RO | 2 bytes | Unit:0.01A
3848 | Master Outlet Port25 Current | RO | 2 bytes | Unit:0.01A
3849 | Master Outlet Port26 Current | RO | 2 bytes | Unit:0.01A
3850 | Master Outlet Port27 Current | RO | 2 bytes | Unit:0.01A
3851 | Master Outlet Port28 Current | RO | 2 bytes | Unit:0.01A
3852 | Master Outlet Port29 Current | RO | 2 bytes | Unit:0.01A
3853 | Master Outlet Port30 Current | RO | 2 bytes | Unit:0.01A
3854 | Master Outlet Port31 Current | RO | 2 bytes | Unit:0.01A
3855 | Master Outlet Port32 Current | RO | 2 bytes | Unit:0.01A
3856 | Master Outlet Port33 Current | RO | 2 bytes | Unit:0.01A
3857 | Master Outlet Port34 Current | RO | 2 bytes | Unit:0.01A
3858 | Master Outlet Port35 Current | RO | 2 bytes | Unit:0.01A
3859 | Master Outlet Port36 Current | RO | 2 bytes | Unit:0.01A
3860 | Master Outlet Port37 Current | RO | 2 bytes | Unit:0.01A
3861 | Master Outlet Port38 Current | RO | 2 bytes | Unit:0.01A
3862 | Master Outlet Port39 Current | RO | 2 bytes | Unit:0.01A
3863 | Master Outlet Port40 Current | RO | 2 bytes | Unit:0.01A
3864 | Master Outlet Port41 Current | RO | 2 bytes | Unit:0.01A
3865 | Master Outlet Port42 Current | RO | 2 bytes | Unit:0.01A
3866 | Slave01 Outlet Port01 Current | RO | 2 bytes | Unit:0.01A
3867 | Slave01 Outlet Port02 Current | RO | 2 bytes | Unit:0.01A
3868 | Slave01 Outlet Port03 Current | RO | 2 bytes | Unit:0.01A
3869 | Slave01 Outlet Port04 Current | RO | 2 bytes | Unit:0.01A
3870 | Slave01 Outlet Port05 Current | RO | 2 bytes | Unit:0.01A
3871 | Slave01 Outlet Port06 Current | RO | 2 bytes | Unit:0.01A
3872 | Slave01 Outlet Port07 Current | RO | 2 bytes | Unit:0.01A
3873 | Slave01 Outlet Port08 Current | RO | 2 bytes | Unit:0.01A
3874 | Slave01 Outlet Port09 Current | RO | 2 bytes | Unit:0.01A
3875 | Slave01 Outlet Port10 Current | RO | 2 bytes | Unit:0.01A
3876 | Slave01 Outlet Port11 Current | RO | 2 bytes | Unit:0.01A
3877 | Slave01 Outlet Port12 Current | RO | 2 bytes | Unit:0.01A
3878 | Slave01 Outlet Port13 Current | RO | 2 bytes | Unit:0.01A
3879 | Slave01 Outlet Port14 Current | RO | 2 bytes | Unit:0.01A
3880 | Slave01 Outlet Port15 Current | RO | 2 bytes | Unit:0.01A
3881 | Slave01 Outlet Port16 Current | RO | 2 bytes | Unit:0.01A
3882 | Slave01 Outlet Port17 Current | RO | 2 bytes | Unit:0.01A
3883 | Slave01 Outlet Port18 Current | RO | 2 bytes | Unit:0.01A
3884 | Slave01 Outlet Port19 Current | RO | 2 bytes | Unit:0.01A
3885 | Slave01 Outlet Port20 Current | RO | 2 bytes | Unit:0.01A
3886 | Slave01 Outlet Port21 Current | RO | 2 bytes | Unit:0.01A
3887 | Slave01 Outlet Port22 Current | RO | 2 bytes | Unit:0.01A
3888 | Slave01 Outlet Port23 Current | RO | 2 bytes | Unit:0.01A
3889 | Slave01 Outlet Port24 Current | RO | 2 bytes | Unit:0.01A
3890 | Slave01 Outlet Port25 Current | RO | 2 bytes | Unit:0.01A
3891 | Slave01 Outlet Port26 Current | RO | 2 bytes | Unit:0.01A
3892 | Slave01 Outlet Port27 Current | RO | 2 bytes | Unit:0.01A
3893 | Slave01 Outlet Port28 Current | RO | 2 bytes | Unit:0.01A
3894 | Slave01 Outlet Port29 Current | RO | 2 bytes | Unit:0.01A
3895 | Slave01 Outlet Port30 Current | RO | 2 bytes | Unit:0.01A
3896 | Slave01 Outlet Port31 Current | RO | 2 bytes | Unit:0.01A
3897 | Slave01 Outlet Port32 Current | RO | 2 bytes | Unit:0.01A
3898 | Slave01 Outlet Port33 Current | RO | 2 bytes | Unit:0.01A
3899 | Slave01 Outlet Port34 Current | RO | 2 bytes | Unit:0.01A
3900 | Slave01 Outlet Port35 Current | RO | 2 bytes | Unit:0.01A
3901 | Slave01 Outlet Port36 Current | RO | 2 bytes | Unit:0.01A
3902 | Slave01 Outlet Port37 Current | RO | 2 bytes | Unit:0.01A
3903 | Slave01 Outlet Port38 Current | RO | 2 bytes | Unit:0.01A
3904 | Slave01 Outlet Port39 Current | RO | 2 bytes | Unit:0.01A
3905 | Slave01 Outlet Port40 Current | RO | 2 bytes | Unit:0.01A
3906 | Slave01 Outlet Port41 Current | RO | 2 bytes | Unit:0.01A
3907 | Slave01 Outlet Port42 Current | RO | 2 bytes | Unit:0.01A
3908 | Slave02 Outlet Port01 Current | RO | 2 bytes | Unit:0.01A
3909 | Slave02 Outlet Port02 Current | RO | 2 bytes | Unit:0.01A
3910 | Slave02 Outlet Port03 Current | RO | 2 bytes | Unit:0.01A
3911 | Slave02 Outlet Port04 Current | RO | 2 bytes | Unit:0.01A
3912 | Slave02 Outlet Port05 Current | RO | 2 bytes | Unit:0.01A
3913 | Slave02 Outlet Port06 Current | RO | 2 bytes | Unit:0.01A
3914 | Slave02 Outlet Port07 Current | RO | 2 bytes | Unit:0.01A
3915 | Slave02 Outlet Port08 Current | RO | 2 bytes | Unit:0.01A
3916 | Slave02 Outlet Port09 Current | RO | 2 bytes | Unit:0.01A
3917 | Slave02 Outlet Port10 Current | RO | 2 bytes | Unit:0.01A
3918 | Slave02 Outlet Port11 Current | RO | 2 bytes | Unit:0.01A
3919 | Slave02 Outlet Port12 Current | RO | 2 bytes | Unit:0.01A
3920 | Slave02 Outlet Port13 Current | RO | 2 bytes | Unit:0.01A
3921 | Slave02 Outlet Port14 Current | RO | 2 bytes | Unit:0.01A
3922 | Slave02 Outlet Port15 Current | RO | 2 bytes | Unit:0.01A
3923 | Slave02 Outlet Port16 Current | RO | 2 bytes | Unit:0.01A
3924 | Slave02 Outlet Port17 Current | RO | 2 bytes | Unit:0.01A
3925 | Slave02 Outlet Port18 Current | RO | 2 bytes | Unit:0.01A
3926 | Slave02 Outlet Port19 Current | RO | 2 bytes | Unit:0.01A
3927 | Slave02 Outlet Port20 Current | RO | 2 bytes | Unit:0.01A
3928 | Slave02 Outlet Port21 Current | RO | 2 bytes | Unit:0.01A
3929 | Slave02 Outlet Port22 Current | RO | 2 bytes | Unit:0.01A
3930 | Slave02 Outlet Port23 Current | RO | 2 bytes | Unit:0.01A
3931 | Slave02 Outlet Port24 Current | RO | 2 bytes | Unit:0.01A
3932 | Slave02 Outlet Port25 Current | RO | 2 bytes | Unit:0.01A
3933 | Slave02 Outlet Port26 Current | RO | 2 bytes | Unit:0.01A
3934 | Slave02 Outlet Port27 Current | RO | 2 bytes | Unit:0.01A
3935 | Slave02 Outlet Port28 Current | RO | 2 bytes | Unit:0.01A
3936 | Slave02 Outlet Port29 Current | RO | 2 bytes | Unit:0.01A
3937 | Slave02 Outlet Port30 Current | RO | 2 bytes | Unit:0.01A
3938 | Slave02 Outlet Port31 Current | RO | 2 bytes | Unit:0.01A
3939 | Slave02 Outlet Port32 Current | RO | 2 bytes | Unit:0.01A
3940 | Slave02 Outlet Port33 Current | RO | 2 bytes | Unit:0.01A
3941 | Slave02 Outlet Port34 Current | RO | 2 bytes | Unit:0.01A
3942 | Slave02 Outlet Port35 Current | RO | 2 bytes | Unit:0.01A
3943 | Slave02 Outlet Port36 Current | RO | 2 bytes | Unit:0.01A
3944 | Slave02 Outlet Port37 Current | RO | 2 bytes | Unit:0.01A
3945 | Slave02 Outlet Port38 Current | RO | 2 bytes | Unit:0.01A
3946 | Slave02 Outlet Port39 Current | RO | 2 bytes | Unit:0.01A
3947 | Slave02 Outlet Port40 Current | RO | 2 bytes | Unit:0.01A
3948 | Slave02 Outlet Port41 Current | RO | 2 bytes | Unit:0.01A
3949 | Slave02 Outlet Port42 Current | RO | 2 bytes | Unit:0.01A
3950 | Slave03 Outlet Port01 Current | RO | 2 bytes | Unit:0.01A
3951 | Slave03 Outlet Port02 Current | RO | 2 bytes | Unit:0.01A
3952 | Slave03 Outlet Port03 Current | RO | 2 bytes | Unit:0.01A
3953 | Slave03 Outlet Port04 Current | RO | 2 bytes | Unit:0.01A
3954 | Slave03 Outlet Port05 Current | RO | 2 bytes | Unit:0.01A
3955 | Slave03 Outlet Port06 Current | RO | 2 bytes | Unit:0.01A
3956 | Slave03 Outlet Port07 Current | RO | 2 bytes | Unit:0.01A
3957 | Slave03 Outlet Port08 Current | RO | 2 bytes | Unit:0.01A
3958 | Slave03 Outlet Port09 Current | RO | 2 bytes | Unit:0.01A
3959 | Slave03 Outlet Port10 Current | RO | 2 bytes | Unit:0.01A
3960 | Slave03 Outlet Port11 Current | RO | 2 bytes | Unit:0.01A
3961 | Slave03 Outlet Port12 Current | RO | 2 bytes | Unit:0.01A
3962 | Slave03 Outlet Port13 Current | RO | 2 bytes | Unit:0.01A
3963 | Slave03 Outlet Port14 Current | RO | 2 bytes | Unit:0.01A
3964 | Slave03 Outlet Port15 Current | RO | 2 bytes | Unit:0.01A
3965 | Slave03 Outlet Port16 Current | RO | 2 bytes | Unit:0.01A
3966 | Slave03 Outlet Port17 Current | RO | 2 bytes | Unit:0.01A
3967 | Slave03 Outlet Port18 Current | RO | 2 bytes | Unit:0.01A
3968 | Slave03 Outlet Port19 Current | RO | 2 bytes | Unit:0.01A
3969 | Slave03 Outlet Port20 Current | RO | 2 bytes | Unit:0.01A
3970 | Slave03 Outlet Port21 Current | RO | 2 bytes | Unit:0.01A
3971 | Slave03 Outlet Port22 Current | RO | 2 bytes | Unit:0.01A
3972 | Slave03 Outlet Port23 Current | RO | 2 bytes | Unit:0.01A
3973 | Slave03 Outlet Port24 Current | RO | 2 bytes | Unit:0.01A
3974 | Slave03 Outlet Port25 Current | RO | 2 bytes | Unit:0.01A
3975 | Slave03 Outlet Port26 Current | RO | 2 bytes | Unit:0.01A
3976 | Slave03 Outlet Port27 Current | RO | 2 bytes | Unit:0.01A
3977 | Slave03 Outlet Port28 Current | RO | 2 bytes | Unit:0.01A
3978 | Slave03 Outlet Port29 Current | RO | 2 bytes | Unit:0.01A
3979 | Slave03 Outlet Port30 Current | RO | 2 bytes | Unit:0.01A
3980 | Slave03 Outlet Port31 Current | RO | 2 bytes | Unit:0.01A
3981 | Slave03 Outlet Port32 Current | RO | 2 bytes | Unit:0.01A
3982 | Slave03 Outlet Port33 Current | RO | 2 bytes | Unit:0.01A
3983 | Slave03 Outlet Port34 Current | RO | 2 bytes | Unit:0.01A
3984 | Slave03 Outlet Port35 Current | RO | 2 bytes | Unit:0.01A
3985 | Slave03 Outlet Port36 Current | RO | 2 bytes | Unit:0.01A
3986 | Slave03 Outlet Port37 Current | RO | 2 bytes | Unit:0.01A
3987 | Slave03 Outlet Port38 Current | RO | 2 bytes | Unit:0.01A
3988 | Slave03 Outlet Port39 Current | RO | 2 bytes | Unit:0.01A
3989 | Slave03 Outlet Port40 Current | RO | 2 bytes | Unit:0.01A
3990 | Slave03 Outlet Port41 Current | RO | 2 bytes | Unit:0.01A
3991 | Slave03 Outlet Port42 Current | RO | 2 bytes | Unit:0.01A
3992 | Slave04 Outlet Port01 Current | RO | 2 bytes | Unit:0.01A
3993 | Slave04 Outlet Port02 Current | RO | 2 bytes | Unit:0.01A
3994 | Slave04 Outlet Port03 Current | RO | 2 bytes | Unit:0.01A
3995 | Slave04 Outlet Port04 Current | RO | 2 bytes | Unit:0.01A
3996 | Slave04 Outlet Port05 Current | RO | 2 bytes | Unit:0.01A
3997 | Slave04 Outlet Port06 Current | RO | 2 bytes | Unit:0.01A
3998 | Slave04 Outlet Port07 Current | RO | 2 bytes | Unit:0.01A
3999 | Slave04 Outlet Port08 Current | RO | 2 bytes | Unit:0.01A
4000 | Slave04 Outlet Port09 Current | RO | 2 bytes | Unit:0.01A
4001 | Slave04 Outlet Port10 Current | RO | 2 bytes | Unit:0.01A
4002 | Slave04 Outlet Port11 Current | RO | 2 bytes | Unit:0.01A
4003 | Slave04 Outlet Port12 Current | RO | 2 bytes | Unit:0.01A
4004 | Slave04 Outlet Port13 Current | RO | 2 bytes | Unit:0.01A
4005 | Slave04 Outlet Port14 Current | RO | 2 bytes | Unit:0.01A
4006 | Slave04 Outlet Port15 Current | RO | 2 bytes | Unit:0.01A
4007 | Slave04 Outlet Port16 Current | RO | 2 bytes | Unit:0.01A
4008 | Slave04 Outlet Port17 Current | RO | 2 bytes | Unit:0.01A
4009 | Slave04 Outlet Port18 Current | RO | 2 bytes | Unit:0.01A
4010 | Slave04 Outlet Port19 Current | RO | 2 bytes | Unit:0.01A
4011 | Slave04 Outlet Port20 Current | RO | 2 bytes | Unit:0.01A
4012 | Slave04 Outlet Port21 Current | RO | 2 bytes | Unit:0.01A
4013 | Slave04 Outlet Port22 Current | RO | 2 bytes | Unit:0.01A
4014 | Slave04 Outlet Port23 Current | RO | 2 bytes | Unit:0.01A
4015 | Slave04 Outlet Port24 Current | RO | 2 bytes | Unit:0.01A
4016 | Slave04 Outlet Port25 Current | RO | 2 bytes | Unit:0.01A
4017 | Slave04 Outlet Port26 Current | RO | 2 bytes | Unit:0.01A
4018 | Slave04 Outlet Port27 Current | RO | 2 bytes | Unit:0.01A
4019 | Slave04 Outlet Port28 Current | RO | 2 bytes | Unit:0.01A
4020 | Slave04 Outlet Port29 Current | RO | 2 bytes | Unit:0.01A
4021 | Slave04 Outlet Port30 Current | RO | 2 bytes | Unit:0.01A
4022 | Slave04 Outlet Port31 Current | RO | 2 bytes | Unit:0.01A
4023 | Slave04 Outlet Port32 Current | RO | 2 bytes | Unit:0.01A
4024 | Slave04 Outlet Port33 Current | RO | 2 bytes | Unit:0.01A
4025 | Slave04 Outlet Port34 Current | RO | 2 bytes | Unit:0.01A
4026 | Slave04 Outlet Port35 Current | RO | 2 bytes | Unit:0.01A
4027 | Slave04 Outlet Port36 Current | RO | 2 bytes | Unit:0.01A
4028 | Slave04 Outlet Port37 Current | RO | 2 bytes | Unit:0.01A
4029 | Slave04 Outlet Port38 Current | RO | 2 bytes | Unit:0.01A
4030 | Slave04 Outlet Port39 Current | RO | 2 bytes | Unit:0.01A
4031 | Slave04 Outlet Port40 Current | RO | 2 bytes | Unit:0.01A
4032 | Slave04 Outlet Port41 Current | RO | 2 bytes | Unit:0.01A
4033 | Slave04 Outlet Port42 Current | RO | 2 bytes | Unit:0.01A
4034 | Slave05 Outlet Port01 Current | RO | 2 bytes | Unit:0.01A
4035 | Slave05 Outlet Port02 Current | RO | 2 bytes | Unit:0.01A
4036 | Slave05 Outlet Port03 Current | RO | 2 bytes | Unit:0.01A
4037 | Slave05 Outlet Port04 Current | RO | 2 bytes | Unit:0.01A
4038 | Slave05 Outlet Port05 Current | RO | 2 bytes | Unit:0.01A
4039 | Slave05 Outlet Port06 Current | RO | 2 bytes | Unit:0.01A
4040 | Slave05 Outlet Port07 Current | RO | 2 bytes | Unit:0.01A
4041 | Slave05 Outlet Port08 Current | RO | 2 bytes | Unit:0.01A
4042 | Slave05 Outlet Port09 Current | RO | 2 bytes | Unit:0.01A
4043 | Slave05 Outlet Port10 Current | RO | 2 bytes | Unit:0.01A
4044 | Slave05 Outlet Port11 Current | RO | 2 bytes | Unit:0.01A
4045 | Slave05 Outlet Port12 Current | RO | 2 bytes | Unit:0.01A
4046 | Slave05 Outlet Port13 Current | RO | 2 bytes | Unit:0.01A
4047 | Slave05 Outlet Port14 Current | RO | 2 bytes | Unit:0.01A
4048 | Slave05 Outlet Port15 Current | RO | 2 bytes | Unit:0.01A
4049 | Slave05 Outlet Port16 Current | RO | 2 bytes | Unit:0.01A
4050 | Slave05 Outlet Port17 Current | RO | 2 bytes | Unit:0.01A
4051 | Slave05 Outlet Port18 Current | RO | 2 bytes | Unit:0.01A
4052 | Slave05 Outlet Port19 Current | RO | 2 bytes | Unit:0.01A
4053 | Slave05 Outlet Port20 Current | RO | 2 bytes | Unit:0.01A
4054 | Slave05 Outlet Port21 Current | RO | 2 bytes | Unit:0.01A
4055 | Slave05 Outlet Port22 Current | RO | 2 bytes | Unit:0.01A
4056 | Slave05 Outlet Port23 Current | RO | 2 bytes | Unit:0.01A
4057 | Slave05 Outlet Port24 Current | RO | 2 bytes | Unit:0.01A
4058 | Slave05 Outlet Port25 Current | RO | 2 bytes | Unit:0.01A
4059 | Slave05 Outlet Port26 Current | RO | 2 bytes | Unit:0.01A
4060 | Slave05 Outlet Port27 Current | RO | 2 bytes | Unit:0.01A
4061 | Slave05 Outlet Port28 Current | RO | 2 bytes | Unit:0.01A
4062 | Slave05 Outlet Port29 Current | RO | 2 bytes | Unit:0.01A
4063 | Slave05 Outlet Port30 Current | RO | 2 bytes | Unit:0.01A
4064 | Slave05 Outlet Port31 Current | RO | 2 bytes | Unit:0.01A
4065 | Slave05 Outlet Port32 Current | RO | 2 bytes | Unit:0.01A
4066 | Slave05 Outlet Port33 Current | RO | 2 bytes | Unit:0.01A
4067 | Slave05 Outlet Port34 Current | RO | 2 bytes | Unit:0.01A
4068 | Slave05 Outlet Port35 Current | RO | 2 bytes | Unit:0.01A
4069 | Slave05 Outlet Port36 Current | RO | 2 bytes | Unit:0.01A
4070 | Slave05 Outlet Port37 Current | RO | 2 bytes | Unit:0.01A
4071 | Slave05 Outlet Port38 Current | RO | 2 bytes | Unit:0.01A
4072 | Slave05 Outlet Port39 Current | RO | 2 bytes | Unit:0.01A
4073 | Slave05 Outlet Port40 Current | RO | 2 bytes | Unit:0.01A
4074 | Slave05 Outlet Port41 Current | RO | 2 bytes | Unit:0.01A
4075 | Slave05 Outlet Port42 Current | RO | 2 bytes | Unit:0.01A
4076 | Slave06 Outlet Port01 Current | RO | 2 bytes | Unit:0.01A
4077 | Slave06 Outlet Port02 Current | RO | 2 bytes | Unit:0.01A
4078 | Slave06 Outlet Port03 Current | RO | 2 bytes | Unit:0.01A
4079 | Slave06 Outlet Port04 Current | RO | 2 bytes | Unit:0.01A
4080 | Slave06 Outlet Port05 Current | RO | 2 bytes | Unit:0.01A
4081 | Slave06 Outlet Port06 Current | RO | 2 bytes | Unit:0.01A
4082 | Slave06 Outlet Port07 Current | RO | 2 bytes | Unit:0.01A
4083 | Slave06 Outlet Port08 Current | RO | 2 bytes | Unit:0.01A
4084 | Slave06 Outlet Port09 Current | RO | 2 bytes | Unit:0.01A
4085 | Slave06 Outlet Port10 Current | RO | 2 bytes | Unit:0.01A
4086 | Slave06 Outlet Port11 Current | RO | 2 bytes | Unit:0.01A
4087 | Slave06 Outlet Port12 Current | RO | 2 bytes | Unit:0.01A
4088 | Slave06 Outlet Port13 Current | RO | 2 bytes | Unit:0.01A
4089 | Slave06 Outlet Port14 Current | RO | 2 bytes | Unit:0.01A
4090 | Slave06 Outlet Port15 Current | RO | 2 bytes | Unit:0.01A
4091 | Slave06 Outlet Port16 Current | RO | 2 bytes | Unit:0.01A
4092 | Slave06 Outlet Port17 Current | RO | 2 bytes | Unit:0.01A
4093 | Slave06 Outlet Port18 Current | RO | 2 bytes | Unit:0.01A
4094 | Slave06 Outlet Port19 Current | RO | 2 bytes | Unit:0.01A
4095 | Slave06 Outlet Port20 Current | RO | 2 bytes | Unit:0.01A
4096 | Slave06 Outlet Port21 Current | RO | 2 bytes | Unit:0.01A
4097 | Slave06 Outlet Port22 Current | RO | 2 bytes | Unit:0.01A
4098 | Slave06 Outlet Port23 Current | RO | 2 bytes | Unit:0.01A
4099 | Slave06 Outlet Port24 Current | RO | 2 bytes | Unit:0.01A
4100 | Slave06 Outlet Port25 Current | RO | 2 bytes | Unit:0.01A
4101 | Slave06 Outlet Port26 Current | RO | 2 bytes | Unit:0.01A
4102 | Slave06 Outlet Port27 Current | RO | 2 bytes | Unit:0.01A
4103 | Slave06 Outlet Port28 Current | RO | 2 bytes | Unit:0.01A
4104 | Slave06 Outlet Port29 Current | RO | 2 bytes | Unit:0.01A
4105 | Slave06 Outlet Port30 Current | RO | 2 bytes | Unit:0.01A
4106 | Slave06 Outlet Port31 Current | RO | 2 bytes | Unit:0.01A
4107 | Slave06 Outlet Port32 Current | RO | 2 bytes | Unit:0.01A
4108 | Slave06 Outlet Port33 Current | RO | 2 bytes | Unit:0.01A
4109 | Slave06 Outlet Port34 Current | RO | 2 bytes | Unit:0.01A
4110 | Slave06 Outlet Port35 Current | RO | 2 bytes | Unit:0.01A
4111 | Slave06 Outlet Port36 Current | RO | 2 bytes | Unit:0.01A
4112 | Slave06 Outlet Port37 Current | RO | 2 bytes | Unit:0.01A
4113 | Slave06 Outlet Port38 Current | RO | 2 bytes | Unit:0.01A
4114 | Slave06 Outlet Port39 Current | RO | 2 bytes | Unit:0.01A
4115 | Slave06 Outlet Port40 Current | RO | 2 bytes | Unit:0.01A
4116 | Slave06 Outlet Port41 Current | RO | 2 bytes | Unit:0.01A
4117 | Slave06 Outlet Port42 Current | RO | 2 bytes | Unit:0.01A
4118 | Slave07 Outlet Port01 Current | RO | 2 bytes | Unit:0.01A
4119 | Slave07 Outlet Port02 Current | RO | 2 bytes | Unit:0.01A
4120 | Slave07 Outlet Port03 Current | RO | 2 bytes | Unit:0.01A
4121 | Slave07 Outlet Port04 Current | RO | 2 bytes | Unit:0.01A
4122 | Slave07 Outlet Port05 Current | RO | 2 bytes | Unit:0.01A
4123 | Slave07 Outlet Port06 Current | RO | 2 bytes | Unit:0.01A
4124 | Slave07 Outlet Port07 Current | RO | 2 bytes | Unit:0.01A
4125 | Slave07 Outlet Port08 Current | RO | 2 bytes | Unit:0.01A
4126 | Slave07 Outlet Port09 Current | RO | 2 bytes | Unit:0.01A
4127 | Slave07 Outlet Port10 Current | RO | 2 bytes | Unit:0.01A
4128 | Slave07 Outlet Port11 Current | RO | 2 bytes | Unit:0.01A
4129 | Slave07 Outlet Port12 Current | RO | 2 bytes | Unit:0.01A
4130 | Slave07 Outlet Port13 Current | RO | 2 bytes | Unit:0.01A
4131 | Slave07 Outlet Port14 Current | RO | 2 bytes | Unit:0.01A
4132 | Slave07 Outlet Port15 Current | RO | 2 bytes | Unit:0.01A
4133 | Slave07 Outlet Port16 Current | RO | 2 bytes | Unit:0.01A
4134 | Slave07 Outlet Port17 Current | RO | 2 bytes | Unit:0.01A
4135 | Slave07 Outlet Port18 Current | RO | 2 bytes | Unit:0.01A
4136 | Slave07 Outlet Port19 Current | RO | 2 bytes | Unit:0.01A
4137 | Slave07 Outlet Port20 Current | RO | 2 bytes | Unit:0.01A
4138 | Slave07 Outlet Port21 Current | RO | 2 bytes | Unit:0.01A
4139 | Slave07 Outlet Port22 Current | RO | 2 bytes | Unit:0.01A
4140 | Slave07 Outlet Port23 Current | RO | 2 bytes | Unit:0.01A
4141 | Slave07 Outlet Port24 Current | RO | 2 bytes | Unit:0.01A
4142 | Slave07 Outlet Port25 Current | RO | 2 bytes | Unit:0.01A
4143 | Slave07 Outlet Port26 Current | RO | 2 bytes | Unit:0.01A
4144 | Slave07 Outlet Port27 Current | RO | 2 bytes | Unit:0.01A
4145 | Slave07 Outlet Port28 Current | RO | 2 bytes | Unit:0.01A
4146 | Slave07 Outlet Port29 Current | RO | 2 bytes | Unit:0.01A
4147 | Slave07 Outlet Port30 Current | RO | 2 bytes | Unit:0.01A
4148 | Slave07 Outlet Port31 Current | RO | 2 bytes | Unit:0.01A
4149 | Slave07 Outlet Port32 Current | RO | 2 bytes | Unit:0.01A
4150 | Slave07 Outlet Port33 Current | RO | 2 bytes | Unit:0.01A
4151 | Slave07 Outlet Port34 Current | RO | 2 bytes | Unit:0.01A
4152 | Slave07 Outlet Port35 Current | RO | 2 bytes | Unit:0.01A
4153 | Slave07 Outlet Port36 Current | RO | 2 bytes | Unit:0.01A
4154 | Slave07 Outlet Port37 Current | RO | 2 bytes | Unit:0.01A
4155 | Slave07 Outlet Port38 Current | RO | 2 bytes | Unit:0.01A
4156 | Slave07 Outlet Port39 Current | RO | 2 bytes | Unit:0.01A
4157 | Slave07 Outlet Port40 Current | RO | 2 bytes | Unit:0.01A
4158 | Slave07 Outlet Port41 Current | RO | 2 bytes | Unit:0.01A
4159 | Slave07 Outlet Port42 Current | RO | 2 bytes | Unit:0.01A
4160 | Slave08 Outlet Port01 Current | RO | 2 bytes | Unit:0.01A
4161 | Slave08 Outlet Port02 Current | RO | 2 bytes | Unit:0.01A
4162 | Slave08 Outlet Port03 Current | RO | 2 bytes | Unit:0.01A
4163 | Slave08 Outlet Port04 Current | RO | 2 bytes | Unit:0.01A
4164 | Slave08 Outlet Port05 Current | RO | 2 bytes | Unit:0.01A
4165 | Slave08 Outlet Port06 Current | RO | 2 bytes | Unit:0.01A
4166 | Slave08 Outlet Port07 Current | RO | 2 bytes | Unit:0.01A
4167 | Slave08 Outlet Port08 Current | RO | 2 bytes | Unit:0.01A
4168 | Slave08 Outlet Port09 Current | RO | 2 bytes | Unit:0.01A
4169 | Slave08 Outlet Port10 Current | RO | 2 bytes | Unit:0.01A
4170 | Slave08 Outlet Port11 Current | RO | 2 bytes | Unit:0.01A
4171 | Slave08 Outlet Port12 Current | RO | 2 bytes | Unit:0.01A
4172 | Slave08 Outlet Port13 Current | RO | 2 bytes | Unit:0.01A
4173 | Slave08 Outlet Port14 Current | RO | 2 bytes | Unit:0.01A
4174 | Slave08 Outlet Port15 Current | RO | 2 bytes | Unit:0.01A
4175 | Slave08 Outlet Port16 Current | RO | 2 bytes | Unit:0.01A
4176 | Slave08 Outlet Port17 Current | RO | 2 bytes | Unit:0.01A
4177 | Slave08 Outlet Port18 Current | RO | 2 bytes | Unit:0.01A
4178 | Slave08 Outlet Port19 Current | RO | 2 bytes | Unit:0.01A
4179 | Slave08 Outlet Port20 Current | RO | 2 bytes | Unit:0.01A
4180 | Slave08 Outlet Port21 Current | RO | 2 bytes | Unit:0.01A
4181 | Slave08 Outlet Port22 Current | RO | 2 bytes | Unit:0.01A
4182 | Slave08 Outlet Port23 Current | RO | 2 bytes | Unit:0.01A
4183 | Slave08 Outlet Port24 Current | RO | 2 bytes | Unit:0.01A
4184 | Slave08 Outlet Port25 Current | RO | 2 bytes | Unit:0.01A
4185 | Slave08 Outlet Port26 Current | RO | 2 bytes | Unit:0.01A
4186 | Slave08 Outlet Port27 Current | RO | 2 bytes | Unit:0.01A
4187 | Slave08 Outlet Port28 Current | RO | 2 bytes | Unit:0.01A
4188 | Slave08 Outlet Port29 Current | RO | 2 bytes | Unit:0.01A
4189 | Slave08 Outlet Port30 Current | RO | 2 bytes | Unit:0.01A
4190 | Slave08 Outlet Port31 Current | RO | 2 bytes | Unit:0.01A
4191 | Slave08 Outlet Port32 Current | RO | 2 bytes | Unit:0.01A
4192 | Slave08 Outlet Port33 Current | RO | 2 bytes | Unit:0.01A
4193 | Slave08 Outlet Port34 Current | RO | 2 bytes | Unit:0.01A
4194 | Slave08 Outlet Port35 Current | RO | 2 bytes | Unit:0.01A
4195 | Slave08 Outlet Port36 Current | RO | 2 bytes | Unit:0.01A
4196 | Slave08 Outlet Port37 Current | RO | 2 bytes | Unit:0.01A
4197 | Slave08 Outlet Port38 Current | RO | 2 bytes | Unit:0.01A
4198 | Slave08 Outlet Port39 Current | RO | 2 bytes | Unit:0.01A
4199 | Slave08 Outlet Port40 Current | RO | 2 bytes | Unit:0.01A
4200 | Slave08 Outlet Port41 Current | RO | 2 bytes | Unit:0.01A
4201 | Slave08 Outlet Port42 Current | RO | 2 bytes | Unit:0.01A
4202 | Slave09 Outlet Port01 Current | RO | 2 bytes | Unit:0.01A
4203 | Slave09 Outlet Port02 Current | RO | 2 bytes | Unit:0.01A
4204 | Slave09 Outlet Port03 Current | RO | 2 bytes | Unit:0.01A
4205 | Slave09 Outlet Port04 Current | RO | 2 bytes | Unit:0.01A
4206 | Slave09 Outlet Port05 Current | RO | 2 bytes | Unit:0.01A
4207 | Slave09 Outlet Port06 Current | RO | 2 bytes | Unit:0.01A
4208 | Slave09 Outlet Port07 Current | RO | 2 bytes | Unit:0.01A
4209 | Slave09 Outlet Port08 Current | RO | 2 bytes | Unit:0.01A
4210 | Slave09 Outlet Port09 Current | RO | 2 bytes | Unit:0.01A
4211 | Slave09 Outlet Port10 Current | RO | 2 bytes | Unit:0.01A
4212 | Slave09 Outlet Port11 Current | RO | 2 bytes | Unit:0.01A
4213 | Slave09 Outlet Port12 Current | RO | 2 bytes | Unit:0.01A
4214 | Slave09 Outlet Port13 Current | RO | 2 bytes | Unit:0.01A
4215 | Slave09 Outlet Port14 Current | RO | 2 bytes | Unit:0.01A
4216 | Slave09 Outlet Port15 Current | RO | 2 bytes | Unit:0.01A
4217 | Slave09 Outlet Port16 Current | RO | 2 bytes | Unit:0.01A
4218 | Slave09 Outlet Port17 Current | RO | 2 bytes | Unit:0.01A
4219 | Slave09 Outlet Port18 Current | RO | 2 bytes | Unit:0.01A
4220 | Slave09 Outlet Port19 Current | RO | 2 bytes | Unit:0.01A
4221 | Slave09 Outlet Port20 Current | RO | 2 bytes | Unit:0.01A
4222 | Slave09 Outlet Port21 Current | RO | 2 bytes | Unit:0.01A
4223 | Slave09 Outlet Port22 Current | RO | 2 bytes | Unit:0.01A
4224 | Slave09 Outlet Port23 Current | RO | 2 bytes | Unit:0.01A
4225 | Slave09 Outlet Port24 Current | RO | 2 bytes | Unit:0.01A
4226 | Slave09 Outlet Port25 Current | RO | 2 bytes | Unit:0.01A
4227 | Slave09 Outlet Port26 Current | RO | 2 bytes | Unit:0.01A
4228 | Slave09 Outlet Port27 Current | RO | 2 bytes | Unit:0.01A
4229 | Slave09 Outlet Port28 Current | RO | 2 bytes | Unit:0.01A
4230 | Slave09 Outlet Port29 Current | RO | 2 bytes | Unit:0.01A
4231 | Slave09 Outlet Port30 Current | RO | 2 bytes | Unit:0.01A
4232 | Slave09 Outlet Port31 Current | RO | 2 bytes | Unit:0.01A
4233 | Slave09 Outlet Port32 Current | RO | 2 bytes | Unit:0.01A
4234 | Slave09 Outlet Port33 Current | RO | 2 bytes | Unit:0.01A
4235 | Slave09 Outlet Port34 Current | RO | 2 bytes | Unit:0.01A
4236 | Slave09 Outlet Port35 Current | RO | 2 bytes | Unit:0.01A
4237 | Slave09 Outlet Port36 Current | RO | 2 bytes | Unit:0.01A
4238 | Slave09 Outlet Port37 Current | RO | 2 bytes | Unit:0.01A
4239 | Slave09 Outlet Port38 Current | RO | 2 bytes | Unit:0.01A
4240 | Slave09 Outlet Port39 Current | RO | 2 bytes | Unit:0.01A
4241 | Slave09 Outlet Port40 Current | RO | 2 bytes | Unit:0.01A
4242 | Slave09 Outlet Port41 Current | RO | 2 bytes | Unit:0.01A
4243 | Slave09 Outlet Port42 Current | RO | 2 bytes | Unit:0.01A
4244 | Slave10 Outlet Port01 Current | RO | 2 bytes | Unit:0.01A
4245 | Slave10 Outlet Port02 Current | RO | 2 bytes | Unit:0.01A
4246 | Slave10 Outlet Port03 Current | RO | 2 bytes | Unit:0.01A
4247 | Slave10 Outlet Port04 Current | RO | 2 bytes | Unit:0.01A
4248 | Slave10 Outlet Port05 Current | RO | 2 bytes | Unit:0.01A
4249 | Slave10 Outlet Port06 Current | RO | 2 bytes | Unit:0.01A
4250 | Slave10 Outlet Port07 Current | RO | 2 bytes | Unit:0.01A
4251 | Slave10 Outlet Port08 Current | RO | 2 bytes | Unit:0.01A
4252 | Slave10 Outlet Port09 Current | RO | 2 bytes | Unit:0.01A
4253 | Slave10 Outlet Port10 Current | RO | 2 bytes | Unit:0.01A
4254 | Slave10 Outlet Port11 Current | RO | 2 bytes | Unit:0.01A
4255 | Slave10 Outlet Port12 Current | RO | 2 bytes | Unit:0.01A
4256 | Slave10 Outlet Port13 Current | RO | 2 bytes | Unit:0.01A
4257 | Slave10 Outlet Port14 Current | RO | 2 bytes | Unit:0.01A
4258 | Slave10 Outlet Port15 Current | RO | 2 bytes | Unit:0.01A
4259 | Slave10 Outlet Port16 Current | RO | 2 bytes | Unit:0.01A
4260 | Slave10 Outlet Port17 Current | RO | 2 bytes | Unit:0.01A
4261 | Slave10 Outlet Port18 Current | RO | 2 bytes | Unit:0.01A
4262 | Slave10 Outlet Port19 Current | RO | 2 bytes | Unit:0.01A
4263 | Slave10 Outlet Port20 Current | RO | 2 bytes | Unit:0.01A
4264 | Slave10 Outlet Port21 Current | RO | 2 bytes | Unit:0.01A
4265 | Slave10 Outlet Port22 Current | RO | 2 bytes | Unit:0.01A
4266 | Slave10 Outlet Port23 Current | RO | 2 bytes | Unit:0.01A
4267 | Slave10 Outlet Port24 Current | RO | 2 bytes | Unit:0.01A
4268 | Slave10 Outlet Port25 Current | RO | 2 bytes | Unit:0.01A
4269 | Slave10 Outlet Port26 Current | RO | 2 bytes | Unit:0.01A
4270 | Slave10 Outlet Port27 Current | RO | 2 bytes | Unit:0.01A
4271 | Slave10 Outlet Port28 Current | RO | 2 bytes | Unit:0.01A
4272 | Slave10 Outlet Port29 Current | RO | 2 bytes | Unit:0.01A
4273 | Slave10 Outlet Port30 Current | RO | 2 bytes | Unit:0.01A
4274 | Slave10 Outlet Port31 Current | RO | 2 bytes | Unit:0.01A
4275 | Slave10 Outlet Port32 Current | RO | 2 bytes | Unit:0.01A
4276 | Slave10 Outlet Port33 Current | RO | 2 bytes | Unit:0.01A
4277 | Slave10 Outlet Port34 Current | RO | 2 bytes | Unit:0.01A
4278 | Slave10 Outlet Port35 Current | RO | 2 bytes | Unit:0.01A
4279 | Slave10 Outlet Port36 Current | RO | 2 bytes | Unit:0.01A
4280 | Slave10 Outlet Port37 Current | RO | 2 bytes | Unit:0.01A
4281 | Slave10 Outlet Port38 Current | RO | 2 bytes | Unit:0.01A
4282 | Slave10 Outlet Port39 Current | RO | 2 bytes | Unit:0.01A
4283 | Slave10 Outlet Port40 Current | RO | 2 bytes | Unit:0.01A
4284 | Slave10 Outlet Port41 Current | RO | 2 bytes | Unit:0.01A
4285 | Slave10 Outlet Port42 Current | RO | 2 bytes | Unit:0.01A
4286 | Slave11 Outlet Port01 Current | RO | 2 bytes | Unit:0.01A
4287 | Slave11 Outlet Port02 Current | RO | 2 bytes | Unit:0.01A
4288 | Slave11 Outlet Port03 Current | RO | 2 bytes | Unit:0.01A
4289 | Slave11 Outlet Port04 Current | RO | 2 bytes | Unit:0.01A
4290 | Slave11 Outlet Port05 Current | RO | 2 bytes | Unit:0.01A
4291 | Slave11 Outlet Port06 Current | RO | 2 bytes | Unit:0.01A
4292 | Slave11 Outlet Port07 Current | RO | 2 bytes | Unit:0.01A
4293 | Slave11 Outlet Port08 Current | RO | 2 bytes | Unit:0.01A
4294 | Slave11 Outlet Port09 Current | RO | 2 bytes | Unit:0.01A
4295 | Slave11 Outlet Port10 Current | RO | 2 bytes | Unit:0.01A
4296 | Slave11 Outlet Port11 Current | RO | 2 bytes | Unit:0.01A
4297 | Slave11 Outlet Port12 Current | RO | 2 bytes | Unit:0.01A
4298 | Slave11 Outlet Port13 Current | RO | 2 bytes | Unit:0.01A
4299 | Slave11 Outlet Port14 Current | RO | 2 bytes | Unit:0.01A
4300 | Slave11 Outlet Port15 Current | RO | 2 bytes | Unit:0.01A
4301 | Slave11 Outlet Port16 Current | RO | 2 bytes | Unit:0.01A
4302 | Slave11 Outlet Port17 Current | RO | 2 bytes | Unit:0.01A
4303 | Slave11 Outlet Port18 Current | RO | 2 bytes | Unit:0.01A
4304 | Slave11 Outlet Port19 Current | RO | 2 bytes | Unit:0.01A
4305 | Slave11 Outlet Port20 Current | RO | 2 bytes | Unit:0.01A
4306 | Slave11 Outlet Port21 Current | RO | 2 bytes | Unit:0.01A
4307 | Slave11 Outlet Port22 Current | RO | 2 bytes | Unit:0.01A
4308 | Slave11 Outlet Port23 Current | RO | 2 bytes | Unit:0.01A
4309 | Slave11 Outlet Port24 Current | RO | 2 bytes | Unit:0.01A
4310 | Slave11 Outlet Port25 Current | RO | 2 bytes | Unit:0.01A
4311 | Slave11 Outlet Port26 Current | RO | 2 bytes | Unit:0.01A
4312 | Slave11 Outlet Port27 Current | RO | 2 bytes | Unit:0.01A
4313 | Slave11 Outlet Port28 Current | RO | 2 bytes | Unit:0.01A
4314 | Slave11 Outlet Port29 Current | RO | 2 bytes | Unit:0.01A
4315 | Slave11 Outlet Port30 Current | RO | 2 bytes | Unit:0.01A
4316 | Slave11 Outlet Port31 Current | RO | 2 bytes | Unit:0.01A
4317 | Slave11 Outlet Port32 Current | RO | 2 bytes | Unit:0.01A
4318 | Slave11 Outlet Port33 Current | RO | 2 bytes | Unit:0.01A
4319 | Slave11 Outlet Port34 Current | RO | 2 bytes | Unit:0.01A
4320 | Slave11 Outlet Port35 Current | RO | 2 bytes | Unit:0.01A
4321 | Slave11 Outlet Port36 Current | RO | 2 bytes | Unit:0.01A
4322 | Slave11 Outlet Port37 Current | RO | 2 bytes | Unit:0.01A
4323 | Slave11 Outlet Port38 Current | RO | 2 bytes | Unit:0.01A
4324 | Slave11 Outlet Port39 Current | RO | 2 bytes | Unit:0.01A
4325 | Slave11 Outlet Port40 Current | RO | 2 bytes | Unit:0.01A
4326 | Slave11 Outlet Port41 Current | RO | 2 bytes | Unit:0.01A
4327 | Slave11 Outlet Port42 Current | RO | 2 bytes | Unit:0.01A
4328 | Slave12 Outlet Port01 Current | RO | 2 bytes | Unit:0.01A
4329 | Slave12 Outlet Port02 Current | RO | 2 bytes | Unit:0.01A
4330 | Slave12 Outlet Port03 Current | RO | 2 bytes | Unit:0.01A
4331 | Slave12 Outlet Port04 Current | RO | 2 bytes | Unit:0.01A
4332 | Slave12 Outlet Port05 Current | RO | 2 bytes | Unit:0.01A
4333 | Slave12 Outlet Port06 Current | RO | 2 bytes | Unit:0.01A
4334 | Slave12 Outlet Port07 Current | RO | 2 bytes | Unit:0.01A
4335 | Slave12 Outlet Port08 Current | RO | 2 bytes | Unit:0.01A
4336 | Slave12 Outlet Port09 Current | RO | 2 bytes | Unit:0.01A
4337 | Slave12 Outlet Port10 Current | RO | 2 bytes | Unit:0.01A
4338 | Slave12 Outlet Port11 Current | RO | 2 bytes | Unit:0.01A
4339 | Slave12 Outlet Port12 Current | RO | 2 bytes | Unit:0.01A
4340 | Slave12 Outlet Port13 Current | RO | 2 bytes | Unit:0.01A
4341 | Slave12 Outlet Port14 Current | RO | 2 bytes | Unit:0.01A
4342 | Slave12 Outlet Port15 Current | RO | 2 bytes | Unit:0.01A
4343 | Slave12 Outlet Port16 Current | RO | 2 bytes | Unit:0.01A
4344 | Slave12 Outlet Port17 Current | RO | 2 bytes | Unit:0.01A
4345 | Slave12 Outlet Port18 Current | RO | 2 bytes | Unit:0.01A
4346 | Slave12 Outlet Port19 Current | RO | 2 bytes | Unit:0.01A
4347 | Slave12 Outlet Port20 Current | RO | 2 bytes | Unit:0.01A
4348 | Slave12 Outlet Port21 Current | RO | 2 bytes | Unit:0.01A
4349 | Slave12 Outlet Port22 Current | RO | 2 bytes | Unit:0.01A
4350 | Slave12 Outlet Port23 Current | RO | 2 bytes | Unit:0.01A
4351 | Slave12 Outlet Port24 Current | RO | 2 bytes | Unit:0.01A
4352 | Slave12 Outlet Port25 Current | RO | 2 bytes | Unit:0.01A
4353 | Slave12 Outlet Port26 Current | RO | 2 bytes | Unit:0.01A
4354 | Slave12 Outlet Port27 Current | RO | 2 bytes | Unit:0.01A
4355 | Slave12 Outlet Port28 Current | RO | 2 bytes | Unit:0.01A
4356 | Slave12 Outlet Port29 Current | RO | 2 bytes | Unit:0.01A
4357 | Slave12 Outlet Port30 Current | RO | 2 bytes | Unit:0.01A
4358 | Slave12 Outlet Port31 Current | RO | 2 bytes | Unit:0.01A
4359 | Slave12 Outlet Port32 Current | RO | 2 bytes | Unit:0.01A
4360 | Slave12 Outlet Port33 Current | RO | 2 bytes | Unit:0.01A
4361 | Slave12 Outlet Port34 Current | RO | 2 bytes | Unit:0.01A
4362 | Slave12 Outlet Port35 Current | RO | 2 bytes | Unit:0.01A
4363 | Slave12 Outlet Port36 Current | RO | 2 bytes | Unit:0.01A
4364 | Slave12 Outlet Port37 Current | RO | 2 bytes | Unit:0.01A
4365 | Slave12 Outlet Port38 Current | RO | 2 bytes | Unit:0.01A
4366 | Slave12 Outlet Port39 Current | RO | 2 bytes | Unit:0.01A
4367 | Slave12 Outlet Port40 Current | RO | 2 bytes | Unit:0.01A
4368 | Slave12 Outlet Port41 Current | RO | 2 bytes | Unit:0.01A
4369 | Slave12 Outlet Port42 Current | RO | 2 bytes | Unit:0.01A
4370 | Slave13 Outlet Port01 Current | RO | 2 bytes | Unit:0.01A
4371 | Slave13 Outlet Port02 Current | RO | 2 bytes | Unit:0.01A
4372 | Slave13 Outlet Port03 Current | RO | 2 bytes | Unit:0.01A
4373 | Slave13 Outlet Port04 Current | RO | 2 bytes | Unit:0.01A
4374 | Slave13 Outlet Port05 Current | RO | 2 bytes | Unit:0.01A
4375 | Slave13 Outlet Port06 Current | RO | 2 bytes | Unit:0.01A
4376 | Slave13 Outlet Port07 Current | RO | 2 bytes | Unit:0.01A
4377 | Slave13 Outlet Port08 Current | RO | 2 bytes | Unit:0.01A
4378 | Slave13 Outlet Port09 Current | RO | 2 bytes | Unit:0.01A
4379 | Slave13 Outlet Port10 Current | RO | 2 bytes | Unit:0.01A
4380 | Slave13 Outlet Port11 Current | RO | 2 bytes | Unit:0.01A
4381 | Slave13 Outlet Port12 Current | RO | 2 bytes | Unit:0.01A
4382 | Slave13 Outlet Port13 Current | RO | 2 bytes | Unit:0.01A
4383 | Slave13 Outlet Port14 Current | RO | 2 bytes | Unit:0.01A
4384 | Slave13 Outlet Port15 Current | RO | 2 bytes | Unit:0.01A
4385 | Slave13 Outlet Port16 Current | RO | 2 bytes | Unit:0.01A
4386 | Slave13 Outlet Port17 Current | RO | 2 bytes | Unit:0.01A
4387 | Slave13 Outlet Port18 Current | RO | 2 bytes | Unit:0.01A
4388 | Slave13 Outlet Port19 Current | RO | 2 bytes | Unit:0.01A
4389 | Slave13 Outlet Port20 Current | RO | 2 bytes | Unit:0.01A
4390 | Slave13 Outlet Port21 Current | RO | 2 bytes | Unit:0.01A
4391 | Slave13 Outlet Port22 Current | RO | 2 bytes | Unit:0.01A
4392 | Slave13 Outlet Port23 Current | RO | 2 bytes | Unit:0.01A
4393 | Slave13 Outlet Port24 Current | RO | 2 bytes | Unit:0.01A
4394 | Slave13 Outlet Port25 Current | RO | 2 bytes | Unit:0.01A
4395 | Slave13 Outlet Port26 Current | RO | 2 bytes | Unit:0.01A
4396 | Slave13 Outlet Port27 Current | RO | 2 bytes | Unit:0.01A
4397 | Slave13 Outlet Port28 Current | RO | 2 bytes | Unit:0.01A
4398 | Slave13 Outlet Port29 Current | RO | 2 bytes | Unit:0.01A
4399 | Slave13 Outlet Port30 Current | RO | 2 bytes | Unit:0.01A
4400 | Slave13 Outlet Port31 Current | RO | 2 bytes | Unit:0.01A
4401 | Slave13 Outlet Port32 Current | RO | 2 bytes | Unit:0.01A
4402 | Slave13 Outlet Port33 Current | RO | 2 bytes | Unit:0.01A
4403 | Slave13 Outlet Port34 Current | RO | 2 bytes | Unit:0.01A
4404 | Slave13 Outlet Port35 Current | RO | 2 bytes | Unit:0.01A
4405 | Slave13 Outlet Port36 Current | RO | 2 bytes | Unit:0.01A
4406 | Slave13 Outlet Port37 Current | RO | 2 bytes | Unit:0.01A
4407 | Slave13 Outlet Port38 Current | RO | 2 bytes | Unit:0.01A
4408 | Slave13 Outlet Port39 Current | RO | 2 bytes | Unit:0.01A
4409 | Slave13 Outlet Port40 Current | RO | 2 bytes | Unit:0.01A
4410 | Slave13 Outlet Port41 Current | RO | 2 bytes | Unit:0.01A
4411 | Slave13 Outlet Port42 Current | RO | 2 bytes | Unit:0.01A
4412 | Slave14 Outlet Port01 Current | RO | 2 bytes | Unit:0.01A
4413 | Slave14 Outlet Port02 Current | RO | 2 bytes | Unit:0.01A
4414 | Slave14 Outlet Port03 Current | RO | 2 bytes | Unit:0.01A
4415 | Slave14 Outlet Port04 Current | RO | 2 bytes | Unit:0.01A
4416 | Slave14 Outlet Port05 Current | RO | 2 bytes | Unit:0.01A
4417 | Slave14 Outlet Port06 Current | RO | 2 bytes | Unit:0.01A
4418 | Slave14 Outlet Port07 Current | RO | 2 bytes | Unit:0.01A
4419 | Slave14 Outlet Port08 Current | RO | 2 bytes | Unit:0.01A
4420 | Slave14 Outlet Port09 Current | RO | 2 bytes | Unit:0.01A
4421 | Slave14 Outlet Port10 Current | RO | 2 bytes | Unit:0.01A
4422 | Slave14 Outlet Port11 Current | RO | 2 bytes | Unit:0.01A
4423 | Slave14 Outlet Port12 Current | RO | 2 bytes | Unit:0.01A
4424 | Slave14 Outlet Port13 Current | RO | 2 bytes | Unit:0.01A
4425 | Slave14 Outlet Port14 Current | RO | 2 bytes | Unit:0.01A
4426 | Slave14 Outlet Port15 Current | RO | 2 bytes | Unit:0.01A
4427 | Slave14 Outlet Port16 Current | RO | 2 bytes | Unit:0.01A
4428 | Slave14 Outlet Port17 Current | RO | 2 bytes | Unit:0.01A
4429 | Slave14 Outlet Port18 Current | RO | 2 bytes | Unit:0.01A
4430 | Slave14 Outlet Port19 Current | RO | 2 bytes | Unit:0.01A
4431 | Slave14 Outlet Port20 Current | RO | 2 bytes | Unit:0.01A
4432 | Slave14 Outlet Port21 Current | RO | 2 bytes | Unit:0.01A
4433 | Slave14 Outlet Port22 Current | RO | 2 bytes | Unit:0.01A
4434 | Slave14 Outlet Port23 Current | RO | 2 bytes | Unit:0.01A
4435 | Slave14 Outlet Port24 Current | RO | 2 bytes | Unit:0.01A
4436 | Slave14 Outlet Port25 Current | RO | 2 bytes | Unit:0.01A
4437 | Slave14 Outlet Port26 Current | RO | 2 bytes | Unit:0.01A
4438 | Slave14 Outlet Port27 Current | RO | 2 bytes | Unit:0.01A
4439 | Slave14 Outlet Port28 Current | RO | 2 bytes | Unit:0.01A
4440 | Slave14 Outlet Port29 Current | RO | 2 bytes | Unit:0.01A
4441 | Slave14 Outlet Port30 Current | RO | 2 bytes | Unit:0.01A
4442 | Slave14 Outlet Port31 Current | RO | 2 bytes | Unit:0.01A
4443 | Slave14 Outlet Port32 Current | RO | 2 bytes | Unit:0.01A
4444 | Slave14 Outlet Port33 Current | RO | 2 bytes | Unit:0.01A
4445 | Slave14 Outlet Port34 Current | RO | 2 bytes | Unit:0.01A
4446 | Slave14 Outlet Port35 Current | RO | 2 bytes | Unit:0.01A
4447 | Slave14 Outlet Port36 Current | RO | 2 bytes | Unit:0.01A
4448 | Slave14 Outlet Port37 Current | RO | 2 bytes | Unit:0.01A
4449 | Slave14 Outlet Port38 Current | RO | 2 bytes | Unit:0.01A
4450 | Slave14 Outlet Port39 Current | RO | 2 bytes | Unit:0.01A
4451 | Slave14 Outlet Port40 Current | RO | 2 bytes | Unit:0.01A
4452 | Slave14 Outlet Port41 Current | RO | 2 bytes | Unit:0.01A
4453 | Slave14 Outlet Port42 Current | RO | 2 bytes | Unit:0.01A
4454 | Slave15 Outlet Port01 Current | RO | 2 bytes | Unit:0.01A
4455 | Slave15 Outlet Port02 Current | RO | 2 bytes | Unit:0.01A
4456 | Slave15 Outlet Port03 Current | RO | 2 bytes | Unit:0.01A
4457 | Slave15 Outlet Port04 Current | RO | 2 bytes | Unit:0.01A
4458 | Slave15 Outlet Port05 Current | RO | 2 bytes | Unit:0.01A
4459 | Slave15 Outlet Port06 Current | RO | 2 bytes | Unit:0.01A
4460 | Slave15 Outlet Port07 Current | RO | 2 bytes | Unit:0.01A
4461 | Slave15 Outlet Port08 Current | RO | 2 bytes | Unit:0.01A
4462 | Slave15 Outlet Port09 Current | RO | 2 bytes | Unit:0.01A
4463 | Slave15 Outlet Port10 Current | RO | 2 bytes | Unit:0.01A
4464 | Slave15 Outlet Port11 Current | RO | 2 bytes | Unit:0.01A
4465 | Slave15 Outlet Port12 Current | RO | 2 bytes | Unit:0.01A
4466 | Slave15 Outlet Port13 Current | RO | 2 bytes | Unit:0.01A
4467 | Slave15 Outlet Port14 Current | RO | 2 bytes | Unit:0.01A
4468 | Slave15 Outlet Port15 Current | RO | 2 bytes | Unit:0.01A
4469 | Slave15 Outlet Port16 Current | RO | 2 bytes | Unit:0.01A
4470 | Slave15 Outlet Port17 Current | RO | 2 bytes | Unit:0.01A
4471 | Slave15 Outlet Port18 Current | RO | 2 bytes | Unit:0.01A
4472 | Slave15 Outlet Port19 Current | RO | 2 bytes | Unit:0.01A
4473 | Slave15 Outlet Port20 Current | RO | 2 bytes | Unit:0.01A
4474 | Slave15 Outlet Port21 Current | RO | 2 bytes | Unit:0.01A
4475 | Slave15 Outlet Port22 Current | RO | 2 bytes | Unit:0.01A
4476 | Slave15 Outlet Port23 Current | RO | 2 bytes | Unit:0.01A
4477 | Slave15 Outlet Port24 Current | RO | 2 bytes | Unit:0.01A
4478 | Slave15 Outlet Port25 Current | RO | 2 bytes | Unit:0.01A
4479 | Slave15 Outlet Port26 Current | RO | 2 bytes | Unit:0.01A
4480 | Slave15 Outlet Port27 Current | RO | 2 bytes | Unit:0.01A
4481 | Slave15 Outlet Port28 Current | RO | 2 bytes | Unit:0.01A
4482 | Slave15 Outlet Port29 Current | RO | 2 bytes | Unit:0.01A
4483 | Slave15 Outlet Port30 Current | RO | 2 bytes | Unit:0.01A
4484 | Slave15 Outlet Port31 Current | RO | 2 bytes | Unit:0.01A
4485 | Slave15 Outlet Port32 Current | RO | 2 bytes | Unit:0.01A
4486 | Slave15 Outlet Port33 Current | RO | 2 bytes | Unit:0.01A
4487 | Slave15 Outlet Port34 Current | RO | 2 bytes | Unit:0.01A
4488 | Slave15 Outlet Port35 Current | RO | 2 bytes | Unit:0.01A
4489 | Slave15 Outlet Port36 Current | RO | 2 bytes | Unit:0.01A
4490 | Slave15 Outlet Port37 Current | RO | 2 bytes | Unit:0.01A
4491 | Slave15 Outlet Port38 Current | RO | 2 bytes | Unit:0.01A
4492 | Slave15 Outlet Port39 Current | RO | 2 bytes | Unit:0.01A
4493 | Slave15 Outlet Port40 Current | RO | 2 bytes | Unit:0.01A
4494 | Slave15 Outlet Port41 Current | RO | 2 bytes | Unit:0.01A
4495 | Slave15 Outlet Port42 Current | RO | 2 bytes | Unit:0.01A
4496 | Master Outlet Port01 PF | RO | 2 bytes | Unit:0.01
4497 | Master Outlet Port02 PF | RO | 2 bytes | Unit:0.01
4498 | Master Outlet Port03 PF | RO | 2 bytes | Unit:0.01
4499 | Master Outlet Port04 PF | RO | 2 bytes | Unit:0.01
4500 | Master Outlet Port05 PF | RO | 2 bytes | Unit:0.01
4501 | Master Outlet Port06 PF | RO | 2 bytes | Unit:0.01
4502 | Master Outlet Port07 PF | RO | 2 bytes | Unit:0.01
4503 | Master Outlet Port08 PF | RO | 2 bytes | Unit:0.01
4504 | Master Outlet Port09 PF | RO | 2 bytes | Unit:0.01
4505 | Master Outlet Port10 PF | RO | 2 bytes | Unit:0.01
4506 | Master Outlet Port11 PF | RO | 2 bytes | Unit:0.01
4507 | Master Outlet Port12 PF | RO | 2 bytes | Unit:0.01
4508 | Master Outlet Port13 PF | RO | 2 bytes | Unit:0.01
4509 | Master Outlet Port14 PF | RO | 2 bytes | Unit:0.01
4510 | Master Outlet Port15 PF | RO | 2 bytes | Unit:0.01
4511 | Master Outlet Port16 PF | RO | 2 bytes | Unit:0.01
4512 | Master Outlet Port17 PF | RO | 2 bytes | Unit:0.01
4513 | Master Outlet Port18 PF | RO | 2 bytes | Unit:0.01
4514 | Master Outlet Port19 PF | RO | 2 bytes | Unit:0.01
4515 | Master Outlet Port20 PF | RO | 2 bytes | Unit:0.01
4516 | Master Outlet Port21 PF | RO | 2 bytes | Unit:0.01
4517 | Master Outlet Port22 PF | RO | 2 bytes | Unit:0.01
4518 | Master Outlet Port23 PF | RO | 2 bytes | Unit:0.01
4519 | Master Outlet Port24 PF | RO | 2 bytes | Unit:0.01
4520 | Master Outlet Port25 PF | RO | 2 bytes | Unit:0.01
4521 | Master Outlet Port26 PF | RO | 2 bytes | Unit:0.01
4522 | Master Outlet Port27 PF | RO | 2 bytes | Unit:0.01
4523 | Master Outlet Port28 PF | RO | 2 bytes | Unit:0.01
4524 | Master Outlet Port29 PF | RO | 2 bytes | Unit:0.01
4525 | Master Outlet Port30 PF | RO | 2 bytes | Unit:0.01
4526 | Master Outlet Port31 PF | RO | 2 bytes | Unit:0.01
4527 | Master Outlet Port32 PF | RO | 2 bytes | Unit:0.01
4528 | Master Outlet Port33 PF | RO | 2 bytes | Unit:0.01
4529 | Master Outlet Port34 PF | RO | 2 bytes | Unit:0.01
4530 | Master Outlet Port35 PF | RO | 2 bytes | Unit:0.01
4531 | Master Outlet Port36 PF | RO | 2 bytes | Unit:0.01
4532 | Master Outlet Port37 PF | RO | 2 bytes | Unit:0.01
4533 | Master Outlet Port38 PF | RO | 2 bytes | Unit:0.01
4534 | Master Outlet Port39 PF | RO | 2 bytes | Unit:0.01
4535 | Master Outlet Port40 PF | RO | 2 bytes | Unit:0.01
4536 | Master Outlet Port41 PF | RO | 2 bytes | Unit:0.01
4537 | Master Outlet Port42 PF | RO | 2 bytes | Unit:0.01
4538 | Slave01 Outlet Port01 PF | RO | 2 bytes | Unit:0.01
4539 | Slave01 Outlet Port02 PF | RO | 2 bytes | Unit:0.01
4540 | Slave01 Outlet Port03 PF | RO | 2 bytes | Unit:0.01
4541 | Slave01 Outlet Port04 PF | RO | 2 bytes | Unit:0.01
4542 | Slave01 Outlet Port05 PF | RO | 2 bytes | Unit:0.01
4543 | Slave01 Outlet Port06 PF | RO | 2 bytes | Unit:0.01
4544 | Slave01 Outlet Port07 PF | RO | 2 bytes | Unit:0.01
4545 | Slave01 Outlet Port08 PF | RO | 2 bytes | Unit:0.01
4546 | Slave01 Outlet Port09 PF | RO | 2 bytes | Unit:0.01
4547 | Slave01 Outlet Port10 PF | RO | 2 bytes | Unit:0.01
4548 | Slave01 Outlet Port11 PF | RO | 2 bytes | Unit:0.01
4549 | Slave01 Outlet Port12 PF | RO | 2 bytes | Unit:0.01
4550 | Slave01 Outlet Port13 PF | RO | 2 bytes | Unit:0.01
4551 | Slave01 Outlet Port14 PF | RO | 2 bytes | Unit:0.01
4552 | Slave01 Outlet Port15 PF | RO | 2 bytes | Unit:0.01
4553 | Slave01 Outlet Port16 PF | RO | 2 bytes | Unit:0.01
4554 | Slave01 Outlet Port17 PF | RO | 2 bytes | Unit:0.01
4555 | Slave01 Outlet Port18 PF | RO | 2 bytes | Unit:0.01
4556 | Slave01 Outlet Port19 PF | RO | 2 bytes | Unit:0.01
4557 | Slave01 Outlet Port20 PF | RO | 2 bytes | Unit:0.01
4558 | Slave01 Outlet Port21 PF | RO | 2 bytes | Unit:0.01
4559 | Slave01 Outlet Port22 PF | RO | 2 bytes | Unit:0.01
4560 | Slave01 Outlet Port23 PF | RO | 2 bytes | Unit:0.01
4561 | Slave01 Outlet Port24 PF | RO | 2 bytes | Unit:0.01
4562 | Slave01 Outlet Port25 PF | RO | 2 bytes | Unit:0.01
4563 | Slave01 Outlet Port26 PF | RO | 2 bytes | Unit:0.01
4564 | Slave01 Outlet Port27 PF | RO | 2 bytes | Unit:0.01
4565 | Slave01 Outlet Port28 PF | RO | 2 bytes | Unit:0.01
4566 | Slave01 Outlet Port29 PF | RO | 2 bytes | Unit:0.01
4567 | Slave01 Outlet Port30 PF | RO | 2 bytes | Unit:0.01
4568 | Slave01 Outlet Port31 PF | RO | 2 bytes | Unit:0.01
4569 | Slave01 Outlet Port32 PF | RO | 2 bytes | Unit:0.01
4570 | Slave01 Outlet Port33 PF | RO | 2 bytes | Unit:0.01
4571 | Slave01 Outlet Port34 PF | RO | 2 bytes | Unit:0.01
4572 | Slave01 Outlet Port35 PF | RO | 2 bytes | Unit:0.01
4573 | Slave01 Outlet Port36 PF | RO | 2 bytes | Unit:0.01
4574 | Slave01 Outlet Port37 PF | RO | 2 bytes | Unit:0.01
4575 | Slave01 Outlet Port38 PF | RO | 2 bytes | Unit:0.01
4576 | Slave01 Outlet Port39 PF | RO | 2 bytes | Unit:0.01
4577 | Slave01 Outlet Port40 PF | RO | 2 bytes | Unit:0.01
4578 | Slave01 Outlet Port41 PF | RO | 2 bytes | Unit:0.01
4579 | Slave01 Outlet Port42 PF | RO | 2 bytes | Unit:0.01
4580 | Slave02 Outlet Port01 PF | RO | 2 bytes | Unit:0.01
4581 | Slave02 Outlet Port02 PF | RO | 2 bytes | Unit:0.01
4582 | Slave02 Outlet Port03 PF | RO | 2 bytes | Unit:0.01
4583 | Slave02 Outlet Port04 PF | RO | 2 bytes | Unit:0.01
4584 | Slave02 Outlet Port05 PF | RO | 2 bytes | Unit:0.01
4585 | Slave02 Outlet Port06 PF | RO | 2 bytes | Unit:0.01
4586 | Slave02 Outlet Port07 PF | RO | 2 bytes | Unit:0.01
4587 | Slave02 Outlet Port08 PF | RO | 2 bytes | Unit:0.01
4588 | Slave02 Outlet Port09 PF | RO | 2 bytes | Unit:0.01
4589 | Slave02 Outlet Port10 PF | RO | 2 bytes | Unit:0.01
4590 | Slave02 Outlet Port11 PF | RO | 2 bytes | Unit:0.01
4591 | Slave02 Outlet Port12 PF | RO | 2 bytes | Unit:0.01
4592 | Slave02 Outlet Port13 PF | RO | 2 bytes | Unit:0.01
4593 | Slave02 Outlet Port14 PF | RO | 2 bytes | Unit:0.01
4594 | Slave02 Outlet Port15 PF | RO | 2 bytes | Unit:0.01
4595 | Slave02 Outlet Port16 PF | RO | 2 bytes | Unit:0.01
4596 | Slave02 Outlet Port17 PF | RO | 2 bytes | Unit:0.01
4597 | Slave02 Outlet Port18 PF | RO | 2 bytes | Unit:0.01
4598 | Slave02 Outlet Port19 PF | RO | 2 bytes | Unit:0.01
4599 | Slave02 Outlet Port20 PF | RO | 2 bytes | Unit:0.01
4600 | Slave02 Outlet Port21 PF | RO | 2 bytes | Unit:0.01
4601 | Slave02 Outlet Port22 PF | RO | 2 bytes | Unit:0.01
4602 | Slave02 Outlet Port23 PF | RO | 2 bytes | Unit:0.01
4603 | Slave02 Outlet Port24 PF | RO | 2 bytes | Unit:0.01
4604 | Slave02 Outlet Port25 PF | RO | 2 bytes | Unit:0.01
4605 | Slave02 Outlet Port26 PF | RO | 2 bytes | Unit:0.01
4606 | Slave02 Outlet Port27 PF | RO | 2 bytes | Unit:0.01
4607 | Slave02 Outlet Port28 PF | RO | 2 bytes | Unit:0.01
4608 | Slave02 Outlet Port29 PF | RO | 2 bytes | Unit:0.01
4609 | Slave02 Outlet Port30 PF | RO | 2 bytes | Unit:0.01
4610 | Slave02 Outlet Port31 PF | RO | 2 bytes | Unit:0.01
4611 | Slave02 Outlet Port32 PF | RO | 2 bytes | Unit:0.01
4612 | Slave02 Outlet Port33 PF | RO | 2 bytes | Unit:0.01
4613 | Slave02 Outlet Port34 PF | RO | 2 bytes | Unit:0.01
4614 | Slave02 Outlet Port35 PF | RO | 2 bytes | Unit:0.01
4615 | Slave02 Outlet Port36 PF | RO | 2 bytes | Unit:0.01
4616 | Slave02 Outlet Port37 PF | RO | 2 bytes | Unit:0.01
4617 | Slave02 Outlet Port38 PF | RO | 2 bytes | Unit:0.01
4618 | Slave02 Outlet Port39 PF | RO | 2 bytes | Unit:0.01
4619 | Slave02 Outlet Port40 PF | RO | 2 bytes | Unit:0.01
4620 | Slave02 Outlet Port41 PF | RO | 2 bytes | Unit:0.01
4621 | Slave02 Outlet Port42 PF | RO | 2 bytes | Unit:0.01
4622 | Slave03 Outlet Port01 PF | RO | 2 bytes | Unit:0.01
4623 | Slave03 Outlet Port02 PF | RO | 2 bytes | Unit:0.01
4624 | Slave03 Outlet Port03 PF | RO | 2 bytes | Unit:0.01
4625 | Slave03 Outlet Port04 PF | RO | 2 bytes | Unit:0.01
4626 | Slave03 Outlet Port05 PF | RO | 2 bytes | Unit:0.01
4627 | Slave03 Outlet Port06 PF | RO | 2 bytes | Unit:0.01
4628 | Slave03 Outlet Port07 PF | RO | 2 bytes | Unit:0.01
4629 | Slave03 Outlet Port08 PF | RO | 2 bytes | Unit:0.01
4630 | Slave03 Outlet Port09 PF | RO | 2 bytes | Unit:0.01
4631 | Slave03 Outlet Port10 PF | RO | 2 bytes | Unit:0.01
4632 | Slave03 Outlet Port11 PF | RO | 2 bytes | Unit:0.01
4633 | Slave03 Outlet Port12 PF | RO | 2 bytes | Unit:0.01
4634 | Slave03 Outlet Port13 PF | RO | 2 bytes | Unit:0.01
4635 | Slave03 Outlet Port14 PF | RO | 2 bytes | Unit:0.01
4636 | Slave03 Outlet Port15 PF | RO | 2 bytes | Unit:0.01
4637 | Slave03 Outlet Port16 PF | RO | 2 bytes | Unit:0.01
4638 | Slave03 Outlet Port17 PF | RO | 2 bytes | Unit:0.01
4639 | Slave03 Outlet Port18 PF | RO | 2 bytes | Unit:0.01
4640 | Slave03 Outlet Port19 PF | RO | 2 bytes | Unit:0.01
4641 | Slave03 Outlet Port20 PF | RO | 2 bytes | Unit:0.01
4642 | Slave03 Outlet Port21 PF | RO | 2 bytes | Unit:0.01
4643 | Slave03 Outlet Port22 PF | RO | 2 bytes | Unit:0.01
4644 | Slave03 Outlet Port23 PF | RO | 2 bytes | Unit:0.01
4645 | Slave03 Outlet Port24 PF | RO | 2 bytes | Unit:0.01
4646 | Slave03 Outlet Port25 PF | RO | 2 bytes | Unit:0.01
4647 | Slave03 Outlet Port26 PF | RO | 2 bytes | Unit:0.01
4648 | Slave03 Outlet Port27 PF | RO | 2 bytes | Unit:0.01
4649 | Slave03 Outlet Port28 PF | RO | 2 bytes | Unit:0.01
4650 | Slave03 Outlet Port29 PF | RO | 2 bytes | Unit:0.01
4651 | Slave03 Outlet Port30 PF | RO | 2 bytes | Unit:0.01
4652 | Slave03 Outlet Port31 PF | RO | 2 bytes | Unit:0.01
4653 | Slave03 Outlet Port32 PF | RO | 2 bytes | Unit:0.01
4654 | Slave03 Outlet Port33 PF | RO | 2 bytes | Unit:0.01
4655 | Slave03 Outlet Port34 PF | RO | 2 bytes | Unit:0.01
4656 | Slave03 Outlet Port35 PF | RO | 2 bytes | Unit:0.01
4657 | Slave03 Outlet Port36 PF | RO | 2 bytes | Unit:0.01
4658 | Slave03 Outlet Port37 PF | RO | 2 bytes | Unit:0.01
4659 | Slave03 Outlet Port38 PF | RO | 2 bytes | Unit:0.01
4660 | Slave03 Outlet Port39 PF | RO | 2 bytes | Unit:0.01
4661 | Slave03 Outlet Port40 PF | RO | 2 bytes | Unit:0.01
4662 | Slave03 Outlet Port41 PF | RO | 2 bytes | Unit:0.01
4663 | Slave03 Outlet Port42 PF | RO | 2 bytes | Unit:0.01
4664 | Slave04 Outlet Port01 PF | RO | 2 bytes | Unit:0.01
4665 | Slave04 Outlet Port02 PF | RO | 2 bytes | Unit:0.01
4666 | Slave04 Outlet Port03 PF | RO | 2 bytes | Unit:0.01
4667 | Slave04 Outlet Port04 PF | RO | 2 bytes | Unit:0.01
4668 | Slave04 Outlet Port05 PF | RO | 2 bytes | Unit:0.01
4669 | Slave04 Outlet Port06 PF | RO | 2 bytes | Unit:0.01
4670 | Slave04 Outlet Port07 PF | RO | 2 bytes | Unit:0.01
4671 | Slave04 Outlet Port08 PF | RO | 2 bytes | Unit:0.01
4672 | Slave04 Outlet Port09 PF | RO | 2 bytes | Unit:0.01
4673 | Slave04 Outlet Port10 PF | RO | 2 bytes | Unit:0.01
4674 | Slave04 Outlet Port11 PF | RO | 2 bytes | Unit:0.01
4675 | Slave04 Outlet Port12 PF | RO | 2 bytes | Unit:0.01
4676 | Slave04 Outlet Port13 PF | RO | 2 bytes | Unit:0.01
4677 | Slave04 Outlet Port14 PF | RO | 2 bytes | Unit:0.01
4678 | Slave04 Outlet Port15 PF | RO | 2 bytes | Unit:0.01
4679 | Slave04 Outlet Port16 PF | RO | 2 bytes | Unit:0.01
4680 | Slave04 Outlet Port17 PF | RO | 2 bytes | Unit:0.01
4681 | Slave04 Outlet Port18 PF | RO | 2 bytes | Unit:0.01
4682 | Slave04 Outlet Port19 PF | RO | 2 bytes | Unit:0.01
4683 | Slave04 Outlet Port20 PF | RO | 2 bytes | Unit:0.01
4684 | Slave04 Outlet Port21 PF | RO | 2 bytes | Unit:0.01
4685 | Slave04 Outlet Port22 PF | RO | 2 bytes | Unit:0.01
4686 | Slave04 Outlet Port23 PF | RO | 2 bytes | Unit:0.01
4687 | Slave04 Outlet Port24 PF | RO | 2 bytes | Unit:0.01
4688 | Slave04 Outlet Port25 PF | RO | 2 bytes | Unit:0.01
4689 | Slave04 Outlet Port26 PF | RO | 2 bytes | Unit:0.01
4690 | Slave04 Outlet Port27 PF | RO | 2 bytes | Unit:0.01
4691 | Slave04 Outlet Port28 PF | RO | 2 bytes | Unit:0.01
4692 | Slave04 Outlet Port29 PF | RO | 2 bytes | Unit:0.01
4693 | Slave04 Outlet Port30 PF | RO | 2 bytes | Unit:0.01
4694 | Slave04 Outlet Port31 PF | RO | 2 bytes | Unit:0.01
4695 | Slave04 Outlet Port32 PF | RO | 2 bytes | Unit:0.01
4696 | Slave04 Outlet Port33 PF | RO | 2 bytes | Unit:0.01
4697 | Slave04 Outlet Port34 PF | RO | 2 bytes | Unit:0.01
4698 | Slave04 Outlet Port35 PF | RO | 2 bytes | Unit:0.01
4699 | Slave04 Outlet Port36 PF | RO | 2 bytes | Unit:0.01
4700 | Slave04 Outlet Port37 PF | RO | 2 bytes | Unit:0.01
4701 | Slave04 Outlet Port38 PF | RO | 2 bytes | Unit:0.01
4702 | Slave04 Outlet Port39 PF | RO | 2 bytes | Unit:0.01
4703 | Slave04 Outlet Port40 PF | RO | 2 bytes | Unit:0.01
4704 | Slave04 Outlet Port41 PF | RO | 2 bytes | Unit:0.01
4705 | Slave04 Outlet Port42 PF | RO | 2 bytes | Unit:0.01
4706 | Slave05 Outlet Port01 PF | RO | 2 bytes | Unit:0.01
4707 | Slave05 Outlet Port02 PF | RO | 2 bytes | Unit:0.01
4708 | Slave05 Outlet Port03 PF | RO | 2 bytes | Unit:0.01
4709 | Slave05 Outlet Port04 PF | RO | 2 bytes | Unit:0.01
4710 | Slave05 Outlet Port05 PF | RO | 2 bytes | Unit:0.01
4711 | Slave05 Outlet Port06 PF | RO | 2 bytes | Unit:0.01
4712 | Slave05 Outlet Port07 PF | RO | 2 bytes | Unit:0.01
4713 | Slave05 Outlet Port08 PF | RO | 2 bytes | Unit:0.01
4714 | Slave05 Outlet Port09 PF | RO | 2 bytes | Unit:0.01
4715 | Slave05 Outlet Port10 PF | RO | 2 bytes | Unit:0.01
4716 | Slave05 Outlet Port11 PF | RO | 2 bytes | Unit:0.01
4717 | Slave05 Outlet Port12 PF | RO | 2 bytes | Unit:0.01
4718 | Slave05 Outlet Port13 PF | RO | 2 bytes | Unit:0.01
4719 | Slave05 Outlet Port14 PF | RO | 2 bytes | Unit:0.01
4720 | Slave05 Outlet Port15 PF | RO | 2 bytes | Unit:0.01
4721 | Slave05 Outlet Port16 PF | RO | 2 bytes | Unit:0.01
4722 | Slave05 Outlet Port17 PF | RO | 2 bytes | Unit:0.01
4723 | Slave05 Outlet Port18 PF | RO | 2 bytes | Unit:0.01
4724 | Slave05 Outlet Port19 PF | RO | 2 bytes | Unit:0.01
4725 | Slave05 Outlet Port20 PF | RO | 2 bytes | Unit:0.01
4726 | Slave05 Outlet Port21 PF | RO | 2 bytes | Unit:0.01
4727 | Slave05 Outlet Port22 PF | RO | 2 bytes | Unit:0.01
4728 | Slave05 Outlet Port23 PF | RO | 2 bytes | Unit:0.01
4729 | Slave05 Outlet Port24 PF | RO | 2 bytes | Unit:0.01
4730 | Slave05 Outlet Port25 PF | RO | 2 bytes | Unit:0.01
4731 | Slave05 Outlet Port26 PF | RO | 2 bytes | Unit:0.01
4732 | Slave05 Outlet Port27 PF | RO | 2 bytes | Unit:0.01
4733 | Slave05 Outlet Port28 PF | RO | 2 bytes | Unit:0.01
4734 | Slave05 Outlet Port29 PF | RO | 2 bytes | Unit:0.01
4735 | Slave05 Outlet Port30 PF | RO | 2 bytes | Unit:0.01
4736 | Slave05 Outlet Port31 PF | RO | 2 bytes | Unit:0.01
4737 | Slave05 Outlet Port32 PF | RO | 2 bytes | Unit:0.01
4738 | Slave05 Outlet Port33 PF | RO | 2 bytes | Unit:0.01
4739 | Slave05 Outlet Port34 PF | RO | 2 bytes | Unit:0.01
4740 | Slave05 Outlet Port35 PF | RO | 2 bytes | Unit:0.01
4741 | Slave05 Outlet Port36 PF | RO | 2 bytes | Unit:0.01
4742 | Slave05 Outlet Port37 PF | RO | 2 bytes | Unit:0.01
4743 | Slave05 Outlet Port38 PF | RO | 2 bytes | Unit:0.01
4744 | Slave05 Outlet Port39 PF | RO | 2 bytes | Unit:0.01
4745 | Slave05 Outlet Port40 PF | RO | 2 bytes | Unit:0.01
4746 | Slave05 Outlet Port41 PF | RO | 2 bytes | Unit:0.01
4747 | Slave05 Outlet Port42 PF | RO | 2 bytes | Unit:0.01
4748 | Slave06 Outlet Port01 PF | RO | 2 bytes | Unit:0.01
4749 | Slave06 Outlet Port02 PF | RO | 2 bytes | Unit:0.01
4750 | Slave06 Outlet Port03 PF | RO | 2 bytes | Unit:0.01
4751 | Slave06 Outlet Port04 PF | RO | 2 bytes | Unit:0.01
4752 | Slave06 Outlet Port05 PF | RO | 2 bytes | Unit:0.01
4753 | Slave06 Outlet Port06 PF | RO | 2 bytes | Unit:0.01
4754 | Slave06 Outlet Port07 PF | RO | 2 bytes | Unit:0.01
4755 | Slave06 Outlet Port08 PF | RO | 2 bytes | Unit:0.01
4756 | Slave06 Outlet Port09 PF | RO | 2 bytes | Unit:0.01
4757 | Slave06 Outlet Port10 PF | RO | 2 bytes | Unit:0.01
4758 | Slave06 Outlet Port11 PF | RO | 2 bytes | Unit:0.01
4759 | Slave06 Outlet Port12 PF | RO | 2 bytes | Unit:0.01
4760 | Slave06 Outlet Port13 PF | RO | 2 bytes | Unit:0.01
4761 | Slave06 Outlet Port14 PF | RO | 2 bytes | Unit:0.01
4762 | Slave06 Outlet Port15 PF | RO | 2 bytes | Unit:0.01
4763 | Slave06 Outlet Port16 PF | RO | 2 bytes | Unit:0.01
4764 | Slave06 Outlet Port17 PF | RO | 2 bytes | Unit:0.01
4765 | Slave06 Outlet Port18 PF | RO | 2 bytes | Unit:0.01
4766 | Slave06 Outlet Port19 PF | RO | 2 bytes | Unit:0.01
4767 | Slave06 Outlet Port20 PF | RO | 2 bytes | Unit:0.01
4768 | Slave06 Outlet Port21 PF | RO | 2 bytes | Unit:0.01
4769 | Slave06 Outlet Port22 PF | RO | 2 bytes | Unit:0.01
4770 | Slave06 Outlet Port23 PF | RO | 2 bytes | Unit:0.01
4771 | Slave06 Outlet Port24 PF | RO | 2 bytes | Unit:0.01
4772 | Slave06 Outlet Port25 PF | RO | 2 bytes | Unit:0.01
4773 | Slave06 Outlet Port26 PF | RO | 2 bytes | Unit:0.01
4774 | Slave06 Outlet Port27 PF | RO | 2 bytes | Unit:0.01
4775 | Slave06 Outlet Port28 PF | RO | 2 bytes | Unit:0.01
4776 | Slave06 Outlet Port29 PF | RO | 2 bytes | Unit:0.01
4777 | Slave06 Outlet Port30 PF | RO | 2 bytes | Unit:0.01
4778 | Slave06 Outlet Port31 PF | RO | 2 bytes | Unit:0.01
4779 | Slave06 Outlet Port32 PF | RO | 2 bytes | Unit:0.01
4780 | Slave06 Outlet Port33 PF | RO | 2 bytes | Unit:0.01
4781 | Slave06 Outlet Port34 PF | RO | 2 bytes | Unit:0.01
4782 | Slave06 Outlet Port35 PF | RO | 2 bytes | Unit:0.01
4783 | Slave06 Outlet Port36 PF | RO | 2 bytes | Unit:0.01
4784 | Slave06 Outlet Port37 PF | RO | 2 bytes | Unit:0.01
4785 | Slave06 Outlet Port38 PF | RO | 2 bytes | Unit:0.01
4786 | Slave06 Outlet Port39 PF | RO | 2 bytes | Unit:0.01
4787 | Slave06 Outlet Port40 PF | RO | 2 bytes | Unit:0.01
4788 | Slave06 Outlet Port41 PF | RO | 2 bytes | Unit:0.01
4789 | Slave06 Outlet Port42 PF | RO | 2 bytes | Unit:0.01
4790 | Slave07 Outlet Port01 PF | RO | 2 bytes | Unit:0.01
4791 | Slave07 Outlet Port02 PF | RO | 2 bytes | Unit:0.01
4792 | Slave07 Outlet Port03 PF | RO | 2 bytes | Unit:0.01
4793 | Slave07 Outlet Port04 PF | RO | 2 bytes | Unit:0.01
4794 | Slave07 Outlet Port05 PF | RO | 2 bytes | Unit:0.01
4795 | Slave07 Outlet Port06 PF | RO | 2 bytes | Unit:0.01
4796 | Slave07 Outlet Port07 PF | RO | 2 bytes | Unit:0.01
4797 | Slave07 Outlet Port08 PF | RO | 2 bytes | Unit:0.01
4798 | Slave07 Outlet Port09 PF | RO | 2 bytes | Unit:0.01
4799 | Slave07 Outlet Port10 PF | RO | 2 bytes | Unit:0.01
4800 | Slave07 Outlet Port11 PF | RO | 2 bytes | Unit:0.01
4801 | Slave07 Outlet Port12 PF | RO | 2 bytes | Unit:0.01
4802 | Slave07 Outlet Port13 PF | RO | 2 bytes | Unit:0.01
4803 | Slave07 Outlet Port14 PF | RO | 2 bytes | Unit:0.01
4804 | Slave07 Outlet Port15 PF | RO | 2 bytes | Unit:0.01
4805 | Slave07 Outlet Port16 PF | RO | 2 bytes | Unit:0.01
4806 | Slave07 Outlet Port17 PF | RO | 2 bytes | Unit:0.01
4807 | Slave07 Outlet Port18 PF | RO | 2 bytes | Unit:0.01
4808 | Slave07 Outlet Port19 PF | RO | 2 bytes | Unit:0.01
4809 | Slave07 Outlet Port20 PF | RO | 2 bytes | Unit:0.01
4810 | Slave07 Outlet Port21 PF | RO | 2 bytes | Unit:0.01
4811 | Slave07 Outlet Port22 PF | RO | 2 bytes | Unit:0.01
4812 | Slave07 Outlet Port23 PF | RO | 2 bytes | Unit:0.01
4813 | Slave07 Outlet Port24 PF | RO | 2 bytes | Unit:0.01
4814 | Slave07 Outlet Port25 PF | RO | 2 bytes | Unit:0.01
4815 | Slave07 Outlet Port26 PF | RO | 2 bytes | Unit:0.01
4816 | Slave07 Outlet Port27 PF | RO | 2 bytes | Unit:0.01
4817 | Slave07 Outlet Port28 PF | RO | 2 bytes | Unit:0.01
4818 | Slave07 Outlet Port29 PF | RO | 2 bytes | Unit:0.01
4819 | Slave07 Outlet Port30 PF | RO | 2 bytes | Unit:0.01
4820 | Slave07 Outlet Port31 PF | RO | 2 bytes | Unit:0.01
4821 | Slave07 Outlet Port32 PF | RO | 2 bytes | Unit:0.01
4822 | Slave07 Outlet Port33 PF | RO | 2 bytes | Unit:0.01
4823 | Slave07 Outlet Port34 PF | RO | 2 bytes | Unit:0.01
4824 | Slave07 Outlet Port35 PF | RO | 2 bytes | Unit:0.01
4825 | Slave07 Outlet Port36 PF | RO | 2 bytes | Unit:0.01
4826 | Slave07 Outlet Port37 PF | RO | 2 bytes | Unit:0.01
4827 | Slave07 Outlet Port38 PF | RO | 2 bytes | Unit:0.01
4828 | Slave07 Outlet Port39 PF | RO | 2 bytes | Unit:0.01
4829 | Slave07 Outlet Port40 PF | RO | 2 bytes | Unit:0.01
4830 | Slave07 Outlet Port41 PF | RO | 2 bytes | Unit:0.01
4831 | Slave07 Outlet Port42 PF | RO | 2 bytes | Unit:0.01
4832 | Slave08 Outlet Port01 PF | RO | 2 bytes | Unit:0.01
4833 | Slave08 Outlet Port02 PF | RO | 2 bytes | Unit:0.01
4834 | Slave08 Outlet Port03 PF | RO | 2 bytes | Unit:0.01
4835 | Slave08 Outlet Port04 PF | RO | 2 bytes | Unit:0.01
4836 | Slave08 Outlet Port05 PF | RO | 2 bytes | Unit:0.01
4837 | Slave08 Outlet Port06 PF | RO | 2 bytes | Unit:0.01
4838 | Slave08 Outlet Port07 PF | RO | 2 bytes | Unit:0.01
4839 | Slave08 Outlet Port08 PF | RO | 2 bytes | Unit:0.01
4840 | Slave08 Outlet Port09 PF | RO | 2 bytes | Unit:0.01
4841 | Slave08 Outlet Port10 PF | RO | 2 bytes | Unit:0.01
4842 | Slave08 Outlet Port11 PF | RO | 2 bytes | Unit:0.01
4843 | Slave08 Outlet Port12 PF | RO | 2 bytes | Unit:0.01
4844 | Slave08 Outlet Port13 PF | RO | 2 bytes | Unit:0.01
4845 | Slave08 Outlet Port14 PF | RO | 2 bytes | Unit:0.01
4846 | Slave08 Outlet Port15 PF | RO | 2 bytes | Unit:0.01
4847 | Slave08 Outlet Port16 PF | RO | 2 bytes | Unit:0.01
4848 | Slave08 Outlet Port17 PF | RO | 2 bytes | Unit:0.01
4849 | Slave08 Outlet Port18 PF | RO | 2 bytes | Unit:0.01
4850 | Slave08 Outlet Port19 PF | RO | 2 bytes | Unit:0.01
4851 | Slave08 Outlet Port20 PF | RO | 2 bytes | Unit:0.01
4852 | Slave08 Outlet Port21 PF | RO | 2 bytes | Unit:0.01
4853 | Slave08 Outlet Port22 PF | RO | 2 bytes | Unit:0.01
4854 | Slave08 Outlet Port23 PF | RO | 2 bytes | Unit:0.01
4855 | Slave08 Outlet Port24 PF | RO | 2 bytes | Unit:0.01
4856 | Slave08 Outlet Port25 PF | RO | 2 bytes | Unit:0.01
4857 | Slave08 Outlet Port26 PF | RO | 2 bytes | Unit:0.01
4858 | Slave08 Outlet Port27 PF | RO | 2 bytes | Unit:0.01
4859 | Slave08 Outlet Port28 PF | RO | 2 bytes | Unit:0.01
4860 | Slave08 Outlet Port29 PF | RO | 2 bytes | Unit:0.01
4861 | Slave08 Outlet Port30 PF | RO | 2 bytes | Unit:0.01
4862 | Slave08 Outlet Port31 PF | RO | 2 bytes | Unit:0.01
4863 | Slave08 Outlet Port32 PF | RO | 2 bytes | Unit:0.01
4864 | Slave08 Outlet Port33 PF | RO | 2 bytes | Unit:0.01
4865 | Slave08 Outlet Port34 PF | RO | 2 bytes | Unit:0.01
4866 | Slave08 Outlet Port35 PF | RO | 2 bytes | Unit:0.01
4867 | Slave08 Outlet Port36 PF | RO | 2 bytes | Unit:0.01
4868 | Slave08 Outlet Port37 PF | RO | 2 bytes | Unit:0.01
4869 | Slave08 Outlet Port38 PF | RO | 2 bytes | Unit:0.01
4870 | Slave08 Outlet Port39 PF | RO | 2 bytes | Unit:0.01
4871 | Slave08 Outlet Port40 PF | RO | 2 bytes | Unit:0.01
4872 | Slave08 Outlet Port41 PF | RO | 2 bytes | Unit:0.01
4873 | Slave08 Outlet Port42 PF | RO | 2 bytes | Unit:0.01
4874 | Slave09 Outlet Port01 PF | RO | 2 bytes | Unit:0.01
4875 | Slave09 Outlet Port02 PF | RO | 2 bytes | Unit:0.01
4876 | Slave09 Outlet Port03 PF | RO | 2 bytes | Unit:0.01
4877 | Slave09 Outlet Port04 PF | RO | 2 bytes | Unit:0.01
4878 | Slave09 Outlet Port05 PF | RO | 2 bytes | Unit:0.01
4879 | Slave09 Outlet Port06 PF | RO | 2 bytes | Unit:0.01
4880 | Slave09 Outlet Port07 PF | RO | 2 bytes | Unit:0.01
4881 | Slave09 Outlet Port08 PF | RO | 2 bytes | Unit:0.01
4882 | Slave09 Outlet Port09 PF | RO | 2 bytes | Unit:0.01
4883 | Slave09 Outlet Port10 PF | RO | 2 bytes | Unit:0.01
4884 | Slave09 Outlet Port11 PF | RO | 2 bytes | Unit:0.01
4885 | Slave09 Outlet Port12 PF | RO | 2 bytes | Unit:0.01
4886 | Slave09 Outlet Port13 PF | RO | 2 bytes | Unit:0.01
4887 | Slave09 Outlet Port14 PF | RO | 2 bytes | Unit:0.01
4888 | Slave09 Outlet Port15 PF | RO | 2 bytes | Unit:0.01
4889 | Slave09 Outlet Port16 PF | RO | 2 bytes | Unit:0.01
4890 | Slave09 Outlet Port17 PF | RO | 2 bytes | Unit:0.01
4891 | Slave09 Outlet Port18 PF | RO | 2 bytes | Unit:0.01
4892 | Slave09 Outlet Port19 PF | RO | 2 bytes | Unit:0.01
4893 | Slave09 Outlet Port20 PF | RO | 2 bytes | Unit:0.01
4894 | Slave09 Outlet Port21 PF | RO | 2 bytes | Unit:0.01
4895 | Slave09 Outlet Port22 PF | RO | 2 bytes | Unit:0.01
4896 | Slave09 Outlet Port23 PF | RO | 2 bytes | Unit:0.01
4897 | Slave09 Outlet Port24 PF | RO | 2 bytes | Unit:0.01
4898 | Slave09 Outlet Port25 PF | RO | 2 bytes | Unit:0.01
4899 | Slave09 Outlet Port26 PF | RO | 2 bytes | Unit:0.01
4900 | Slave09 Outlet Port27 PF | RO | 2 bytes | Unit:0.01
4901 | Slave09 Outlet Port28 PF | RO | 2 bytes | Unit:0.01
4902 | Slave09 Outlet Port29 PF | RO | 2 bytes | Unit:0.01
4903 | Slave09 Outlet Port30 PF | RO | 2 bytes | Unit:0.01
4904 | Slave09 Outlet Port31 PF | RO | 2 bytes | Unit:0.01
4905 | Slave09 Outlet Port32 PF | RO | 2 bytes | Unit:0.01
4906 | Slave09 Outlet Port33 PF | RO | 2 bytes | Unit:0.01
4907 | Slave09 Outlet Port34 PF | RO | 2 bytes | Unit:0.01
4908 | Slave09 Outlet Port35 PF | RO | 2 bytes | Unit:0.01
4909 | Slave09 Outlet Port36 PF | RO | 2 bytes | Unit:0.01
4910 | Slave09 Outlet Port37 PF | RO | 2 bytes | Unit:0.01
4911 | Slave09 Outlet Port38 PF | RO | 2 bytes | Unit:0.01
4912 | Slave09 Outlet Port39 PF | RO | 2 bytes | Unit:0.01
4913 | Slave09 Outlet Port40 PF | RO | 2 bytes | Unit:0.01
4914 | Slave09 Outlet Port41 PF | RO | 2 bytes | Unit:0.01
4915 | Slave09 Outlet Port42 PF | RO | 2 bytes | Unit:0.01
4916 | Slave10 Outlet Port01 PF | RO | 2 bytes | Unit:0.01
4917 | Slave10 Outlet Port02 PF | RO | 2 bytes | Unit:0.01
4918 | Slave10 Outlet Port03 PF | RO | 2 bytes | Unit:0.01
4919 | Slave10 Outlet Port04 PF | RO | 2 bytes | Unit:0.01
4920 | Slave10 Outlet Port05 PF | RO | 2 bytes | Unit:0.01
4921 | Slave10 Outlet Port06 PF | RO | 2 bytes | Unit:0.01
4922 | Slave10 Outlet Port07 PF | RO | 2 bytes | Unit:0.01
4923 | Slave10 Outlet Port08 PF | RO | 2 bytes | Unit:0.01
4924 | Slave10 Outlet Port09 PF | RO | 2 bytes | Unit:0.01
4925 | Slave10 Outlet Port10 PF | RO | 2 bytes | Unit:0.01
4926 | Slave10 Outlet Port11 PF | RO | 2 bytes | Unit:0.01
4927 | Slave10 Outlet Port12 PF | RO | 2 bytes | Unit:0.01
4928 | Slave10 Outlet Port13 PF | RO | 2 bytes | Unit:0.01
4929 | Slave10 Outlet Port14 PF | RO | 2 bytes | Unit:0.01
4930 | Slave10 Outlet Port15 PF | RO | 2 bytes | Unit:0.01
4931 | Slave10 Outlet Port16 PF | RO | 2 bytes | Unit:0.01
4932 | Slave10 Outlet Port17 PF | RO | 2 bytes | Unit:0.01
4933 | Slave10 Outlet Port18 PF | RO | 2 bytes | Unit:0.01
4934 | Slave10 Outlet Port19 PF | RO | 2 bytes | Unit:0.01
4935 | Slave10 Outlet Port20 PF | RO | 2 bytes | Unit:0.01
4936 | Slave10 Outlet Port21 PF | RO | 2 bytes | Unit:0.01
4937 | Slave10 Outlet Port22 PF | RO | 2 bytes | Unit:0.01
4938 | Slave10 Outlet Port23 PF | RO | 2 bytes | Unit:0.01
4939 | Slave10 Outlet Port24 PF | RO | 2 bytes | Unit:0.01
4940 | Slave10 Outlet Port25 PF | RO | 2 bytes | Unit:0.01
4941 | Slave10 Outlet Port26 PF | RO | 2 bytes | Unit:0.01
4942 | Slave10 Outlet Port27 PF | RO | 2 bytes | Unit:0.01
4943 | Slave10 Outlet Port28 PF | RO | 2 bytes | Unit:0.01
4944 | Slave10 Outlet Port29 PF | RO | 2 bytes | Unit:0.01
4945 | Slave10 Outlet Port30 PF | RO | 2 bytes | Unit:0.01
4946 | Slave10 Outlet Port31 PF | RO | 2 bytes | Unit:0.01
4947 | Slave10 Outlet Port32 PF | RO | 2 bytes | Unit:0.01
4948 | Slave10 Outlet Port33 PF | RO | 2 bytes | Unit:0.01
4949 | Slave10 Outlet Port34 PF | RO | 2 bytes | Unit:0.01
4950 | Slave10 Outlet Port35 PF | RO | 2 bytes | Unit:0.01
4951 | Slave10 Outlet Port36 PF | RO | 2 bytes | Unit:0.01
4952 | Slave10 Outlet Port37 PF | RO | 2 bytes | Unit:0.01
4953 | Slave10 Outlet Port38 PF | RO | 2 bytes | Unit:0.01
4954 | Slave10 Outlet Port39 PF | RO | 2 bytes | Unit:0.01
4955 | Slave10 Outlet Port40 PF | RO | 2 bytes | Unit:0.01
4956 | Slave10 Outlet Port41 PF | RO | 2 bytes | Unit:0.01
4957 | Slave10 Outlet Port42 PF | RO | 2 bytes | Unit:0.01
4958 | Slave11 Outlet Port01 PF | RO | 2 bytes | Unit:0.01
4959 | Slave11 Outlet Port02 PF | RO | 2 bytes | Unit:0.01
4960 | Slave11 Outlet Port03 PF | RO | 2 bytes | Unit:0.01
4961 | Slave11 Outlet Port04 PF | RO | 2 bytes | Unit:0.01
4962 | Slave11 Outlet Port05 PF | RO | 2 bytes | Unit:0.01
4963 | Slave11 Outlet Port06 PF | RO | 2 bytes | Unit:0.01
4964 | Slave11 Outlet Port07 PF | RO | 2 bytes | Unit:0.01
4965 | Slave11 Outlet Port08 PF | RO | 2 bytes | Unit:0.01
4966 | Slave11 Outlet Port09 PF | RO | 2 bytes | Unit:0.01
4967 | Slave11 Outlet Port10 PF | RO | 2 bytes | Unit:0.01
4968 | Slave11 Outlet Port11 PF | RO | 2 bytes | Unit:0.01
4969 | Slave11 Outlet Port12 PF | RO | 2 bytes | Unit:0.01
4970 | Slave11 Outlet Port13 PF | RO | 2 bytes | Unit:0.01
4971 | Slave11 Outlet Port14 PF | RO | 2 bytes | Unit:0.01
4972 | Slave11 Outlet Port15 PF | RO | 2 bytes | Unit:0.01
4973 | Slave11 Outlet Port16 PF | RO | 2 bytes | Unit:0.01
4974 | Slave11 Outlet Port17 PF | RO | 2 bytes | Unit:0.01
4975 | Slave11 Outlet Port18 PF | RO | 2 bytes | Unit:0.01
4976 | Slave11 Outlet Port19 PF | RO | 2 bytes | Unit:0.01
4977 | Slave11 Outlet Port20 PF | RO | 2 bytes | Unit:0.01
4978 | Slave11 Outlet Port21 PF | RO | 2 bytes | Unit:0.01
4979 | Slave11 Outlet Port22 PF | RO | 2 bytes | Unit:0.01
4980 | Slave11 Outlet Port23 PF | RO | 2 bytes | Unit:0.01
4981 | Slave11 Outlet Port24 PF | RO | 2 bytes | Unit:0.01
4982 | Slave11 Outlet Port25 PF | RO | 2 bytes | Unit:0.01
4983 | Slave11 Outlet Port26 PF | RO | 2 bytes | Unit:0.01
4984 | Slave11 Outlet Port27 PF | RO | 2 bytes | Unit:0.01
4985 | Slave11 Outlet Port28 PF | RO | 2 bytes | Unit:0.01
4986 | Slave11 Outlet Port29 PF | RO | 2 bytes | Unit:0.01
4987 | Slave11 Outlet Port30 PF | RO | 2 bytes | Unit:0.01
4988 | Slave11 Outlet Port31 PF | RO | 2 bytes | Unit:0.01
4989 | Slave11 Outlet Port32 PF | RO | 2 bytes | Unit:0.01
4990 | Slave11 Outlet Port33 PF | RO | 2 bytes | Unit:0.01
4991 | Slave11 Outlet Port34 PF | RO | 2 bytes | Unit:0.01
4992 | Slave11 Outlet Port35 PF | RO | 2 bytes | Unit:0.01
4993 | Slave11 Outlet Port36 PF | RO | 2 bytes | Unit:0.01
4994 | Slave11 Outlet Port37 PF | RO | 2 bytes | Unit:0.01
4995 | Slave11 Outlet Port38 PF | RO | 2 bytes | Unit:0.01
4996 | Slave11 Outlet Port39 PF | RO | 2 bytes | Unit:0.01
4997 | Slave11 Outlet Port40 PF | RO | 2 bytes | Unit:0.01
4998 | Slave11 Outlet Port41 PF | RO | 2 bytes | Unit:0.01
4999 | Slave11 Outlet Port42 PF | RO | 2 bytes | Unit:0.01
5000 | Slave12 Outlet Port01 PF | RO | 2 bytes | Unit:0.01
5001 | Slave12 Outlet Port02 PF | RO | 2 bytes | Unit:0.01
5002 | Slave12 Outlet Port03 PF | RO | 2 bytes | Unit:0.01
5003 | Slave12 Outlet Port04 PF | RO | 2 bytes | Unit:0.01
5004 | Slave12 Outlet Port05 PF | RO | 2 bytes | Unit:0.01
5005 | Slave12 Outlet Port06 PF | RO | 2 bytes | Unit:0.01
5006 | Slave12 Outlet Port07 PF | RO | 2 bytes | Unit:0.01
5007 | Slave12 Outlet Port08 PF | RO | 2 bytes | Unit:0.01
5008 | Slave12 Outlet Port09 PF | RO | 2 bytes | Unit:0.01
5009 | Slave12 Outlet Port10 PF | RO | 2 bytes | Unit:0.01
5010 | Slave12 Outlet Port11 PF | RO | 2 bytes | Unit:0.01
5011 | Slave12 Outlet Port12 PF | RO | 2 bytes | Unit:0.01
5012 | Slave12 Outlet Port13 PF | RO | 2 bytes | Unit:0.01
5013 | Slave12 Outlet Port14 PF | RO | 2 bytes | Unit:0.01
5014 | Slave12 Outlet Port15 PF | RO | 2 bytes | Unit:0.01
5015 | Slave12 Outlet Port16 PF | RO | 2 bytes | Unit:0.01
5016 | Slave12 Outlet Port17 PF | RO | 2 bytes | Unit:0.01
5017 | Slave12 Outlet Port18 PF | RO | 2 bytes | Unit:0.01
5018 | Slave12 Outlet Port19 PF | RO | 2 bytes | Unit:0.01
5019 | Slave12 Outlet Port20 PF | RO | 2 bytes | Unit:0.01
5020 | Slave12 Outlet Port21 PF | RO | 2 bytes | Unit:0.01
5021 | Slave12 Outlet Port22 PF | RO | 2 bytes | Unit:0.01
5022 | Slave12 Outlet Port23 PF | RO | 2 bytes | Unit:0.01
5023 | Slave12 Outlet Port24 PF | RO | 2 bytes | Unit:0.01
5024 | Slave12 Outlet Port25 PF | RO | 2 bytes | Unit:0.01
5025 | Slave12 Outlet Port26 PF | RO | 2 bytes | Unit:0.01
5026 | Slave12 Outlet Port27 PF | RO | 2 bytes | Unit:0.01
5027 | Slave12 Outlet Port28 PF | RO | 2 bytes | Unit:0.01
5028 | Slave12 Outlet Port29 PF | RO | 2 bytes | Unit:0.01
5029 | Slave12 Outlet Port30 PF | RO | 2 bytes | Unit:0.01
5030 | Slave12 Outlet Port31 PF | RO | 2 bytes | Unit:0.01
5031 | Slave12 Outlet Port32 PF | RO | 2 bytes | Unit:0.01
5032 | Slave12 Outlet Port33 PF | RO | 2 bytes | Unit:0.01
5033 | Slave12 Outlet Port34 PF | RO | 2 bytes | Unit:0.01
5034 | Slave12 Outlet Port35 PF | RO | 2 bytes | Unit:0.01
5035 | Slave12 Outlet Port36 PF | RO | 2 bytes | Unit:0.01
5036 | Slave12 Outlet Port37 PF | RO | 2 bytes | Unit:0.01
5037 | Slave12 Outlet Port38 PF | RO | 2 bytes | Unit:0.01
5038 | Slave12 Outlet Port39 PF | RO | 2 bytes | Unit:0.01
5039 | Slave12 Outlet Port40 PF | RO | 2 bytes | Unit:0.01
5040 | Slave12 Outlet Port41 PF | RO | 2 bytes | Unit:0.01
5041 | Slave12 Outlet Port42 PF | RO | 2 bytes | Unit:0.01
5042 | Slave13 Outlet Port01 PF | RO | 2 bytes | Unit:0.01
5043 | Slave13 Outlet Port02 PF | RO | 2 bytes | Unit:0.01
5044 | Slave13 Outlet Port03 PF | RO | 2 bytes | Unit:0.01
5045 | Slave13 Outlet Port04 PF | RO | 2 bytes | Unit:0.01
5046 | Slave13 Outlet Port05 PF | RO | 2 bytes | Unit:0.01
5047 | Slave13 Outlet Port06 PF | RO | 2 bytes | Unit:0.01
5048 | Slave13 Outlet Port07 PF | RO | 2 bytes | Unit:0.01
5049 | Slave13 Outlet Port08 PF | RO | 2 bytes | Unit:0.01
5050 | Slave13 Outlet Port09 PF | RO | 2 bytes | Unit:0.01
5051 | Slave13 Outlet Port10 PF | RO | 2 bytes | Unit:0.01
5052 | Slave13 Outlet Port11 PF | RO | 2 bytes | Unit:0.01
5053 | Slave13 Outlet Port12 PF | RO | 2 bytes | Unit:0.01
5054 | Slave13 Outlet Port13 PF | RO | 2 bytes | Unit:0.01
5055 | Slave13 Outlet Port14 PF | RO | 2 bytes | Unit:0.01
5056 | Slave13 Outlet Port15 PF | RO | 2 bytes | Unit:0.01
5057 | Slave13 Outlet Port16 PF | RO | 2 bytes | Unit:0.01
5058 | Slave13 Outlet Port17 PF | RO | 2 bytes | Unit:0.01
5059 | Slave13 Outlet Port18 PF | RO | 2 bytes | Unit:0.01
5060 | Slave13 Outlet Port19 PF | RO | 2 bytes | Unit:0.01
5061 | Slave13 Outlet Port20 PF | RO | 2 bytes | Unit:0.01
5062 | Slave13 Outlet Port21 PF | RO | 2 bytes | Unit:0.01
5063 | Slave13 Outlet Port22 PF | RO | 2 bytes | Unit:0.01
5064 | Slave13 Outlet Port23 PF | RO | 2 bytes | Unit:0.01
5065 | Slave13 Outlet Port24 PF | RO | 2 bytes | Unit:0.01
5066 | Slave13 Outlet Port25 PF | RO | 2 bytes | Unit:0.01
5067 | Slave13 Outlet Port26 PF | RO | 2 bytes | Unit:0.01
5068 | Slave13 Outlet Port27 PF | RO | 2 bytes | Unit:0.01
5069 | Slave13 Outlet Port28 PF | RO | 2 bytes | Unit:0.01
5070 | Slave13 Outlet Port29 PF | RO | 2 bytes | Unit:0.01
5071 | Slave13 Outlet Port30 PF | RO | 2 bytes | Unit:0.01
5072 | Slave13 Outlet Port31 PF | RO | 2 bytes | Unit:0.01
5073 | Slave13 Outlet Port32 PF | RO | 2 bytes | Unit:0.01
5074 | Slave13 Outlet Port33 PF | RO | 2 bytes | Unit:0.01
5075 | Slave13 Outlet Port34 PF | RO | 2 bytes | Unit:0.01
5076 | Slave13 Outlet Port35 PF | RO | 2 bytes | Unit:0.01
5077 | Slave13 Outlet Port36 PF | RO | 2 bytes | Unit:0.01
5078 | Slave13 Outlet Port37 PF | RO | 2 bytes | Unit:0.01
5079 | Slave13 Outlet Port38 PF | RO | 2 bytes | Unit:0.01
5080 | Slave13 Outlet Port39 PF | RO | 2 bytes | Unit:0.01
5081 | Slave13 Outlet Port40 PF | RO | 2 bytes | Unit:0.01
5082 | Slave13 Outlet Port41 PF | RO | 2 bytes | Unit:0.01
5083 | Slave13 Outlet Port42 PF | RO | 2 bytes | Unit:0.01
5084 | Slave14 Outlet Port01 PF | RO | 2 bytes | Unit:0.01
5085 | Slave14 Outlet Port02 PF | RO | 2 bytes | Unit:0.01
5086 | Slave14 Outlet Port03 PF | RO | 2 bytes | Unit:0.01
5087 | Slave14 Outlet Port04 PF | RO | 2 bytes | Unit:0.01
5088 | Slave14 Outlet Port05 PF | RO | 2 bytes | Unit:0.01
5089 | Slave14 Outlet Port06 PF | RO | 2 bytes | Unit:0.01
5090 | Slave14 Outlet Port07 PF | RO | 2 bytes | Unit:0.01
5091 | Slave14 Outlet Port08 PF | RO | 2 bytes | Unit:0.01
5092 | Slave14 Outlet Port09 PF | RO | 2 bytes | Unit:0.01
5093 | Slave14 Outlet Port10 PF | RO | 2 bytes | Unit:0.01
5094 | Slave14 Outlet Port11 PF | RO | 2 bytes | Unit:0.01
5095 | Slave14 Outlet Port12 PF | RO | 2 bytes | Unit:0.01
5096 | Slave14 Outlet Port13 PF | RO | 2 bytes | Unit:0.01
5097 | Slave14 Outlet Port14 PF | RO | 2 bytes | Unit:0.01
5098 | Slave14 Outlet Port15 PF | RO | 2 bytes | Unit:0.01
5099 | Slave14 Outlet Port16 PF | RO | 2 bytes | Unit:0.01
5100 | Slave14 Outlet Port17 PF | RO | 2 bytes | Unit:0.01
5101 | Slave14 Outlet Port18 PF | RO | 2 bytes | Unit:0.01
5102 | Slave14 Outlet Port19 PF | RO | 2 bytes | Unit:0.01
5103 | Slave14 Outlet Port20 PF | RO | 2 bytes | Unit:0.01
5104 | Slave14 Outlet Port21 PF | RO | 2 bytes | Unit:0.01
5105 | Slave14 Outlet Port22 PF | RO | 2 bytes | Unit:0.01
5106 | Slave14 Outlet Port23 PF | RO | 2 bytes | Unit:0.01
5107 | Slave14 Outlet Port24 PF | RO | 2 bytes | Unit:0.01
5108 | Slave14 Outlet Port25 PF | RO | 2 bytes | Unit:0.01
5109 | Slave14 Outlet Port26 PF | RO | 2 bytes | Unit:0.01
5110 | Slave14 Outlet Port27 PF | RO | 2 bytes | Unit:0.01
5111 | Slave14 Outlet Port28 PF | RO | 2 bytes | Unit:0.01
5112 | Slave14 Outlet Port29 PF | RO | 2 bytes | Unit:0.01
5113 | Slave14 Outlet Port30 PF | RO | 2 bytes | Unit:0.01
5114 | Slave14 Outlet Port31 PF | RO | 2 bytes | Unit:0.01
5115 | Slave14 Outlet Port32 PF | RO | 2 bytes | Unit:0.01
5116 | Slave14 Outlet Port33 PF | RO | 2 bytes | Unit:0.01
5117 | Slave14 Outlet Port34 PF | RO | 2 bytes | Unit:0.01
5118 | Slave14 Outlet Port35 PF | RO | 2 bytes | Unit:0.01
5119 | Slave14 Outlet Port36 PF | RO | 2 bytes | Unit:0.01
5120 | Slave14 Outlet Port37 PF | RO | 2 bytes | Unit:0.01
5121 | Slave14 Outlet Port38 PF | RO | 2 bytes | Unit:0.01
5122 | Slave14 Outlet Port39 PF | RO | 2 bytes | Unit:0.01
5123 | Slave14 Outlet Port40 PF | RO | 2 bytes | Unit:0.01
5124 | Slave14 Outlet Port41 PF | RO | 2 bytes | Unit:0.01
5125 | Slave14 Outlet Port42 PF | RO | 2 bytes | Unit:0.01
5126 | Slave15 Outlet Port01 PF | RO | 2 bytes | Unit:0.01
5127 | Slave15 Outlet Port02 PF | RO | 2 bytes | Unit:0.01
5128 | Slave15 Outlet Port03 PF | RO | 2 bytes | Unit:0.01
5129 | Slave15 Outlet Port04 PF | RO | 2 bytes | Unit:0.01
5130 | Slave15 Outlet Port05 PF | RO | 2 bytes | Unit:0.01
5131 | Slave15 Outlet Port06 PF | RO | 2 bytes | Unit:0.01
5132 | Slave15 Outlet Port07 PF | RO | 2 bytes | Unit:0.01
5133 | Slave15 Outlet Port08 PF | RO | 2 bytes | Unit:0.01
5134 | Slave15 Outlet Port09 PF | RO | 2 bytes | Unit:0.01
5135 | Slave15 Outlet Port10 PF | RO | 2 bytes | Unit:0.01
5136 | Slave15 Outlet Port11 PF | RO | 2 bytes | Unit:0.01
5137 | Slave15 Outlet Port12 PF | RO | 2 bytes | Unit:0.01
5138 | Slave15 Outlet Port13 PF | RO | 2 bytes | Unit:0.01
5139 | Slave15 Outlet Port14 PF | RO | 2 bytes | Unit:0.01
5140 | Slave15 Outlet Port15 PF | RO | 2 bytes | Unit:0.01
5141 | Slave15 Outlet Port16 PF | RO | 2 bytes | Unit:0.01
5142 | Slave15 Outlet Port17 PF | RO | 2 bytes | Unit:0.01
5143 | Slave15 Outlet Port18 PF | RO | 2 bytes | Unit:0.01
5144 | Slave15 Outlet Port19 PF | RO | 2 bytes | Unit:0.01
5145 | Slave15 Outlet Port20 PF | RO | 2 bytes | Unit:0.01
5146 | Slave15 Outlet Port21 PF | RO | 2 bytes | Unit:0.01
5147 | Slave15 Outlet Port22 PF | RO | 2 bytes | Unit:0.01
5148 | Slave15 Outlet Port23 PF | RO | 2 bytes | Unit:0.01
5149 | Slave15 Outlet Port24 PF | RO | 2 bytes | Unit:0.01
5150 | Slave15 Outlet Port25 PF | RO | 2 bytes | Unit:0.01
5151 | Slave15 Outlet Port26 PF | RO | 2 bytes | Unit:0.01
5152 | Slave15 Outlet Port27 PF | RO | 2 bytes | Unit:0.01
5153 | Slave15 Outlet Port28 PF | RO | 2 bytes | Unit:0.01
5154 | Slave15 Outlet Port29 PF | RO | 2 bytes | Unit:0.01
5155 | Slave15 Outlet Port30 PF | RO | 2 bytes | Unit:0.01
5156 | Slave15 Outlet Port31 PF | RO | 2 bytes | Unit:0.01
5157 | Slave15 Outlet Port32 PF | RO | 2 bytes | Unit:0.01
5158 | Slave15 Outlet Port33 PF | RO | 2 bytes | Unit:0.01
5159 | Slave15 Outlet Port34 PF | RO | 2 bytes | Unit:0.01
5160 | Slave15 Outlet Port35 PF | RO | 2 bytes | Unit:0.01
5161 | Slave15 Outlet Port36 PF | RO | 2 bytes | Unit:0.01
5162 | Slave15 Outlet Port37 PF | RO | 2 bytes | Unit:0.01
5163 | Slave15 Outlet Port38 PF | RO | 2 bytes | Unit:0.01
5164 | Slave15 Outlet Port39 PF | RO | 2 bytes | Unit:0.01
5165 | Slave15 Outlet Port40 PF | RO | 2 bytes | Unit:0.01
5166 | Slave15 Outlet Port41 PF | RO | 2 bytes | Unit:0.01
5167 | Slave15 Outlet Port42 PF | RO | 2 bytes | Unit:0.01
5168 | Master EMD-1 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5169 | Master EMD-2 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5170 | Master EMD-3 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5171 | Master EMD-4 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5172 | Master EMD-5 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5173 | Master EMD-6 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5174 | Master EMD-7 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5175 | Master EMD-8 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5176 | Slave01 EMD-1 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5177 | Slave01 EMD-2 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5178 | Slave01 EMD-3 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5179 | Slave01 EMD-4 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5180 | Slave01 EMD-5 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5181 | Slave01 EMD-6 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5182 | Slave01 EMD-7 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5183 | Slave01 EMD-8 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5184 | Slave02 EMD-1 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5185 | Slave02 EMD-2 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5186 | Slave02 EMD-3 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5187 | Slave02 EMD-4 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5188 | Slave02 EMD-5 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5189 | Slave02 EMD-6 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5190 | Slave02 EMD-7 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5191 | Slave02 EMD-8 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5192 | Slave03 EMD-1 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5193 | Slave03 EMD-2 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5194 | Slave03 EMD-3 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5195 | Slave03 EMD-4 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5196 | Slave03 EMD-5 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5197 | Slave03 EMD-6 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5198 | Slave03 EMD-7 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5199 | Slave03 EMD-8 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5200 | Slave04 EMD-1 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5201 | Slave04 EMD-2 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5202 | Slave04 EMD-3 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5203 | Slave04 EMD-4 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5204 | Slave04 EMD-5 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5205 | Slave04 EMD-6 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5206 | Slave04 EMD-7 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5207 | Slave04 EMD-8 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5208 | Slave05 EMD-1 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5209 | Slave05 EMD-2 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5210 | Slave05 EMD-3 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5211 | Slave05 EMD-4 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5212 | Slave05 EMD-5 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5213 | Slave05 EMD-6 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5214 | Slave05 EMD-7 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5215 | Slave05 EMD-8 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5216 | Slave06 EMD-1 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5217 | Slave06 EMD-2 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5218 | Slave06 EMD-3 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5219 | Slave06 EMD-4 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5220 | Slave06 EMD-5 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5221 | Slave06 EMD-6 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5222 | Slave06 EMD-7 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5223 | Slave06 EMD-8 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5224 | Slave07 EMD-1 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5225 | Slave07 EMD-2 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5226 | Slave07 EMD-3 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5227 | Slave07 EMD-4 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5228 | Slave07 EMD-5 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5229 | Slave07 EMD-6 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5230 | Slave07 EMD-7 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5231 | Slave07 EMD-8 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5232 | Slave08 EMD-1 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5233 | Slave08 EMD-2 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5234 | Slave08 EMD-3 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5235 | Slave08 EMD-4 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5236 | Slave08 EMD-5 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5237 | Slave08 EMD-6 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5238 | Slave08 EMD-7 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5239 | Slave08 EMD-8 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5240 | Slave09 EMD-1 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5241 | Slave09 EMD-2 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5242 | Slave09 EMD-3 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5243 | Slave09 EMD-4 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5244 | Slave09 EMD-5 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5245 | Slave09 EMD-6 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5246 | Slave09 EMD-7 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5247 | Slave09 EMD-8 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5248 | Slave10 EMD-1 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5249 | Slave10 EMD-2 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5250 | Slave10 EMD-3 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5251 | Slave10 EMD-4 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5252 | Slave10 EMD-5 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5253 | Slave10 EMD-6 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5254 | Slave10 EMD-7 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5255 | Slave10 EMD-8 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5256 | Slave11 EMD-1 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5257 | Slave11 EMD-2 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5258 | Slave11 EMD-3 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5259 | Slave11 EMD-4 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5260 | Slave11 EMD-5 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5261 | Slave11 EMD-6 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5262 | Slave11 EMD-7 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5263 | Slave11 EMD-8 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5264 | Slave12 EMD-1 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5265 | Slave12 EMD-2 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5266 | Slave12 EMD-3 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5267 | Slave12 EMD-4 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5268 | Slave12 EMD-5 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5269 | Slave12 EMD-6 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5270 | Slave12 EMD-7 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5271 | Slave12 EMD-8 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5272 | Slave13 EMD-1 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5273 | Slave13 EMD-2 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5274 | Slave13 EMD-3 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5275 | Slave13 EMD-4 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5276 | Slave13 EMD-5 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5277 | Slave13 EMD-6 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5278 | Slave13 EMD-7 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5279 | Slave13 EMD-8 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5280 | Slave14 EMD-1 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5281 | Slave14 EMD-2 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5282 | Slave14 EMD-3 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5283 | Slave14 EMD-4 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5284 | Slave14 EMD-5 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5285 | Slave14 EMD-6 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5286 | Slave14 EMD-7 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5287 | Slave14 EMD-8 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5288 | Slave15 EMD-1 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5289 | Slave15 EMD-2 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5290 | Slave15 EMD-3 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5291 | Slave15 EMD-4 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5292 | Slave15 EMD-5 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5293 | Slave15 EMD-6 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5294 | Slave15 EMD-7 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5295 | Slave15 EMD-8 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5296 | Master EMD-1 Temperature | RO | 2 bytes | Unit0.1C
5297 | Master EMD-2 Temperature | RO | 2 bytes | Unit0.1C
5298 | Master EMD-3 Temperature | RO | 2 bytes | Unit0.1C
5299 | Master EMD-4 Temperature | RO | 2 bytes | Unit0.1C
5300 | Master EMD-5 Temperature | RO | 2 bytes | Unit0.1C
5301 | Master EMD-6 Temperature | RO | 2 bytes | Unit0.1C
5302 | Master EMD-7 Temperature | RO | 2 bytes | Unit0.1C
5303 | Master EMD-8 Temperature | RO | 2 bytes | Unit0.1C
5304 | Slave01 EMD-1 Temperature | RO | 2 bytes | Unit0.1C
5305 | Slave01 EMD-2 Temperature | RO | 2 bytes | Unit0.1C
5306 | Slave01 EMD-3 Temperature | RO | 2 bytes | Unit0.1C
5307 | Slave01 EMD-4 Temperature | RO | 2 bytes | Unit0.1C
5308 | Slave01 EMD-5 Temperature | RO | 2 bytes | Unit0.1C
5309 | Slave01 EMD-6 Temperature | RO | 2 bytes | Unit0.1C
5310 | Slave01 EMD-7 Temperature | RO | 2 bytes | Unit0.1C
5311 | Slave01 EMD-8 Temperature | RO | 2 bytes | Unit0.1C
5312 | Slave02 EMD-1 Temperature | RO | 2 bytes | Unit0.1C
5313 | Slave02 EMD-2 Temperature | RO | 2 bytes | Unit0.1C
5314 | Slave02 EMD-3 Temperature | RO | 2 bytes | Unit0.1C
5315 | Slave02 EMD-4 Temperature | RO | 2 bytes | Unit0.1C
5316 | Slave02 EMD-5 Temperature | RO | 2 bytes | Unit0.1C
5317 | Slave02 EMD-6 Temperature | RO | 2 bytes | Unit0.1C
5318 | Slave02 EMD-7 Temperature | RO | 2 bytes | Unit0.1C
5319 | Slave02 EMD-8 Temperature | RO | 2 bytes | Unit0.1C
5320 | Slave03 EMD-1 Temperature | RO | 2 bytes | Unit0.1C
5321 | Slave03 EMD-2 Temperature | RO | 2 bytes | Unit0.1C
5322 | Slave03 EMD-3 Temperature | RO | 2 bytes | Unit0.1C
5323 | Slave03 EMD-4 Temperature | RO | 2 bytes | Unit0.1C
5324 | Slave03 EMD-5 Temperature | RO | 2 bytes | Unit0.1C
5325 | Slave03 EMD-6 Temperature | RO | 2 bytes | Unit0.1C
5326 | Slave03 EMD-7 Temperature | RO | 2 bytes | Unit0.1C
5327 | Slave03 EMD-8 Temperature | RO | 2 bytes | Unit0.1C
5328 | Slave04 EMD-1 Temperature | RO | 2 bytes | Unit0.1C
5329 | Slave04 EMD-2 Temperature | RO | 2 bytes | Unit0.1C
5330 | Slave04 EMD-3 Temperature | RO | 2 bytes | Unit0.1C
5331 | Slave04 EMD-4 Temperature | RO | 2 bytes | Unit0.1C
5332 | Slave04 EMD-5 Temperature | RO | 2 bytes | Unit0.1C
5333 | Slave04 EMD-6 Temperature | RO | 2 bytes | Unit0.1C
5334 | Slave04 EMD-7 Temperature | RO | 2 bytes | Unit0.1C
5335 | Slave04 EMD-8 Temperature | RO | 2 bytes | Unit0.1C
5336 | Slave05 EMD-1 Temperature | RO | 2 bytes | Unit0.1C
5337 | Slave05 EMD-2 Temperature | RO | 2 bytes | Unit0.1C
5338 | Slave05 EMD-3 Temperature | RO | 2 bytes | Unit0.1C
5339 | Slave05 EMD-4 Temperature | RO | 2 bytes | Unit0.1C
5340 | Slave05 EMD-5 Temperature | RO | 2 bytes | Unit0.1C
5341 | Slave05 EMD-6 Temperature | RO | 2 bytes | Unit0.1C
5342 | Slave05 EMD-7 Temperature | RO | 2 bytes | Unit0.1C
5343 | Slave05 EMD-8 Temperature | RO | 2 bytes | Unit0.1C
5344 | Slave06 EMD-1 Temperature | RO | 2 bytes | Unit0.1C
5345 | Slave06 EMD-2 Temperature | RO | 2 bytes | Unit0.1C
5346 | Slave06 EMD-3 Temperature | RO | 2 bytes | Unit0.1C
5347 | Slave06 EMD-4 Temperature | RO | 2 bytes | Unit0.1C
5348 | Slave06 EMD-5 Temperature | RO | 2 bytes | Unit0.1C
5349 | Slave06 EMD-6 Temperature | RO | 2 bytes | Unit0.1C
5350 | Slave06 EMD-7 Temperature | RO | 2 bytes | Unit0.1C
5351 | Slave06 EMD-8 Temperature | RO | 2 bytes | Unit0.1C
5352 | Slave07 EMD-1 Temperature | RO | 2 bytes | Unit0.1C
5353 | Slave07 EMD-2 Temperature | RO | 2 bytes | Unit0.1C
5354 | Slave07 EMD-3 Temperature | RO | 2 bytes | Unit0.1C
5355 | Slave07 EMD-4 Temperature | RO | 2 bytes | Unit0.1C
5356 | Slave07 EMD-5 Temperature | RO | 2 bytes | Unit0.1C
5357 | Slave07 EMD-6 Temperature | RO | 2 bytes | Unit0.1C
5358 | Slave07 EMD-7 Temperature | RO | 2 bytes | Unit0.1C
5359 | Slave07 EMD-8 Temperature | RO | 2 bytes | Unit0.1C
5360 | Slave08 EMD-1 Temperature | RO | 2 bytes | Unit0.1C
5361 | Slave08 EMD-2 Temperature | RO | 2 bytes | Unit0.1C
5362 | Slave08 EMD-3 Temperature | RO | 2 bytes | Unit0.1C
5363 | Slave08 EMD-4 Temperature | RO | 2 bytes | Unit0.1C
5364 | Slave08 EMD-5 Temperature | RO | 2 bytes | Unit0.1C
5365 | Slave08 EMD-6 Temperature | RO | 2 bytes | Unit0.1C
5366 | Slave08 EMD-7 Temperature | RO | 2 bytes | Unit0.1C
5367 | Slave08 EMD-8 Temperature | RO | 2 bytes | Unit0.1C
5368 | Slave09 EMD-1 Temperature | RO | 2 bytes | Unit0.1C
5369 | Slave09 EMD-2 Temperature | RO | 2 bytes | Unit0.1C
5370 | Slave09 EMD-3 Temperature | RO | 2 bytes | Unit0.1C
5371 | Slave09 EMD-4 Temperature | RO | 2 bytes | Unit0.1C
5372 | Slave09 EMD-5 Temperature | RO | 2 bytes | Unit0.1C
5373 | Slave09 EMD-6 Temperature | RO | 2 bytes | Unit0.1C
5374 | Slave09 EMD-7 Temperature | RO | 2 bytes | Unit0.1C
5375 | Slave09 EMD-8 Temperature | RO | 2 bytes | Unit0.1C
5376 | Slave10 EMD-1 Temperature | RO | 2 bytes | Unit0.1C
5377 | Slave10 EMD-2 Temperature | RO | 2 bytes | Unit0.1C
5378 | Slave10 EMD-3 Temperature | RO | 2 bytes | Unit0.1C
5379 | Slave10 EMD-4 Temperature | RO | 2 bytes | Unit0.1C
5380 | Slave10 EMD-5 Temperature | RO | 2 bytes | Unit0.1C
5381 | Slave10 EMD-6 Temperature | RO | 2 bytes | Unit0.1C
5382 | Slave10 EMD-7 Temperature | RO | 2 bytes | Unit0.1C
5383 | Slave10 EMD-8 Temperature | RO | 2 bytes | Unit0.1C
5384 | Slave11 EMD-1 Temperature | RO | 2 bytes | Unit0.1C
5385 | Slave11 EMD-2 Temperature | RO | 2 bytes | Unit0.1C
5386 | Slave11 EMD-3 Temperature | RO | 2 bytes | Unit0.1C
5387 | Slave11 EMD-4 Temperature | RO | 2 bytes | Unit0.1C
5388 | Slave11 EMD-5 Temperature | RO | 2 bytes | Unit0.1C
5389 | Slave11 EMD-6 Temperature | RO | 2 bytes | Unit0.1C
5390 | Slave11 EMD-7 Temperature | RO | 2 bytes | Unit0.1C
5391 | Slave11 EMD-8 Temperature | RO | 2 bytes | Unit0.1C
5392 | Slave12 EMD-1 Temperature | RO | 2 bytes | Unit0.1C
5393 | Slave12 EMD-2 Temperature | RO | 2 bytes | Unit0.1C
5394 | Slave12 EMD-3 Temperature | RO | 2 bytes | Unit0.1C
5395 | Slave12 EMD-4 Temperature | RO | 2 bytes | Unit0.1C
5396 | Slave12 EMD-5 Temperature | RO | 2 bytes | Unit0.1C
5397 | Slave12 EMD-6 Temperature | RO | 2 bytes | Unit0.1C
5398 | Slave12 EMD-7 Temperature | RO | 2 bytes | Unit0.1C
5399 | Slave12 EMD-8 Temperature | RO | 2 bytes | Unit0.1C
5400 | Slave13 EMD-1 Temperature | RO | 2 bytes | Unit0.1C
5401 | Slave13 EMD-2 Temperature | RO | 2 bytes | Unit0.1C
5402 | Slave13 EMD-3 Temperature | RO | 2 bytes | Unit0.1C
5403 | Slave13 EMD-4 Temperature | RO | 2 bytes | Unit0.1C
5404 | Slave13 EMD-5 Temperature | RO | 2 bytes | Unit0.1C
5405 | Slave13 EMD-6 Temperature | RO | 2 bytes | Unit0.1C
5406 | Slave13 EMD-7 Temperature | RO | 2 bytes | Unit0.1C
5407 | Slave13 EMD-8 Temperature | RO | 2 bytes | Unit0.1C
5408 | Slave14 EMD-1 Temperature | RO | 2 bytes | Unit0.1C
5409 | Slave14 EMD-2 Temperature | RO | 2 bytes | Unit0.1C
5410 | Slave14 EMD-3 Temperature | RO | 2 bytes | Unit0.1C
5411 | Slave14 EMD-4 Temperature | RO | 2 bytes | Unit0.1C
5412 | Slave14 EMD-5 Temperature | RO | 2 bytes | Unit0.1C
5413 | Slave14 EMD-6 Temperature | RO | 2 bytes | Unit0.1C
5414 | Slave14 EMD-7 Temperature | RO | 2 bytes | Unit0.1C
5415 | Slave14 EMD-8 Temperature | RO | 2 bytes | Unit0.1C
5416 | Slave15 EMD-1 Temperature | RO | 2 bytes | Unit0.1C
5417 | Slave15 EMD-2 Temperature | RO | 2 bytes | Unit0.1C
5418 | Slave15 EMD-3 Temperature | RO | 2 bytes | Unit0.1C
5419 | Slave15 EMD-4 Temperature | RO | 2 bytes | Unit0.1C
5420 | Slave15 EMD-5 Temperature | RO | 2 bytes | Unit0.1C
5421 | Slave15 EMD-6 Temperature | RO | 2 bytes | Unit0.1C
5422 | Slave15 EMD-7 Temperature | RO | 2 bytes | Unit0.1C
5423 | Slave15 EMD-8 Temperature | RO | 2 bytes | Unit0.1C
5424 | Master EMD-1 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5425 | Master EMD-2 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5426 | Master EMD-3 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5427 | Master EMD-4 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5428 | Master EMD-5 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5429 | Master EMD-6 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5430 | Master EMD-7 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5431 | Master EMD-8 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5432 | Slave01 EMD-1 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5433 | Slave01 EMD-2 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5434 | Slave01 EMD-3 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5435 | Slave01 EMD-4 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5436 | Slave01 EMD-5 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5437 | Slave01 EMD-6 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5438 | Slave01 EMD-7 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5439 | Slave01 EMD-8 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5440 | Slave02 EMD-1 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5441 | Slave02 EMD-2 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5442 | Slave02 EMD-3 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5443 | Slave02 EMD-4 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5444 | Slave02 EMD-5 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5445 | Slave02 EMD-6 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5446 | Slave02 EMD-7 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5447 | Slave02 EMD-8 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5448 | Slave03 EMD-1 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5449 | Slave03 EMD-2 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5450 | Slave03 EMD-3 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5451 | Slave03 EMD-4 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5452 | Slave03 EMD-5 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5453 | Slave03 EMD-6 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5454 | Slave03 EMD-7 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5455 | Slave03 EMD-8 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5456 | Slave04 EMD-1 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5457 | Slave04 EMD-2 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5458 | Slave04 EMD-3 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5459 | Slave04 EMD-4 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5460 | Slave04 EMD-5 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5461 | Slave04 EMD-6 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5462 | Slave04 EMD-7 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5463 | Slave04 EMD-8 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5464 | Slave05 EMD-1 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5465 | Slave05 EMD-2 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5466 | Slave05 EMD-3 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5467 | Slave05 EMD-4 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5468 | Slave05 EMD-5 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5469 | Slave05 EMD-6 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5470 | Slave05 EMD-7 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5471 | Slave05 EMD-8 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5472 | Slave06 EMD-1 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5473 | Slave06 EMD-2 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5474 | Slave06 EMD-3 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5475 | Slave06 EMD-4 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5476 | Slave06 EMD-5 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5477 | Slave06 EMD-6 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5478 | Slave06 EMD-7 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5479 | Slave06 EMD-8 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5480 | Slave07 EMD-1 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5481 | Slave07 EMD-2 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5482 | Slave07 EMD-3 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5483 | Slave07 EMD-4 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5484 | Slave07 EMD-5 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5485 | Slave07 EMD-6 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5486 | Slave07 EMD-7 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5487 | Slave07 EMD-8 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5488 | Slave08 EMD-1 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5489 | Slave08 EMD-2 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5490 | Slave08 EMD-3 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5491 | Slave08 EMD-4 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5492 | Slave08 EMD-5 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5493 | Slave08 EMD-6 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5494 | Slave08 EMD-7 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5495 | Slave08 EMD-8 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5496 | Slave09 EMD-1 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5497 | Slave09 EMD-2 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5498 | Slave09 EMD-3 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5499 | Slave09 EMD-4 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5500 | Slave09 EMD-5 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5501 | Slave09 EMD-6 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5502 | Slave09 EMD-7 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5503 | Slave09 EMD-8 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5504 | Slave10 EMD-1 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5505 | Slave10 EMD-2 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5506 | Slave10 EMD-3 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5507 | Slave10 EMD-4 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5508 | Slave10 EMD-5 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5509 | Slave10 EMD-6 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5510 | Slave10 EMD-7 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5511 | Slave10 EMD-8 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5512 | Slave11 EMD-1 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5513 | Slave11 EMD-2 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5514 | Slave11 EMD-3 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5515 | Slave11 EMD-4 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5516 | Slave11 EMD-5 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5517 | Slave11 EMD-6 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5518 | Slave11 EMD-7 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5519 | Slave11 EMD-8 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5520 | Slave12 EMD-1 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5521 | Slave12 EMD-2 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5522 | Slave12 EMD-3 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5523 | Slave12 EMD-4 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5524 | Slave12 EMD-5 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5525 | Slave12 EMD-6 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5526 | Slave12 EMD-7 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5527 | Slave12 EMD-8 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5528 | Slave13 EMD-1 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5529 | Slave13 EMD-2 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5530 | Slave13 EMD-3 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5531 | Slave13 EMD-4 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5532 | Slave13 EMD-5 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5533 | Slave13 EMD-6 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5534 | Slave13 EMD-7 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5535 | Slave13 EMD-8 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5536 | Slave14 EMD-1 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5537 | Slave14 EMD-2 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5538 | Slave14 EMD-3 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5539 | Slave14 EMD-4 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5540 | Slave14 EMD-5 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5541 | Slave14 EMD-6 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5542 | Slave14 EMD-7 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5543 | Slave14 EMD-8 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5544 | Slave15 EMD-1 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5545 | Slave15 EMD-2 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5546 | Slave15 EMD-3 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5547 | Slave15 EMD-4 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5548 | Slave15 EMD-5 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5549 | Slave15 EMD-6 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5550 | Slave15 EMD-7 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5551 | Slave15 EMD-8 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5552 | Master EMD-1 Humidity | RO | 2 bytes | Unit:0.1%
5553 | Master EMD-2 Humidity | RO | 2 bytes | Unit:0.1%
5554 | Master EMD-3 Humidity | RO | 2 bytes | Unit:0.1%
5555 | Master EMD-4 Humidity | RO | 2 bytes | Unit:0.1%
5556 | Master EMD-5 Humidity | RO | 2 bytes | Unit:0.1%
5557 | Master EMD-6 Humidity | RO | 2 bytes | Unit:0.1%
5558 | Master EMD-7 Humidity | RO | 2 bytes | Unit:0.1%
5559 | Master EMD-8 Humidity | RO | 2 bytes | Unit:0.1%
5560 | Slave01 EMD-1 Humidity | RO | 2 bytes | Unit:0.1%
5561 | Slave01 EMD-2 Humidity | RO | 2 bytes | Unit:0.1%
5562 | Slave01 EMD-3 Humidity | RO | 2 bytes | Unit:0.1%
5563 | Slave01 EMD-4 Humidity | RO | 2 bytes | Unit:0.1%
5564 | Slave01 EMD-5 Humidity | RO | 2 bytes | Unit:0.1%
5565 | Slave01 EMD-6 Humidity | RO | 2 bytes | Unit:0.1%
5566 | Slave01 EMD-7 Humidity | RO | 2 bytes | Unit:0.1%
5567 | Slave01 EMD-8 Humidity | RO | 2 bytes | Unit:0.1%
5568 | Slave02 EMD-1 Humidity | RO | 2 bytes | Unit:0.1%
5569 | Slave02 EMD-2 Humidity | RO | 2 bytes | Unit:0.1%
5570 | Slave02 EMD-3 Humidity | RO | 2 bytes | Unit:0.1%
5571 | Slave02 EMD-4 Humidity | RO | 2 bytes | Unit:0.1%
5572 | Slave02 EMD-5 Humidity | RO | 2 bytes | Unit:0.1%
5573 | Slave02 EMD-6 Humidity | RO | 2 bytes | Unit:0.1%
5574 | Slave02 EMD-7 Humidity | RO | 2 bytes | Unit:0.1%
5575 | Slave02 EMD-8 Humidity | RO | 2 bytes | Unit:0.1%
5576 | Slave03 EMD-1 Humidity | RO | 2 bytes | Unit:0.1%
5577 | Slave03 EMD-2 Humidity | RO | 2 bytes | Unit:0.1%
5578 | Slave03 EMD-3 Humidity | RO | 2 bytes | Unit:0.1%
5579 | Slave03 EMD-4 Humidity | RO | 2 bytes | Unit:0.1%
5580 | Slave03 EMD-5 Humidity | RO | 2 bytes | Unit:0.1%
5581 | Slave03 EMD-6 Humidity | RO | 2 bytes | Unit:0.1%
5582 | Slave03 EMD-7 Humidity | RO | 2 bytes | Unit:0.1%
5583 | Slave03 EMD-8 Humidity | RO | 2 bytes | Unit:0.1%
5584 | Slave04 EMD-1 Humidity | RO | 2 bytes | Unit:0.1%
5585 | Slave04 EMD-2 Humidity | RO | 2 bytes | Unit:0.1%
5586 | Slave04 EMD-3 Humidity | RO | 2 bytes | Unit:0.1%
5587 | Slave04 EMD-4 Humidity | RO | 2 bytes | Unit:0.1%
5588 | Slave04 EMD-5 Humidity | RO | 2 bytes | Unit:0.1%
5589 | Slave04 EMD-6 Humidity | RO | 2 bytes | Unit:0.1%
5590 | Slave04 EMD-7 Humidity | RO | 2 bytes | Unit:0.1%
5591 | Slave04 EMD-8 Humidity | RO | 2 bytes | Unit:0.1%
5592 | Slave05 EMD-1 Humidity | RO | 2 bytes | Unit:0.1%
5593 | Slave05 EMD-2 Humidity | RO | 2 bytes | Unit:0.1%
5594 | Slave05 EMD-3 Humidity | RO | 2 bytes | Unit:0.1%
5595 | Slave05 EMD-4 Humidity | RO | 2 bytes | Unit:0.1%
5596 | Slave05 EMD-5 Humidity | RO | 2 bytes | Unit:0.1%
5597 | Slave05 EMD-6 Humidity | RO | 2 bytes | Unit:0.1%
5598 | Slave05 EMD-7 Humidity | RO | 2 bytes | Unit:0.1%
5599 | Slave05 EMD-8 Humidity | RO | 2 bytes | Unit:0.1%
5600 | Slave06 EMD-1 Humidity | RO | 2 bytes | Unit:0.1%
5601 | Slave06 EMD-2 Humidity | RO | 2 bytes | Unit:0.1%
5602 | Slave06 EMD-3 Humidity | RO | 2 bytes | Unit:0.1%
5603 | Slave06 EMD-4 Humidity | RO | 2 bytes | Unit:0.1%
5604 | Slave06 EMD-5 Humidity | RO | 2 bytes | Unit:0.1%
5605 | Slave06 EMD-6 Humidity | RO | 2 bytes | Unit:0.1%
5606 | Slave06 EMD-7 Humidity | RO | 2 bytes | Unit:0.1%
5607 | Slave06 EMD-8 Humidity | RO | 2 bytes | Unit:0.1%
5608 | Slave07 EMD-1 Humidity | RO | 2 bytes | Unit:0.1%
5609 | Slave07 EMD-2 Humidity | RO | 2 bytes | Unit:0.1%
5610 | Slave07 EMD-3 Humidity | RO | 2 bytes | Unit:0.1%
5611 | Slave07 EMD-4 Humidity | RO | 2 bytes | Unit:0.1%
5612 | Slave07 EMD-5 Humidity | RO | 2 bytes | Unit:0.1%
5613 | Slave07 EMD-6 Humidity | RO | 2 bytes | Unit:0.1%
5614 | Slave07 EMD-7 Humidity | RO | 2 bytes | Unit:0.1%
5615 | Slave07 EMD-8 Humidity | RO | 2 bytes | Unit:0.1%
5616 | Slave08 EMD-1 Humidity | RO | 2 bytes | Unit:0.1%
5617 | Slave08 EMD-2 Humidity | RO | 2 bytes | Unit:0.1%
5618 | Slave08 EMD-3 Humidity | RO | 2 bytes | Unit:0.1%
5619 | Slave08 EMD-4 Humidity | RO | 2 bytes | Unit:0.1%
5620 | Slave08 EMD-5 Humidity | RO | 2 bytes | Unit:0.1%
5621 | Slave08 EMD-6 Humidity | RO | 2 bytes | Unit:0.1%
5622 | Slave08 EMD-7 Humidity | RO | 2 bytes | Unit:0.1%
5623 | Slave08 EMD-8 Humidity | RO | 2 bytes | Unit:0.1%
5624 | Slave09 EMD-1 Humidity | RO | 2 bytes | Unit:0.1%
5625 | Slave09 EMD-2 Humidity | RO | 2 bytes | Unit:0.1%
5626 | Slave09 EMD-3 Humidity | RO | 2 bytes | Unit:0.1%
5627 | Slave09 EMD-4 Humidity | RO | 2 bytes | Unit:0.1%
5628 | Slave09 EMD-5 Humidity | RO | 2 bytes | Unit:0.1%
5629 | Slave09 EMD-6 Humidity | RO | 2 bytes | Unit:0.1%
5630 | Slave09 EMD-7 Humidity | RO | 2 bytes | Unit:0.1%
5631 | Slave09 EMD-8 Humidity | RO | 2 bytes | Unit:0.1%
5632 | Slave10 EMD-1 Humidity | RO | 2 bytes | Unit:0.1%
5633 | Slave10 EMD-2 Humidity | RO | 2 bytes | Unit:0.1%
5634 | Slave10 EMD-3 Humidity | RO | 2 bytes | Unit:0.1%
5635 | Slave10 EMD-4 Humidity | RO | 2 bytes | Unit:0.1%
5636 | Slave10 EMD-5 Humidity | RO | 2 bytes | Unit:0.1%
5637 | Slave10 EMD-6 Humidity | RO | 2 bytes | Unit:0.1%
5638 | Slave10 EMD-7 Humidity | RO | 2 bytes | Unit:0.1%
5639 | Slave10 EMD-8 Humidity | RO | 2 bytes | Unit:0.1%
5640 | Slave11 EMD-1 Humidity | RO | 2 bytes | Unit:0.1%
5641 | Slave11 EMD-2 Humidity | RO | 2 bytes | Unit:0.1%
5642 | Slave11 EMD-3 Humidity | RO | 2 bytes | Unit:0.1%
5643 | Slave11 EMD-4 Humidity | RO | 2 bytes | Unit:0.1%
5644 | Slave11 EMD-5 Humidity | RO | 2 bytes | Unit:0.1%
5645 | Slave11 EMD-6 Humidity | RO | 2 bytes | Unit:0.1%
5646 | Slave11 EMD-7 Humidity | RO | 2 bytes | Unit:0.1%
5647 | Slave11 EMD-8 Humidity | RO | 2 bytes | Unit:0.1%
5648 | Slave12 EMD-1 Humidity | RO | 2 bytes | Unit:0.1%
5649 | Slave12 EMD-2 Humidity | RO | 2 bytes | Unit:0.1%
5650 | Slave12 EMD-3 Humidity | RO | 2 bytes | Unit:0.1%
5651 | Slave12 EMD-4 Humidity | RO | 2 bytes | Unit:0.1%
5652 | Slave12 EMD-5 Humidity | RO | 2 bytes | Unit:0.1%
5653 | Slave12 EMD-6 Humidity | RO | 2 bytes | Unit:0.1%
5654 | Slave12 EMD-7 Humidity | RO | 2 bytes | Unit:0.1%
5655 | Slave12 EMD-8 Humidity | RO | 2 bytes | Unit:0.1%
5656 | Slave13 EMD-1 Humidity | RO | 2 bytes | Unit:0.1%
5657 | Slave13 EMD-2 Humidity | RO | 2 bytes | Unit:0.1%
5658 | Slave13 EMD-3 Humidity | RO | 2 bytes | Unit:0.1%
5659 | Slave13 EMD-4 Humidity | RO | 2 bytes | Unit:0.1%
5660 | Slave13 EMD-5 Humidity | RO | 2 bytes | Unit:0.1%
5661 | Slave13 EMD-6 Humidity | RO | 2 bytes | Unit:0.1%
5662 | Slave13 EMD-7 Humidity | RO | 2 bytes | Unit:0.1%
5663 | Slave13 EMD-8 Humidity | RO | 2 bytes | Unit:0.1%
5664 | Slave14 EMD-1 Humidity | RO | 2 bytes | Unit:0.1%
5665 | Slave14 EMD-2 Humidity | RO | 2 bytes | Unit:0.1%
5666 | Slave14 EMD-3 Humidity | RO | 2 bytes | Unit:0.1%
5667 | Slave14 EMD-4 Humidity | RO | 2 bytes | Unit:0.1%
5668 | Slave14 EMD-5 Humidity | RO | 2 bytes | Unit:0.1%
5669 | Slave14 EMD-6 Humidity | RO | 2 bytes | Unit:0.1%
5670 | Slave14 EMD-7 Humidity | RO | 2 bytes | Unit:0.1%
5671 | Slave14 EMD-8 Humidity | RO | 2 bytes | Unit:0.1%
5672 | Slave15 EMD-1 Humidity | RO | 2 bytes | Unit:0.1%
5673 | Slave15 EMD-2 Humidity | RO | 2 bytes | Unit:0.1%
5674 | Slave15 EMD-3 Humidity | RO | 2 bytes | Unit:0.1%
5675 | Slave15 EMD-4 Humidity | RO | 2 bytes | Unit:0.1%
5676 | Slave15 EMD-5 Humidity | RO | 2 bytes | Unit:0.1%
5677 | Slave15 EMD-6 Humidity | RO | 2 bytes | Unit:0.1%
5678 | Slave15 EMD-7 Humidity | RO | 2 bytes | Unit:0.1%
5679 | Slave15 EMD-8 Humidity | RO | 2 bytes | Unit:0.1%
5680 | Master EMD-1 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5681 | Master EMD-2 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5682 | Master EMD-3 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5683 | Master EMD-4 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5684 | Master EMD-5 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5685 | Master EMD-6 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5686 | Master EMD-7 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5687 | Master EMD-8 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5688 | Slave01 EMD-1 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5689 | Slave01 EMD-2 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5690 | Slave01 EMD-3 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5691 | Slave01 EMD-4 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5692 | Slave01 EMD-5 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5693 | Slave01 EMD-6 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5694 | Slave01 EMD-7 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5695 | Slave01 EMD-8 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5696 | Slave02 EMD-1 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5697 | Slave02 EMD-2 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5698 | Slave02 EMD-3 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5699 | Slave02 EMD-4 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5700 | Slave02 EMD-5 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5701 | Slave02 EMD-6 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5702 | Slave02 EMD-7 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5703 | Slave02 EMD-8 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5704 | Slave03 EMD-1 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5705 | Slave03 EMD-2 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5706 | Slave03 EMD-3 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5707 | Slave03 EMD-4 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5708 | Slave03 EMD-5 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5709 | Slave03 EMD-6 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5710 | Slave03 EMD-7 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5711 | Slave03 EMD-8 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5712 | Slave04 EMD-1 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5713 | Slave04 EMD-2 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5714 | Slave04 EMD-3 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5715 | Slave04 EMD-4 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5716 | Slave04 EMD-5 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5717 | Slave04 EMD-6 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5718 | Slave04 EMD-7 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5719 | Slave04 EMD-8 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5720 | Slave05 EMD-1 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5721 | Slave05 EMD-2 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5722 | Slave05 EMD-3 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5723 | Slave05 EMD-4 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5724 | Slave05 EMD-5 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5725 | Slave05 EMD-6 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5726 | Slave05 EMD-7 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5727 | Slave05 EMD-8 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5728 | Slave06 EMD-1 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5729 | Slave06 EMD-2 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5730 | Slave06 EMD-3 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5731 | Slave06 EMD-4 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5732 | Slave06 EMD-5 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5733 | Slave06 EMD-6 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5734 | Slave06 EMD-7 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5735 | Slave06 EMD-8 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5736 | Slave07 EMD-1 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5737 | Slave07 EMD-2 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5738 | Slave07 EMD-3 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5739 | Slave07 EMD-4 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5740 | Slave07 EMD-5 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5741 | Slave07 EMD-6 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5742 | Slave07 EMD-7 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5743 | Slave07 EMD-8 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5744 | Slave08 EMD-1 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5745 | Slave08 EMD-2 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5746 | Slave08 EMD-3 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5747 | Slave08 EMD-4 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5748 | Slave08 EMD-5 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5749 | Slave08 EMD-6 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5750 | Slave08 EMD-7 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5751 | Slave08 EMD-8 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5752 | Slave09 EMD-1 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5753 | Slave09 EMD-2 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5754 | Slave09 EMD-3 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5755 | Slave09 EMD-4 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5756 | Slave09 EMD-5 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5757 | Slave09 EMD-6 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5758 | Slave09 EMD-7 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5759 | Slave09 EMD-8 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5760 | Slave10 EMD-1 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5761 | Slave10 EMD-2 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5762 | Slave10 EMD-3 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5763 | Slave10 EMD-4 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5764 | Slave10 EMD-5 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5765 | Slave10 EMD-6 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5766 | Slave10 EMD-7 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5767 | Slave10 EMD-8 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5768 | Slave11 EMD-1 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5769 | Slave11 EMD-2 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5770 | Slave11 EMD-3 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5771 | Slave11 EMD-4 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5772 | Slave11 EMD-5 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5773 | Slave11 EMD-6 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5774 | Slave11 EMD-7 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5775 | Slave11 EMD-8 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5776 | Slave12 EMD-1 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5777 | Slave12 EMD-2 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5778 | Slave12 EMD-3 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5779 | Slave12 EMD-4 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5780 | Slave12 EMD-5 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5781 | Slave12 EMD-6 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5782 | Slave12 EMD-7 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5783 | Slave12 EMD-8 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5784 | Slave13 EMD-1 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5785 | Slave13 EMD-2 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5786 | Slave13 EMD-3 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5787 | Slave13 EMD-4 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5788 | Slave13 EMD-5 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5789 | Slave13 EMD-6 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5790 | Slave13 EMD-7 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5791 | Slave13 EMD-8 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5792 | Slave14 EMD-1 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5793 | Slave14 EMD-2 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5794 | Slave14 EMD-3 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5795 | Slave14 EMD-4 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5796 | Slave14 EMD-5 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5797 | Slave14 EMD-6 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5798 | Slave14 EMD-7 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5799 | Slave14 EMD-8 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5800 | Slave15 EMD-1 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5801 | Slave15 EMD-2 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5802 | Slave15 EMD-3 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5803 | Slave15 EMD-4 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5804 | Slave15 EMD-5 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5805 | Slave15 EMD-6 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5806 | Slave15 EMD-7 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5807 | Slave15 EMD-8 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
5808 | Master EMD-1 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
5809 | Master EMD-2 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
5810 | Master EMD-3 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
5811 | Master EMD-4 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
5812 | Master EMD-5 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
5813 | Master EMD-6 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
5814 | Master EMD-7 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
5815 | Master EMD-8 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
5816 | Slave01 EMD-1 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
5817 | Slave01 EMD-2 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
5818 | Slave01 EMD-3 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
5819 | Slave01 EMD-4 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
5820 | Slave01 EMD-5 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
5821 | Slave01 EMD-6 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
5822 | Slave01 EMD-7 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
5823 | Slave01 EMD-8 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
5824 | Slave02 EMD-1 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
5825 | Slave02 EMD-2 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
5826 | Slave02 EMD-3 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
5827 | Slave02 EMD-4 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
5828 | Slave02 EMD-5 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
5829 | Slave02 EMD-6 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
5830 | Slave02 EMD-7 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
5831 | Slave02 EMD-8 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
5832 | Slave03 EMD-1 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
5833 | Slave03 EMD-2 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
5834 | Slave03 EMD-3 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
5835 | Slave03 EMD-4 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
5836 | Slave03 EMD-5 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
5837 | Slave03 EMD-6 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
5838 | Slave03 EMD-7 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
5839 | Slave03 EMD-8 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
5840 | Slave04 EMD-1 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
5841 | Slave04 EMD-2 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
5842 | Slave04 EMD-3 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
5843 | Slave04 EMD-4 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
5844 | Slave04 EMD-5 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
5845 | Slave04 EMD-6 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
5846 | Slave04 EMD-7 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
5847 | Slave04 EMD-8 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
5848 | Slave05 EMD-1 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
5849 | Slave05 EMD-2 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
5850 | Slave05 EMD-3 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
5851 | Slave05 EMD-4 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
5852 | Slave05 EMD-5 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
5853 | Slave05 EMD-6 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
5854 | Slave05 EMD-7 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
5855 | Slave05 EMD-8 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
5856 | Slave06 EMD-1 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
5857 | Slave06 EMD-2 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
5858 | Slave06 EMD-3 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
5859 | Slave06 EMD-4 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
5860 | Slave06 EMD-5 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
5861 | Slave06 EMD-6 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
5862 | Slave06 EMD-7 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
5863 | Slave06 EMD-8 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
5864 | Slave07 EMD-1 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
5865 | Slave07 EMD-2 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
5866 | Slave07 EMD-3 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
5867 | Slave07 EMD-4 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
5868 | Slave07 EMD-5 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
5869 | Slave07 EMD-6 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
5870 | Slave07 EMD-7 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
5871 | Slave07 EMD-8 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
5872 | Slave08 EMD-1 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
5873 | Slave08 EMD-2 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
5874 | Slave08 EMD-3 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
5875 | Slave08 EMD-4 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
5876 | Slave08 EMD-5 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
5877 | Slave08 EMD-6 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
5878 | Slave08 EMD-7 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
5879 | Slave08 EMD-8 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
5880 | Slave09 EMD-1 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
5881 | Slave09 EMD-2 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
5882 | Slave09 EMD-3 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
5883 | Slave09 EMD-4 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
5884 | Slave09 EMD-5 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
5885 | Slave09 EMD-6 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
5886 | Slave09 EMD-7 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
5887 | Slave09 EMD-8 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
5888 | Slave10 EMD-1 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
5889 | Slave10 EMD-2 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
5890 | Slave10 EMD-3 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
5891 | Slave10 EMD-4 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
5892 | Slave10 EMD-5 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
5893 | Slave10 EMD-6 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
5894 | Slave10 EMD-7 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
5895 | Slave10 EMD-8 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
5896 | Slave11 EMD-1 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
5897 | Slave11 EMD-2 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
5898 | Slave11 EMD-3 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
5899 | Slave11 EMD-4 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
5900 | Slave11 EMD-5 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
5901 | Slave11 EMD-6 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
5902 | Slave11 EMD-7 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
5903 | Slave11 EMD-8 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
5904 | Slave12 EMD-1 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
5905 | Slave12 EMD-2 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
5906 | Slave12 EMD-3 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
5907 | Slave12 EMD-4 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
5908 | Slave12 EMD-5 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
5909 | Slave12 EMD-6 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
5910 | Slave12 EMD-7 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
5911 | Slave12 EMD-8 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
5912 | Slave13 EMD-1 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
5913 | Slave13 EMD-2 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
5914 | Slave13 EMD-3 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
5915 | Slave13 EMD-4 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
5916 | Slave13 EMD-5 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
5917 | Slave13 EMD-6 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
5918 | Slave13 EMD-7 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
5919 | Slave13 EMD-8 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
5920 | Slave14 EMD-1 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
5921 | Slave14 EMD-2 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
5922 | Slave14 EMD-3 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
5923 | Slave14 EMD-4 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
5924 | Slave14 EMD-5 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
5925 | Slave14 EMD-6 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
5926 | Slave14 EMD-7 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
5927 | Slave14 EMD-8 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
5928 | Slave15 EMD-1 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
5929 | Slave15 EMD-2 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
5930 | Slave15 EMD-3 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
5931 | Slave15 EMD-4 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
5932 | Slave15 EMD-5 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
5933 | Slave15 EMD-6 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
5934 | Slave15 EMD-7 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
5935 | Slave15 EMD-8 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
5936 | Master EMD-1 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
5937 | Master EMD-2 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
5938 | Master EMD-3 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
5939 | Master EMD-4 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
5940 | Master EMD-5 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
5941 | Master EMD-6 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
5942 | Master EMD-7 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
5943 | Master EMD-8 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
5944 | Slave01 EMD-1 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
5945 | Slave01 EMD-2 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
5946 | Slave01 EMD-3 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
5947 | Slave01 EMD-4 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
5948 | Slave01 EMD-5 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
5949 | Slave01 EMD-6 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
5950 | Slave01 EMD-7 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
5951 | Slave01 EMD-8 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
5952 | Slave02 EMD-1 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
5953 | Slave02 EMD-2 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
5954 | Slave02 EMD-3 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
5955 | Slave02 EMD-4 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
5956 | Slave02 EMD-5 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
5957 | Slave02 EMD-6 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
5958 | Slave02 EMD-7 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
5959 | Slave02 EMD-8 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
5960 | Slave03 EMD-1 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
5961 | Slave03 EMD-2 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
5962 | Slave03 EMD-3 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
5963 | Slave03 EMD-4 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
5964 | Slave03 EMD-5 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
5965 | Slave03 EMD-6 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
5966 | Slave03 EMD-7 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
5967 | Slave03 EMD-8 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
5968 | Slave04 EMD-1 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
5969 | Slave04 EMD-2 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
5970 | Slave04 EMD-3 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
5971 | Slave04 EMD-4 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
5972 | Slave04 EMD-5 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
5973 | Slave04 EMD-6 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
5974 | Slave04 EMD-7 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
5975 | Slave04 EMD-8 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
5976 | Slave05 EMD-1 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
5977 | Slave05 EMD-2 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
5978 | Slave05 EMD-3 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
5979 | Slave05 EMD-4 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
5980 | Slave05 EMD-5 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
5981 | Slave05 EMD-6 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
5982 | Slave05 EMD-7 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
5983 | Slave05 EMD-8 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
5984 | Slave06 EMD-1 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
5985 | Slave06 EMD-2 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
5986 | Slave06 EMD-3 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
5987 | Slave06 EMD-4 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
5988 | Slave06 EMD-5 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
5989 | Slave06 EMD-6 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
5990 | Slave06 EMD-7 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
5991 | Slave06 EMD-8 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
5992 | Slave07 EMD-1 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
5993 | Slave07 EMD-2 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
5994 | Slave07 EMD-3 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
5995 | Slave07 EMD-4 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
5996 | Slave07 EMD-5 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
5997 | Slave07 EMD-6 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
5998 | Slave07 EMD-7 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
5999 | Slave07 EMD-8 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6000 | Slave08 EMD-1 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6001 | Slave08 EMD-2 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6002 | Slave08 EMD-3 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6003 | Slave08 EMD-4 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6004 | Slave08 EMD-5 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6005 | Slave08 EMD-6 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6006 | Slave08 EMD-7 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6007 | Slave08 EMD-8 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6008 | Slave09 EMD-1 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6009 | Slave09 EMD-2 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6010 | Slave09 EMD-3 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6011 | Slave09 EMD-4 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6012 | Slave09 EMD-5 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6013 | Slave09 EMD-6 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6014 | Slave09 EMD-7 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6015 | Slave09 EMD-8 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6016 | Slave10 EMD-1 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6017 | Slave10 EMD-2 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6018 | Slave10 EMD-3 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6019 | Slave10 EMD-4 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6020 | Slave10 EMD-5 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6021 | Slave10 EMD-6 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6022 | Slave10 EMD-7 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6023 | Slave10 EMD-8 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6024 | Slave11 EMD-1 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6025 | Slave11 EMD-2 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6026 | Slave11 EMD-3 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6027 | Slave11 EMD-4 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6028 | Slave11 EMD-5 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6029 | Slave11 EMD-6 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6030 | Slave11 EMD-7 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6031 | Slave11 EMD-8 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6032 | Slave12 EMD-1 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6033 | Slave12 EMD-2 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6034 | Slave12 EMD-3 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6035 | Slave12 EMD-4 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6036 | Slave12 EMD-5 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6037 | Slave12 EMD-6 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6038 | Slave12 EMD-7 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6039 | Slave12 EMD-8 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6040 | Slave13 EMD-1 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6041 | Slave13 EMD-2 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6042 | Slave13 EMD-3 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6043 | Slave13 EMD-4 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6044 | Slave13 EMD-5 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6045 | Slave13 EMD-6 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6046 | Slave13 EMD-7 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6047 | Slave13 EMD-8 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6048 | Slave14 EMD-1 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6049 | Slave14 EMD-2 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6050 | Slave14 EMD-3 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6051 | Slave14 EMD-4 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6052 | Slave14 EMD-5 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6053 | Slave14 EMD-6 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6054 | Slave14 EMD-7 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6055 | Slave14 EMD-8 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6056 | Slave15 EMD-1 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6057 | Slave15 EMD-2 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6058 | Slave15 EMD-3 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6059 | Slave15 EMD-4 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6060 | Slave15 EMD-5 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6061 | Slave15 EMD-6 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6062 | Slave15 EMD-7 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6063 | Slave15 EMD-8 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6064 | Master Inlet Phase1 Active Power | RO | 4 bytes | Unit:0.1
6066 | Slave01 Inlet Phase1 Active Power | RO | 4 bytes | Unit:0.1
6068 | Slave02 Inlet Phase1 Active Power | RO | 4 bytes | Unit:0.1
6070 | Slave03 Inlet Phase1 Active Power | RO | 4 bytes | Unit:0.1
6072 | Slave04 Inlet Phase1 Active Power | RO | 4 bytes | Unit:0.1
6074 | Slave05 Inlet Phase1 Active Power | RO | 4 bytes | Unit:0.1
6076 | Slave06 Inlet Phase1 Active Power | RO | 4 bytes | Unit:0.1
6078 | Slave07 Inlet Phase1 Active Power | RO | 4 bytes | Unit:0.1
6080 | Slave08 Inlet Phase1 Active Power | RO | 4 bytes | Unit:0.1
6082 | Slave09 Inlet Phase1 Active Power | RO | 4 bytes | Unit:0.1
6084 | Slave10 Inlet Phase1 Active Power | RO | 4 bytes | Unit:0.1
6086 | Slave11 Inlet Phase1 Active Power | RO | 4 bytes | Unit:0.1
6088 | Slave12 Inlet Phase1 Active Power | RO | 4 bytes | Unit:0.1
6090 | Slave13 Inlet Phase1 Active Power | RO | 4 bytes | Unit:0.1
6092 | Slave14 Inlet Phase1 Active Power | RO | 4 bytes | Unit:0.1
6094 | Slave15 Inlet Phase1 Active Power | RO | 4 bytes | Unit:0.1
6096 | Master Inlet Phase2 Active Power | RO | 4 bytes | Unit:0.1
6098 | Slave01 Inlet Phase2 Active Power | RO | 4 bytes | Unit:0.1
6100 | Slave02 Inlet Phase2 Active Power | RO | 4 bytes | Unit:0.1
6102 | Slave03 Inlet Phase2 Active Power | RO | 4 bytes | Unit:0.1
6104 | Slave04 Inlet Phase2 Active Power | RO | 4 bytes | Unit:0.1
6106 | Slave05 Inlet Phase2 Active Power | RO | 4 bytes | Unit:0.1
6108 | Slave06 Inlet Phase2 Active Power | RO | 4 bytes | Unit:0.1
6110 | Slave07 Inlet Phase2 Active Power | RO | 4 bytes | Unit:0.1
6112 | Slave08 Inlet Phase2 Active Power | RO | 4 bytes | Unit:0.1
6114 | Slave09 Inlet Phase2 Active Power | RO | 4 bytes | Unit:0.1
6116 | Slave10 Inlet Phase2 Active Power | RO | 4 bytes | Unit:0.1
6118 | Slave11 Inlet Phase2 Active Power | RO | 4 bytes | Unit:0.1
6120 | Slave12 Inlet Phase2 Active Power | RO | 4 bytes | Unit:0.1
6122 | Slave13 Inlet Phase2 Active Power | RO | 4 bytes | Unit:0.1
6124 | Slave14 Inlet Phase2 Active Power | RO | 4 bytes | Unit:0.1
6126 | Slave15 Inlet Phase2 Active Power | RO | 4 bytes | Unit:0.1
6128 | Master Inlet Phase3 Active Power | RO | 4 bytes | Unit:0.1
6130 | Slave01 Inlet Phase3 Active Power | RO | 4 bytes | Unit:0.1
6132 | Slave02 Inlet Phase3 Active Power | RO | 4 bytes | Unit:0.1
6134 | Slave03 Inlet Phase3 Active Power | RO | 4 bytes | Unit:0.1
6136 | Slave04 Inlet Phase3 Active Power | RO | 4 bytes | Unit:0.1
6138 | Slave05 Inlet Phase3 Active Power | RO | 4 bytes | Unit:0.1
6140 | Slave06 Inlet Phase3 Active Power | RO | 4 bytes | Unit:0.1
6142 | Slave07 Inlet Phase3 Active Power | RO | 4 bytes | Unit:0.1
6144 | Slave08 Inlet Phase3 Active Power | RO | 4 bytes | Unit:0.1
6146 | Slave09 Inlet Phase3 Active Power | RO | 4 bytes | Unit:0.1
6148 | Slave10 Inlet Phase3 Active Power | RO | 4 bytes | Unit:0.1
6150 | Slave11 Inlet Phase3 Active Power | RO | 4 bytes | Unit:0.1
6152 | Slave12 Inlet Phase3 Active Power | RO | 4 bytes | Unit:0.1
6154 | Slave13 Inlet Phase3 Active Power | RO | 4 bytes | Unit:0.1
6156 | Slave14 Inlet Phase3 Active Power | RO | 4 bytes | Unit:0.1
6158 | Slave15 Inlet Phase3 Active Power | RO | 4 bytes | Unit:0.1
6160 | Master Inlet Phase1 Apparent Power | RO | 4 bytes | Unit:0.1
6162 | Slave01 Inlet Phase1 Apparent Power | RO | 4 bytes | Unit:0.1
6164 | Slave02 Inlet Phase1 Apparent Power | RO | 4 bytes | Unit:0.1
6166 | Slave03 Inlet Phase1 Apparent Power | RO | 4 bytes | Unit:0.1
6168 | Slave04 Inlet Phase1 Apparent Power | RO | 4 bytes | Unit:0.1
6170 | Slave05 Inlet Phase1 Apparent Power | RO | 4 bytes | Unit:0.1
6172 | Slave06 Inlet Phase1 Apparent Power | RO | 4 bytes | Unit:0.1
6174 | Slave07 Inlet Phase1 Apparent Power | RO | 4 bytes | Unit:0.1
6176 | Slave08 Inlet Phase1 Apparent Power | RO | 4 bytes | Unit:0.1
6178 | Slave09 Inlet Phase1 Apparent Power | RO | 4 bytes | Unit:0.1
6180 | Slave10 Inlet Phase1 Apparent Power | RO | 4 bytes | Unit:0.1
6182 | Slave11 Inlet Phase1 Apparent Power | RO | 4 bytes | Unit:0.1
6184 | Slave12 Inlet Phase1 Apparent Power | RO | 4 bytes | Unit:0.1
6186 | Slave13 Inlet Phase1 Apparent Power | RO | 4 bytes | Unit:0.1
6188 | Slave14 Inlet Phase1 Apparent Power | RO | 4 bytes | Unit:0.1
6190 | Slave15 Inlet Phase1 Apparent Power | RO | 4 bytes | Unit:0.1
6192 | Master Inlet Phase2 Apparent Power | RO | 4 bytes | Unit:0.1
6194 | Slave01 Inlet Phase2 Apparent Power | RO | 4 bytes | Unit:0.1
6196 | Slave02 Inlet Phase2 Apparent Power | RO | 4 bytes | Unit:0.1
6198 | Slave03 Inlet Phase2 Apparent Power | RO | 4 bytes | Unit:0.1
6200 | Slave04 Inlet Phase2 Apparent Power | RO | 4 bytes | Unit:0.1
6202 | Slave05 Inlet Phase2 Apparent Power | RO | 4 bytes | Unit:0.1
6204 | Slave06 Inlet Phase2 Apparent Power | RO | 4 bytes | Unit:0.1
6206 | Slave07 Inlet Phase2 Apparent Power | RO | 4 bytes | Unit:0.1
6208 | Slave08 Inlet Phase2 Apparent Power | RO | 4 bytes | Unit:0.1
6210 | Slave09 Inlet Phase2 Apparent Power | RO | 4 bytes | Unit:0.1
6212 | Slave10 Inlet Phase2 Apparent Power | RO | 4 bytes | Unit:0.1
6214 | Slave11 Inlet Phase2 Apparent Power | RO | 4 bytes | Unit:0.1
6216 | Slave12 Inlet Phase2 Apparent Power | RO | 4 bytes | Unit:0.1
6218 | Slave13 Inlet Phase2 Apparent Power | RO | 4 bytes | Unit:0.1
6220 | Slave14 Inlet Phase2 Apparent Power | RO | 4 bytes | Unit:0.1
6222 | Slave15 Inlet Phase2 Apparent Power | RO | 4 bytes | Unit:0.1
6224 | Master Inlet Phase3 Apparent Power | RO | 4 bytes | Unit:0.1
6226 | Slave01 Inlet Phase3 Apparent Power | RO | 4 bytes | Unit:0.1
6228 | Slave02 Inlet Phase3 Apparent Power | RO | 4 bytes | Unit:0.1
6230 | Slave03 Inlet Phase3 Apparent Power | RO | 4 bytes | Unit:0.1
6232 | Slave04 Inlet Phase3 Apparent Power | RO | 4 bytes | Unit:0.1
6234 | Slave05 Inlet Phase3 Apparent Power | RO | 4 bytes | Unit:0.1
6236 | Slave06 Inlet Phase3 Apparent Power | RO | 4 bytes | Unit:0.1
6238 | Slave07 Inlet Phase3 Apparent Power | RO | 4 bytes | Unit:0.1
6240 | Slave08 Inlet Phase3 Apparent Power | RO | 4 bytes | Unit:0.1
6242 | Slave09 Inlet Phase3 Apparent Power | RO | 4 bytes | Unit:0.1
6244 | Slave10 Inlet Phase3 Apparent Power | RO | 4 bytes | Unit:0.1
6246 | Slave11 Inlet Phase3 Apparent Power | RO | 4 bytes | Unit:0.1
6248 | Slave12 Inlet Phase3 Apparent Power | RO | 4 bytes | Unit:0.1
6250 | Slave13 Inlet Phase3 Apparent Power | RO | 4 bytes | Unit:0.1
6252 | Slave14 Inlet Phase3 Apparent Power | RO | 4 bytes | Unit:0.1
6254 | Slave15 Inlet Phase3 Apparent Power | RO | 4 bytes | Unit:0.1
6256 | Master Inlet Phase1 Reactive Power | RO | 4 bytes | Unit:0.1
6258 | Slave01 Inlet Phase1 Reactive Power | RO | 4 bytes | Unit:0.1
6260 | Slave02 Inlet Phase1 Reactive Power | RO | 4 bytes | Unit:0.1
6262 | Slave03 Inlet Phase1 Reactive Power | RO | 4 bytes | Unit:0.1
6264 | Slave04 Inlet Phase1 Reactive Power | RO | 4 bytes | Unit:0.1
6266 | Slave05 Inlet Phase1 Reactive Power | RO | 4 bytes | Unit:0.1
6268 | Slave06 Inlet Phase1 Reactive Power | RO | 4 bytes | Unit:0.1
6270 | Slave07 Inlet Phase1 Reactive Power | RO | 4 bytes | Unit:0.1
6272 | Slave08 Inlet Phase1 Reactive Power | RO | 4 bytes | Unit:0.1
6274 | Slave09 Inlet Phase1 Reactive Power | RO | 4 bytes | Unit:0.1
6276 | Slave10 Inlet Phase1 Reactive Power | RO | 4 bytes | Unit:0.1
6278 | Slave11 Inlet Phase1 Reactive Power | RO | 4 bytes | Unit:0.1
6280 | Slave12 Inlet Phase1 Reactive Power | RO | 4 bytes | Unit:0.1
6282 | Slave13 Inlet Phase1 Reactive Power | RO | 4 bytes | Unit:0.1
6284 | Slave14 Inlet Phase1 Reactive Power | RO | 4 bytes | Unit:0.1
6286 | Slave15 Inlet Phase1 Reactive Power | RO | 4 bytes | Unit:0.1
6288 | Master Inlet Phase2 Reactive Power | RO | 4 bytes | Unit:0.1
6290 | Slave01 Inlet Phase2 Reactive Power | RO | 4 bytes | Unit:0.1
6292 | Slave02 Inlet Phase2 Reactive Power | RO | 4 bytes | Unit:0.1
6294 | Slave03 Inlet Phase2 Reactive Power | RO | 4 bytes | Unit:0.1
6296 | Slave04 Inlet Phase2 Reactive Power | RO | 4 bytes | Unit:0.1
6298 | Slave05 Inlet Phase2 Reactive Power | RO | 4 bytes | Unit:0.1
6300 | Slave06 Inlet Phase2 Reactive Power | RO | 4 bytes | Unit:0.1
6302 | Slave07 Inlet Phase2 Reactive Power | RO | 4 bytes | Unit:0.1
6304 | Slave08 Inlet Phase2 Reactive Power | RO | 4 bytes | Unit:0.1
6306 | Slave09 Inlet Phase2 Reactive Power | RO | 4 bytes | Unit:0.1
6308 | Slave10 Inlet Phase2 Reactive Power | RO | 4 bytes | Unit:0.1
6310 | Slave11 Inlet Phase2 Reactive Power | RO | 4 bytes | Unit:0.1
6312 | Slave12 Inlet Phase2 Reactive Power | RO | 4 bytes | Unit:0.1
6314 | Slave13 Inlet Phase2 Reactive Power | RO | 4 bytes | Unit:0.1
6316 | Slave14 Inlet Phase2 Reactive Power | RO | 4 bytes | Unit:0.1
6318 | Slave15 Inlet Phase2 Reactive Power | RO | 4 bytes | Unit:0.1
6320 | Master Inlet Phase3 Reactive Power | RO | 4 bytes | Unit:0.1
6322 | Slave01 Inlet Phase3 Reactive Power | RO | 4 bytes | Unit:0.1
6324 | Slave02 Inlet Phase3 Reactive Power | RO | 4 bytes | Unit:0.1
6326 | Slave03 Inlet Phase3 Reactive Power | RO | 4 bytes | Unit:0.1
6328 | Slave04 Inlet Phase3 Reactive Power | RO | 4 bytes | Unit:0.1
6330 | Slave05 Inlet Phase3 Reactive Power | RO | 4 bytes | Unit:0.1
6332 | Slave06 Inlet Phase3 Reactive Power | RO | 4 bytes | Unit:0.1
6334 | Slave07 Inlet Phase3 Reactive Power | RO | 4 bytes | Unit:0.1
6336 | Slave08 Inlet Phase3 Reactive Power | RO | 4 bytes | Unit:0.1
6338 | Slave09 Inlet Phase3 Reactive Power | RO | 4 bytes | Unit:0.1
6340 | Slave10 Inlet Phase3 Reactive Power | RO | 4 bytes | Unit:0.1
6342 | Slave11 Inlet Phase3 Reactive Power | RO | 4 bytes | Unit:0.1
6344 | Slave12 Inlet Phase3 Reactive Power | RO | 4 bytes | Unit:0.1
6346 | Slave13 Inlet Phase3 Reactive Power | RO | 4 bytes | Unit:0.1
6348 | Slave14 Inlet Phase3 Reactive Power | RO | 4 bytes | Unit:0.1
6350 | Slave15 Inlet Phase3 Reactive Power | RO | 4 bytes | Unit:0.1
6352 | Master Inlet Phase1 Energy | RO | 4 bytes | Unit:0.001KW
6354 | Slave01 Inlet Phase1 Energy | RO | 4 bytes | Unit:0.001KW
6356 | Slave02 Inlet Phase1 Energy | RO | 4 bytes | Unit:0.001KW
6358 | Slave03 Inlet Phase1 Energy | RO | 4 bytes | Unit:0.001KW
6360 | Slave04 Inlet Phase1 Energy | RO | 4 bytes | Unit:0.001KW
6362 | Slave05 Inlet Phase1 Energy | RO | 4 bytes | Unit:0.001KW
6364 | Slave06 Inlet Phase1 Energy | RO | 4 bytes | Unit:0.001KW
6366 | Slave07 Inlet Phase1 Energy | RO | 4 bytes | Unit:0.001KW
6368 | Slave08 Inlet Phase1 Energy | RO | 4 bytes | Unit:0.001KW
6370 | Slave09 Inlet Phase1 Energy | RO | 4 bytes | Unit:0.001KW
6372 | Slave10 Inlet Phase1 Energy | RO | 4 bytes | Unit:0.001KW
6374 | Slave11 Inlet Phase1 Energy | RO | 4 bytes | Unit:0.001KW
6376 | Slave12 Inlet Phase1 Energy | RO | 4 bytes | Unit:0.001KW
6378 | Slave13 Inlet Phase1 Energy | RO | 4 bytes | Unit:0.001KW
6380 | Slave14 Inlet Phase1 Energy | RO | 4 bytes | Unit:0.001KW
6382 | Slave15 Inlet Phase1 Energy | RO | 4 bytes | Unit:0.001KW
6384 | Master Inlet Phase2 Energy | RO | 4 bytes | Unit:0.001KW
6386 | Slave01 Inlet Phase2 Energy | RO | 4 bytes | Unit:0.001KW
6388 | Slave02 Inlet Phase2 Energy | RO | 4 bytes | Unit:0.001KW
6390 | Slave03 Inlet Phase2 Energy | RO | 4 bytes | Unit:0.001KW
6392 | Slave04 Inlet Phase2 Energy | RO | 4 bytes | Unit:0.001KW
6394 | Slave05 Inlet Phase2 Energy | RO | 4 bytes | Unit:0.001KW
6396 | Slave06 Inlet Phase2 Energy | RO | 4 bytes | Unit:0.001KW
6398 | Slave07 Inlet Phase2 Energy | RO | 4 bytes | Unit:0.001KW
6400 | Slave08 Inlet Phase2 Energy | RO | 4 bytes | Unit:0.001KW
6402 | Slave09 Inlet Phase2 Energy | RO | 4 bytes | Unit:0.001KW
6404 | Slave10 Inlet Phase2 Energy | RO | 4 bytes | Unit:0.001KW
6406 | Slave11 Inlet Phase2 Energy | RO | 4 bytes | Unit:0.001KW
6408 | Slave12 Inlet Phase2 Energy | RO | 4 bytes | Unit:0.001KW
6410 | Slave13 Inlet Phase2 Energy | RO | 4 bytes | Unit:0.001KW
6412 | Slave14 Inlet Phase2 Energy | RO | 4 bytes | Unit:0.001KW
6414 | Slave15 Inlet Phase2 Energy | RO | 4 bytes | Unit:0.001KW
6416 | Master Inlet Phase3 Energy | RO | 4 bytes | Unit:0.001KW
6418 | Slave01 Inlet Phase3 Energy | RO | 4 bytes | Unit:0.001KW
6420 | Slave02 Inlet Phase3 Energy | RO | 4 bytes | Unit:0.001KW
6422 | Slave03 Inlet Phase3 Energy | RO | 4 bytes | Unit:0.001KW
6424 | Slave04 Inlet Phase3 Energy | RO | 4 bytes | Unit:0.001KW
6426 | Slave05 Inlet Phase3 Energy | RO | 4 bytes | Unit:0.001KW
6428 | Slave06 Inlet Phase3 Energy | RO | 4 bytes | Unit:0.001KW
6430 | Slave07 Inlet Phase3 Energy | RO | 4 bytes | Unit:0.001KW
6432 | Slave08 Inlet Phase3 Energy | RO | 4 bytes | Unit:0.001KW
6434 | Slave09 Inlet Phase3 Energy | RO | 4 bytes | Unit:0.001KW
6436 | Slave10 Inlet Phase3 Energy | RO | 4 bytes | Unit:0.001KW
6438 | Slave11 Inlet Phase3 Energy | RO | 4 bytes | Unit:0.001KW
6440 | Slave12 Inlet Phase3 Energy | RO | 4 bytes | Unit:0.001KW
6442 | Slave13 Inlet Phase3 Energy | RO | 4 bytes | Unit:0.001KW
6444 | Slave14 Inlet Phase3 Energy | RO | 4 bytes | Unit:0.001KW
6446 | Slave15 Inlet Phase3 Energy | RO | 4 bytes | Unit:0.001KW
6448 | Master Inlet Total Energy | RO | 4 bytes | Unit:0.001KW
6450 | Slave01 Inlet Total Energy | RO | 4 bytes | Unit:0.001KW
6452 | Slave02 Inlet Total Energy | RO | 4 bytes | Unit:0.001KW
6454 | Slave03 Inlet Total Energy | RO | 4 bytes | Unit:0.001KW
6456 | Slave04 Inlet Total Energy | RO | 4 bytes | Unit:0.001KW
6458 | Slave05 Inlet Total Energy | RO | 4 bytes | Unit:0.001KW
6460 | Slave06 Inlet Total Energy | RO | 4 bytes | Unit:0.001KW
6462 | Slave07 Inlet Total Energy | RO | 4 bytes | Unit:0.001KW
6464 | Slave08 Inlet Total Energy | RO | 4 bytes | Unit:0.001KW
6466 | Slave09 Inlet Total Energy | RO | 4 bytes | Unit:0.001KW
6468 | Slave10 Inlet Total Energy | RO | 4 bytes | Unit:0.001KW
6470 | Slave11 Inlet Total Energy | RO | 4 bytes | Unit:0.001KW
6472 | Slave12 Inlet Total Energy | RO | 4 bytes | Unit:0.001KW
6474 | Slave13 Inlet Total Energy | RO | 4 bytes | Unit:0.001KW
6476 | Slave14 Inlet Total Energy | RO | 4 bytes | Unit:0.001KW
6478 | Slave15 Inlet Total Energy | RO | 4 bytes | Unit:0.001KW
6480 | Master Inlet Load Balance | RO | 4 bytes | Unit:1
6482 | Slave01 Inlet Load Balance | RO | 4 bytes | Unit:1
6484 | Slave02 Inlet Load Balance | RO | 4 bytes | Unit:1
6486 | Slave03 Inlet Load Balance | RO | 4 bytes | Unit:1
6488 | Slave04 Inlet Load Balance | RO | 4 bytes | Unit:1
6490 | Slave05 Inlet Load Balance | RO | 4 bytes | Unit:1
6492 | Slave06 Inlet Load Balance | RO | 4 bytes | Unit:1
6494 | Slave07 Inlet Load Balance | RO | 4 bytes | Unit:1
6496 | Slave08 Inlet Load Balance | RO | 4 bytes | Unit:1
6498 | Slave09 Inlet Load Balance | RO | 4 bytes | Unit:1
6500 | Slave10 Inlet Load Balance | RO | 4 bytes | Unit:1
6502 | Slave11 Inlet Load Balance | RO | 4 bytes | Unit:1
6504 | Slave12 Inlet Load Balance | RO | 4 bytes | Unit:1
6506 | Slave13 Inlet Load Balance | RO | 4 bytes | Unit:1
6508 | Slave14 Inlet Load Balance | RO | 4 bytes | Unit:1
6510 | Slave15 Inlet Load Balance | RO | 4 bytes | Unit:1
6512 | Master Outlet Port01 Active Power | RO | 4 bytes | Unit:0.1
6514 | Master Outlet Port02 Active Power | RO | 4 bytes | Unit:0.1
6516 | Master Outlet Port03 Active Power | RO | 4 bytes | Unit:0.1
6518 | Master Outlet Port04 Active Power | RO | 4 bytes | Unit:0.1
6520 | Master Outlet Port05 Active Power | RO | 4 bytes | Unit:0.1
6522 | Master Outlet Port06 Active Power | RO | 4 bytes | Unit:0.1
6524 | Master Outlet Port07 Active Power | RO | 4 bytes | Unit:0.1
6526 | Master Outlet Port08 Active Power | RO | 4 bytes | Unit:0.1
6528 | Master Outlet Port09 Active Power | RO | 4 bytes | Unit:0.1
6530 | Master Outlet Port10 Active Power | RO | 4 bytes | Unit:0.1
6532 | Master Outlet Port11 Active Power | RO | 4 bytes | Unit:0.1
6534 | Master Outlet Port12 Active Power | RO | 4 bytes | Unit:0.1
6536 | Master Outlet Port13 Active Power | RO | 4 bytes | Unit:0.1
6538 | Master Outlet Port14 Active Power | RO | 4 bytes | Unit:0.1
6540 | Master Outlet Port15 Active Power | RO | 4 bytes | Unit:0.1
6542 | Master Outlet Port16 Active Power | RO | 4 bytes | Unit:0.1
6544 | Master Outlet Port17 Active Power | RO | 4 bytes | Unit:0.1
6546 | Master Outlet Port18 Active Power | RO | 4 bytes | Unit:0.1
6548 | Master Outlet Port19 Active Power | RO | 4 bytes | Unit:0.1
6550 | Master Outlet Port20 Active Power | RO | 4 bytes | Unit:0.1
6552 | Master Outlet Port21 Active Power | RO | 4 bytes | Unit:0.1
6554 | Master Outlet Port22 Active Power | RO | 4 bytes | Unit:0.1
6556 | Master Outlet Port23 Active Power | RO | 4 bytes | Unit:0.1
6558 | Master Outlet Port24 Active Power | RO | 4 bytes | Unit:0.1
6560 | Master Outlet Port25 Active Power | RO | 4 bytes | Unit:0.1
6562 | Master Outlet Port26 Active Power | RO | 4 bytes | Unit:0.1
6564 | Master Outlet Port27 Active Power | RO | 4 bytes | Unit:0.1
6566 | Master Outlet Port28 Active Power | RO | 4 bytes | Unit:0.1
6568 | Master Outlet Port29 Active Power | RO | 4 bytes | Unit:0.1
6570 | Master Outlet Port30 Active Power | RO | 4 bytes | Unit:0.1
6572 | Master Outlet Port31 Active Power | RO | 4 bytes | Unit:0.1
6574 | Master Outlet Port32 Active Power | RO | 4 bytes | Unit:0.1
6576 | Master Outlet Port33 Active Power | RO | 4 bytes | Unit:0.1
6578 | Master Outlet Port34 Active Power | RO | 4 bytes | Unit:0.1
6580 | Master Outlet Port35 Active Power | RO | 4 bytes | Unit:0.1
6582 | Master Outlet Port36 Active Power | RO | 4 bytes | Unit:0.1
6584 | Master Outlet Port37 Active Power | RO | 4 bytes | Unit:0.1
6586 | Master Outlet Port38 Active Power | RO | 4 bytes | Unit:0.1
6588 | Master Outlet Port39 Active Power | RO | 4 bytes | Unit:0.1
6590 | Master Outlet Port40 Active Power | RO | 4 bytes | Unit:0.1
6592 | Master Outlet Port41 Active Power | RO | 4 bytes | Unit:0.1
6594 | Master Outlet Port42 Active Power | RO | 4 bytes | Unit:0.1
6596 | Slave01 Outlet Port01 Active Power | RO | 4 bytes | Unit:0.1
6598 | Slave01 Outlet Port02 Active Power | RO | 4 bytes | Unit:0.1
6600 | Slave01 Outlet Port03 Active Power | RO | 4 bytes | Unit:0.1
6602 | Slave01 Outlet Port04 Active Power | RO | 4 bytes | Unit:0.1
6604 | Slave01 Outlet Port05 Active Power | RO | 4 bytes | Unit:0.1
6606 | Slave01 Outlet Port06 Active Power | RO | 4 bytes | Unit:0.1
6608 | Slave01 Outlet Port07 Active Power | RO | 4 bytes | Unit:0.1
6610 | Slave01 Outlet Port08 Active Power | RO | 4 bytes | Unit:0.1
6612 | Slave01 Outlet Port09 Active Power | RO | 4 bytes | Unit:0.1
6614 | Slave01 Outlet Port10 Active Power | RO | 4 bytes | Unit:0.1
6616 | Slave01 Outlet Port11 Active Power | RO | 4 bytes | Unit:0.1
6618 | Slave01 Outlet Port12 Active Power | RO | 4 bytes | Unit:0.1
6620 | Slave01 Outlet Port13 Active Power | RO | 4 bytes | Unit:0.1
6622 | Slave01 Outlet Port14 Active Power | RO | 4 bytes | Unit:0.1
6624 | Slave01 Outlet Port15 Active Power | RO | 4 bytes | Unit:0.1
6626 | Slave01 Outlet Port16 Active Power | RO | 4 bytes | Unit:0.1
6628 | Slave01 Outlet Port17 Active Power | RO | 4 bytes | Unit:0.1
6630 | Slave01 Outlet Port18 Active Power | RO | 4 bytes | Unit:0.1
6632 | Slave01 Outlet Port19 Active Power | RO | 4 bytes | Unit:0.1
6634 | Slave01 Outlet Port20 Active Power | RO | 4 bytes | Unit:0.1
6636 | Slave01 Outlet Port21 Active Power | RO | 4 bytes | Unit:0.1
6638 | Slave01 Outlet Port22 Active Power | RO | 4 bytes | Unit:0.1
6640 | Slave01 Outlet Port23 Active Power | RO | 4 bytes | Unit:0.1
6642 | Slave01 Outlet Port24 Active Power | RO | 4 bytes | Unit:0.1
6644 | Slave01 Outlet Port25 Active Power | RO | 4 bytes | Unit:0.1
6646 | Slave01 Outlet Port26 Active Power | RO | 4 bytes | Unit:0.1
6648 | Slave01 Outlet Port27 Active Power | RO | 4 bytes | Unit:0.1
6650 | Slave01 Outlet Port28 Active Power | RO | 4 bytes | Unit:0.1
6652 | Slave01 Outlet Port29 Active Power | RO | 4 bytes | Unit:0.1
6654 | Slave01 Outlet Port30 Active Power | RO | 4 bytes | Unit:0.1
6656 | Slave01 Outlet Port31 Active Power | RO | 4 bytes | Unit:0.1
6658 | Slave01 Outlet Port32 Active Power | RO | 4 bytes | Unit:0.1
6660 | Slave01 Outlet Port33 Active Power | RO | 4 bytes | Unit:0.1
6662 | Slave01 Outlet Port34 Active Power | RO | 4 bytes | Unit:0.1
6664 | Slave01 Outlet Port35 Active Power | RO | 4 bytes | Unit:0.1
6666 | Slave01 Outlet Port36 Active Power | RO | 4 bytes | Unit:0.1
6668 | Slave01 Outlet Port37 Active Power | RO | 4 bytes | Unit:0.1
6670 | Slave01 Outlet Port38 Active Power | RO | 4 bytes | Unit:0.1
6672 | Slave01 Outlet Port39 Active Power | RO | 4 bytes | Unit:0.1
6674 | Slave01 Outlet Port40 Active Power | RO | 4 bytes | Unit:0.1
6676 | Slave01 Outlet Port41 Active Power | RO | 4 bytes | Unit:0.1
6678 | Slave01 Outlet Port42 Active Power | RO | 4 bytes | Unit:0.1
6680 | Slave02 Outlet Port01 Active Power | RO | 4 bytes | Unit:0.1
6682 | Slave02 Outlet Port02 Active Power | RO | 4 bytes | Unit:0.1
6684 | Slave02 Outlet Port03 Active Power | RO | 4 bytes | Unit:0.1
6686 | Slave02 Outlet Port04 Active Power | RO | 4 bytes | Unit:0.1
6688 | Slave02 Outlet Port05 Active Power | RO | 4 bytes | Unit:0.1
6690 | Slave02 Outlet Port06 Active Power | RO | 4 bytes | Unit:0.1
6692 | Slave02 Outlet Port07 Active Power | RO | 4 bytes | Unit:0.1
6694 | Slave02 Outlet Port08 Active Power | RO | 4 bytes | Unit:0.1
6696 | Slave02 Outlet Port09 Active Power | RO | 4 bytes | Unit:0.1
6698 | Slave02 Outlet Port10 Active Power | RO | 4 bytes | Unit:0.1
6700 | Slave02 Outlet Port11 Active Power | RO | 4 bytes | Unit:0.1
6702 | Slave02 Outlet Port12 Active Power | RO | 4 bytes | Unit:0.1
6704 | Slave02 Outlet Port13 Active Power | RO | 4 bytes | Unit:0.1
6706 | Slave02 Outlet Port14 Active Power | RO | 4 bytes | Unit:0.1
6708 | Slave02 Outlet Port15 Active Power | RO | 4 bytes | Unit:0.1
6710 | Slave02 Outlet Port16 Active Power | RO | 4 bytes | Unit:0.1
6712 | Slave02 Outlet Port17 Active Power | RO | 4 bytes | Unit:0.1
6714 | Slave02 Outlet Port18 Active Power | RO | 4 bytes | Unit:0.1
6716 | Slave02 Outlet Port19 Active Power | RO | 4 bytes | Unit:0.1
6718 | Slave02 Outlet Port20 Active Power | RO | 4 bytes | Unit:0.1
6720 | Slave02 Outlet Port21 Active Power | RO | 4 bytes | Unit:0.1
6722 | Slave02 Outlet Port22 Active Power | RO | 4 bytes | Unit:0.1
6724 | Slave02 Outlet Port23 Active Power | RO | 4 bytes | Unit:0.1
6726 | Slave02 Outlet Port24 Active Power | RO | 4 bytes | Unit:0.1
6728 | Slave02 Outlet Port25 Active Power | RO | 4 bytes | Unit:0.1
6730 | Slave02 Outlet Port26 Active Power | RO | 4 bytes | Unit:0.1
6732 | Slave02 Outlet Port27 Active Power | RO | 4 bytes | Unit:0.1
6734 | Slave02 Outlet Port28 Active Power | RO | 4 bytes | Unit:0.1
6736 | Slave02 Outlet Port29 Active Power | RO | 4 bytes | Unit:0.1
6738 | Slave02 Outlet Port30 Active Power | RO | 4 bytes | Unit:0.1
6740 | Slave02 Outlet Port31 Active Power | RO | 4 bytes | Unit:0.1
6742 | Slave02 Outlet Port32 Active Power | RO | 4 bytes | Unit:0.1
6744 | Slave02 Outlet Port33 Active Power | RO | 4 bytes | Unit:0.1
6746 | Slave02 Outlet Port34 Active Power | RO | 4 bytes | Unit:0.1
6748 | Slave02 Outlet Port35 Active Power | RO | 4 bytes | Unit:0.1
6750 | Slave02 Outlet Port36 Active Power | RO | 4 bytes | Unit:0.1
6752 | Slave02 Outlet Port37 Active Power | RO | 4 bytes | Unit:0.1
6754 | Slave02 Outlet Port38 Active Power | RO | 4 bytes | Unit:0.1
6756 | Slave02 Outlet Port39 Active Power | RO | 4 bytes | Unit:0.1
6758 | Slave02 Outlet Port40 Active Power | RO | 4 bytes | Unit:0.1
6760 | Slave02 Outlet Port41 Active Power | RO | 4 bytes | Unit:0.1
6762 | Slave02 Outlet Port42 Active Power | RO | 4 bytes | Unit:0.1
6764 | Slave03 Outlet Port01 Active Power | RO | 4 bytes | Unit:0.1
6766 | Slave03 Outlet Port02 Active Power | RO | 4 bytes | Unit:0.1
6768 | Slave03 Outlet Port03 Active Power | RO | 4 bytes | Unit:0.1
6770 | Slave03 Outlet Port04 Active Power | RO | 4 bytes | Unit:0.1
6772 | Slave03 Outlet Port05 Active Power | RO | 4 bytes | Unit:0.1
6774 | Slave03 Outlet Port06 Active Power | RO | 4 bytes | Unit:0.1
6776 | Slave03 Outlet Port07 Active Power | RO | 4 bytes | Unit:0.1
6778 | Slave03 Outlet Port08 Active Power | RO | 4 bytes | Unit:0.1
6780 | Slave03 Outlet Port09 Active Power | RO | 4 bytes | Unit:0.1
6782 | Slave03 Outlet Port10 Active Power | RO | 4 bytes | Unit:0.1
6784 | Slave03 Outlet Port11 Active Power | RO | 4 bytes | Unit:0.1
6786 | Slave03 Outlet Port12 Active Power | RO | 4 bytes | Unit:0.1
6788 | Slave03 Outlet Port13 Active Power | RO | 4 bytes | Unit:0.1
6790 | Slave03 Outlet Port14 Active Power | RO | 4 bytes | Unit:0.1
6792 | Slave03 Outlet Port15 Active Power | RO | 4 bytes | Unit:0.1
6794 | Slave03 Outlet Port16 Active Power | RO | 4 bytes | Unit:0.1
6796 | Slave03 Outlet Port17 Active Power | RO | 4 bytes | Unit:0.1
6798 | Slave03 Outlet Port18 Active Power | RO | 4 bytes | Unit:0.1
6800 | Slave03 Outlet Port19 Active Power | RO | 4 bytes | Unit:0.1
6802 | Slave03 Outlet Port20 Active Power | RO | 4 bytes | Unit:0.1
6804 | Slave03 Outlet Port21 Active Power | RO | 4 bytes | Unit:0.1
6806 | Slave03 Outlet Port22 Active Power | RO | 4 bytes | Unit:0.1
6808 | Slave03 Outlet Port23 Active Power | RO | 4 bytes | Unit:0.1
6810 | Slave03 Outlet Port24 Active Power | RO | 4 bytes | Unit:0.1
6812 | Slave03 Outlet Port25 Active Power | RO | 4 bytes | Unit:0.1
6814 | Slave03 Outlet Port26 Active Power | RO | 4 bytes | Unit:0.1
6816 | Slave03 Outlet Port27 Active Power | RO | 4 bytes | Unit:0.1
6818 | Slave03 Outlet Port28 Active Power | RO | 4 bytes | Unit:0.1
6820 | Slave03 Outlet Port29 Active Power | RO | 4 bytes | Unit:0.1
6822 | Slave03 Outlet Port30 Active Power | RO | 4 bytes | Unit:0.1
6824 | Slave03 Outlet Port31 Active Power | RO | 4 bytes | Unit:0.1
6826 | Slave03 Outlet Port32 Active Power | RO | 4 bytes | Unit:0.1
6828 | Slave03 Outlet Port33 Active Power | RO | 4 bytes | Unit:0.1
6830 | Slave03 Outlet Port34 Active Power | RO | 4 bytes | Unit:0.1
6832 | Slave03 Outlet Port35 Active Power | RO | 4 bytes | Unit:0.1
6834 | Slave03 Outlet Port36 Active Power | RO | 4 bytes | Unit:0.1
6836 | Slave03 Outlet Port37 Active Power | RO | 4 bytes | Unit:0.1
6838 | Slave03 Outlet Port38 Active Power | RO | 4 bytes | Unit:0.1
6840 | Slave03 Outlet Port39 Active Power | RO | 4 bytes | Unit:0.1
6842 | Slave03 Outlet Port40 Active Power | RO | 4 bytes | Unit:0.1
6844 | Slave03 Outlet Port41 Active Power | RO | 4 bytes | Unit:0.1
6846 | Slave03 Outlet Port42 Active Power | RO | 4 bytes | Unit:0.1
6848 | Slave04 Outlet Port01 Active Power | RO | 4 bytes | Unit:0.1
6850 | Slave04 Outlet Port02 Active Power | RO | 4 bytes | Unit:0.1
6852 | Slave04 Outlet Port03 Active Power | RO | 4 bytes | Unit:0.1
6854 | Slave04 Outlet Port04 Active Power | RO | 4 bytes | Unit:0.1
6856 | Slave04 Outlet Port05 Active Power | RO | 4 bytes | Unit:0.1
6858 | Slave04 Outlet Port06 Active Power | RO | 4 bytes | Unit:0.1
6860 | Slave04 Outlet Port07 Active Power | RO | 4 bytes | Unit:0.1
6862 | Slave04 Outlet Port08 Active Power | RO | 4 bytes | Unit:0.1
6864 | Slave04 Outlet Port09 Active Power | RO | 4 bytes | Unit:0.1
6866 | Slave04 Outlet Port10 Active Power | RO | 4 bytes | Unit:0.1
6868 | Slave04 Outlet Port11 Active Power | RO | 4 bytes | Unit:0.1
6870 | Slave04 Outlet Port12 Active Power | RO | 4 bytes | Unit:0.1
6872 | Slave04 Outlet Port13 Active Power | RO | 4 bytes | Unit:0.1
6874 | Slave04 Outlet Port14 Active Power | RO | 4 bytes | Unit:0.1
6876 | Slave04 Outlet Port15 Active Power | RO | 4 bytes | Unit:0.1
6878 | Slave04 Outlet Port16 Active Power | RO | 4 bytes | Unit:0.1
6880 | Slave04 Outlet Port17 Active Power | RO | 4 bytes | Unit:0.1
6882 | Slave04 Outlet Port18 Active Power | RO | 4 bytes | Unit:0.1
6884 | Slave04 Outlet Port19 Active Power | RO | 4 bytes | Unit:0.1
6886 | Slave04 Outlet Port20 Active Power | RO | 4 bytes | Unit:0.1
6888 | Slave04 Outlet Port21 Active Power | RO | 4 bytes | Unit:0.1
6890 | Slave04 Outlet Port22 Active Power | RO | 4 bytes | Unit:0.1
6892 | Slave04 Outlet Port23 Active Power | RO | 4 bytes | Unit:0.1
6894 | Slave04 Outlet Port24 Active Power | RO | 4 bytes | Unit:0.1
6896 | Slave04 Outlet Port25 Active Power | RO | 4 bytes | Unit:0.1
6898 | Slave04 Outlet Port26 Active Power | RO | 4 bytes | Unit:0.1
6900 | Slave04 Outlet Port27 Active Power | RO | 4 bytes | Unit:0.1
6902 | Slave04 Outlet Port28 Active Power | RO | 4 bytes | Unit:0.1
6904 | Slave04 Outlet Port29 Active Power | RO | 4 bytes | Unit:0.1
6906 | Slave04 Outlet Port30 Active Power | RO | 4 bytes | Unit:0.1
6908 | Slave04 Outlet Port31 Active Power | RO | 4 bytes | Unit:0.1
6910 | Slave04 Outlet Port32 Active Power | RO | 4 bytes | Unit:0.1
6912 | Slave04 Outlet Port33 Active Power | RO | 4 bytes | Unit:0.1
6914 | Slave04 Outlet Port34 Active Power | RO | 4 bytes | Unit:0.1
6916 | Slave04 Outlet Port35 Active Power | RO | 4 bytes | Unit:0.1
6918 | Slave04 Outlet Port36 Active Power | RO | 4 bytes | Unit:0.1
6920 | Slave04 Outlet Port37 Active Power | RO | 4 bytes | Unit:0.1
6922 | Slave04 Outlet Port38 Active Power | RO | 4 bytes | Unit:0.1
6924 | Slave04 Outlet Port39 Active Power | RO | 4 bytes | Unit:0.1
6926 | Slave04 Outlet Port40 Active Power | RO | 4 bytes | Unit:0.1
6928 | Slave04 Outlet Port41 Active Power | RO | 4 bytes | Unit:0.1
6930 | Slave04 Outlet Port42 Active Power | RO | 4 bytes | Unit:0.1
6932 | Slave05 Outlet Port01 Active Power | RO | 4 bytes | Unit:0.1
6934 | Slave05 Outlet Port02 Active Power | RO | 4 bytes | Unit:0.1
6936 | Slave05 Outlet Port03 Active Power | RO | 4 bytes | Unit:0.1
6938 | Slave05 Outlet Port04 Active Power | RO | 4 bytes | Unit:0.1
6940 | Slave05 Outlet Port05 Active Power | RO | 4 bytes | Unit:0.1
6942 | Slave05 Outlet Port06 Active Power | RO | 4 bytes | Unit:0.1
6944 | Slave05 Outlet Port07 Active Power | RO | 4 bytes | Unit:0.1
6946 | Slave05 Outlet Port08 Active Power | RO | 4 bytes | Unit:0.1
6948 | Slave05 Outlet Port09 Active Power | RO | 4 bytes | Unit:0.1
6950 | Slave05 Outlet Port10 Active Power | RO | 4 bytes | Unit:0.1
6952 | Slave05 Outlet Port11 Active Power | RO | 4 bytes | Unit:0.1
6954 | Slave05 Outlet Port12 Active Power | RO | 4 bytes | Unit:0.1
6956 | Slave05 Outlet Port13 Active Power | RO | 4 bytes | Unit:0.1
6958 | Slave05 Outlet Port14 Active Power | RO | 4 bytes | Unit:0.1
6960 | Slave05 Outlet Port15 Active Power | RO | 4 bytes | Unit:0.1
6962 | Slave05 Outlet Port16 Active Power | RO | 4 bytes | Unit:0.1
6964 | Slave05 Outlet Port17 Active Power | RO | 4 bytes | Unit:0.1
6966 | Slave05 Outlet Port18 Active Power | RO | 4 bytes | Unit:0.1
6968 | Slave05 Outlet Port19 Active Power | RO | 4 bytes | Unit:0.1
6970 | Slave05 Outlet Port20 Active Power | RO | 4 bytes | Unit:0.1
6972 | Slave05 Outlet Port21 Active Power | RO | 4 bytes | Unit:0.1
6974 | Slave05 Outlet Port22 Active Power | RO | 4 bytes | Unit:0.1
6976 | Slave05 Outlet Port23 Active Power | RO | 4 bytes | Unit:0.1
6978 | Slave05 Outlet Port24 Active Power | RO | 4 bytes | Unit:0.1
6980 | Slave05 Outlet Port25 Active Power | RO | 4 bytes | Unit:0.1
6982 | Slave05 Outlet Port26 Active Power | RO | 4 bytes | Unit:0.1
6984 | Slave05 Outlet Port27 Active Power | RO | 4 bytes | Unit:0.1
6986 | Slave05 Outlet Port28 Active Power | RO | 4 bytes | Unit:0.1
6988 | Slave05 Outlet Port29 Active Power | RO | 4 bytes | Unit:0.1
6990 | Slave05 Outlet Port30 Active Power | RO | 4 bytes | Unit:0.1
6992 | Slave05 Outlet Port31 Active Power | RO | 4 bytes | Unit:0.1
6994 | Slave05 Outlet Port32 Active Power | RO | 4 bytes | Unit:0.1
6996 | Slave05 Outlet Port33 Active Power | RO | 4 bytes | Unit:0.1
6998 | Slave05 Outlet Port34 Active Power | RO | 4 bytes | Unit:0.1
7000 | Slave05 Outlet Port35 Active Power | RO | 4 bytes | Unit:0.1
7002 | Slave05 Outlet Port36 Active Power | RO | 4 bytes | Unit:0.1
7004 | Slave05 Outlet Port37 Active Power | RO | 4 bytes | Unit:0.1
7006 | Slave05 Outlet Port38 Active Power | RO | 4 bytes | Unit:0.1
7008 | Slave05 Outlet Port39 Active Power | RO | 4 bytes | Unit:0.1
7010 | Slave05 Outlet Port40 Active Power | RO | 4 bytes | Unit:0.1
7012 | Slave05 Outlet Port41 Active Power | RO | 4 bytes | Unit:0.1
7014 | Slave05 Outlet Port42 Active Power | RO | 4 bytes | Unit:0.1
7016 | Slave06 Outlet Port01 Active Power | RO | 4 bytes | Unit:0.1
7018 | Slave06 Outlet Port02 Active Power | RO | 4 bytes | Unit:0.1
7020 | Slave06 Outlet Port03 Active Power | RO | 4 bytes | Unit:0.1
7022 | Slave06 Outlet Port04 Active Power | RO | 4 bytes | Unit:0.1
7024 | Slave06 Outlet Port05 Active Power | RO | 4 bytes | Unit:0.1
7026 | Slave06 Outlet Port06 Active Power | RO | 4 bytes | Unit:0.1
7028 | Slave06 Outlet Port07 Active Power | RO | 4 bytes | Unit:0.1
7030 | Slave06 Outlet Port08 Active Power | RO | 4 bytes | Unit:0.1
7032 | Slave06 Outlet Port09 Active Power | RO | 4 bytes | Unit:0.1
7034 | Slave06 Outlet Port10 Active Power | RO | 4 bytes | Unit:0.1
7036 | Slave06 Outlet Port11 Active Power | RO | 4 bytes | Unit:0.1
7038 | Slave06 Outlet Port12 Active Power | RO | 4 bytes | Unit:0.1
7040 | Slave06 Outlet Port13 Active Power | RO | 4 bytes | Unit:0.1
7042 | Slave06 Outlet Port14 Active Power | RO | 4 bytes | Unit:0.1
7044 | Slave06 Outlet Port15 Active Power | RO | 4 bytes | Unit:0.1
7046 | Slave06 Outlet Port16 Active Power | RO | 4 bytes | Unit:0.1
7048 | Slave06 Outlet Port17 Active Power | RO | 4 bytes | Unit:0.1
7050 | Slave06 Outlet Port18 Active Power | RO | 4 bytes | Unit:0.1
7052 | Slave06 Outlet Port19 Active Power | RO | 4 bytes | Unit:0.1
7054 | Slave06 Outlet Port20 Active Power | RO | 4 bytes | Unit:0.1
7056 | Slave06 Outlet Port21 Active Power | RO | 4 bytes | Unit:0.1
7058 | Slave06 Outlet Port22 Active Power | RO | 4 bytes | Unit:0.1
7060 | Slave06 Outlet Port23 Active Power | RO | 4 bytes | Unit:0.1
7062 | Slave06 Outlet Port24 Active Power | RO | 4 bytes | Unit:0.1
7064 | Slave06 Outlet Port25 Active Power | RO | 4 bytes | Unit:0.1
7066 | Slave06 Outlet Port26 Active Power | RO | 4 bytes | Unit:0.1
7068 | Slave06 Outlet Port27 Active Power | RO | 4 bytes | Unit:0.1
7070 | Slave06 Outlet Port28 Active Power | RO | 4 bytes | Unit:0.1
7072 | Slave06 Outlet Port29 Active Power | RO | 4 bytes | Unit:0.1
7074 | Slave06 Outlet Port30 Active Power | RO | 4 bytes | Unit:0.1
7076 | Slave06 Outlet Port31 Active Power | RO | 4 bytes | Unit:0.1
7078 | Slave06 Outlet Port32 Active Power | RO | 4 bytes | Unit:0.1
7080 | Slave06 Outlet Port33 Active Power | RO | 4 bytes | Unit:0.1
7082 | Slave06 Outlet Port34 Active Power | RO | 4 bytes | Unit:0.1
7084 | Slave06 Outlet Port35 Active Power | RO | 4 bytes | Unit:0.1
7086 | Slave06 Outlet Port36 Active Power | RO | 4 bytes | Unit:0.1
7088 | Slave06 Outlet Port37 Active Power | RO | 4 bytes | Unit:0.1
7090 | Slave06 Outlet Port38 Active Power | RO | 4 bytes | Unit:0.1
7092 | Slave06 Outlet Port39 Active Power | RO | 4 bytes | Unit:0.1
7094 | Slave06 Outlet Port40 Active Power | RO | 4 bytes | Unit:0.1
7096 | Slave06 Outlet Port41 Active Power | RO | 4 bytes | Unit:0.1
7098 | Slave06 Outlet Port42 Active Power | RO | 4 bytes | Unit:0.1
7100 | Slave07 Outlet Port01 Active Power | RO | 4 bytes | Unit:0.1
7102 | Slave07 Outlet Port02 Active Power | RO | 4 bytes | Unit:0.1
7104 | Slave07 Outlet Port03 Active Power | RO | 4 bytes | Unit:0.1
7106 | Slave07 Outlet Port04 Active Power | RO | 4 bytes | Unit:0.1
7108 | Slave07 Outlet Port05 Active Power | RO | 4 bytes | Unit:0.1
7110 | Slave07 Outlet Port06 Active Power | RO | 4 bytes | Unit:0.1
7112 | Slave07 Outlet Port07 Active Power | RO | 4 bytes | Unit:0.1
7114 | Slave07 Outlet Port08 Active Power | RO | 4 bytes | Unit:0.1
7116 | Slave07 Outlet Port09 Active Power | RO | 4 bytes | Unit:0.1
7118 | Slave07 Outlet Port10 Active Power | RO | 4 bytes | Unit:0.1
7120 | Slave07 Outlet Port11 Active Power | RO | 4 bytes | Unit:0.1
7122 | Slave07 Outlet Port12 Active Power | RO | 4 bytes | Unit:0.1
7124 | Slave07 Outlet Port13 Active Power | RO | 4 bytes | Unit:0.1
7126 | Slave07 Outlet Port14 Active Power | RO | 4 bytes | Unit:0.1
7128 | Slave07 Outlet Port15 Active Power | RO | 4 bytes | Unit:0.1
7130 | Slave07 Outlet Port16 Active Power | RO | 4 bytes | Unit:0.1
7132 | Slave07 Outlet Port17 Active Power | RO | 4 bytes | Unit:0.1
7134 | Slave07 Outlet Port18 Active Power | RO | 4 bytes | Unit:0.1
7136 | Slave07 Outlet Port19 Active Power | RO | 4 bytes | Unit:0.1
7138 | Slave07 Outlet Port20 Active Power | RO | 4 bytes | Unit:0.1
7140 | Slave07 Outlet Port21 Active Power | RO | 4 bytes | Unit:0.1
7142 | Slave07 Outlet Port22 Active Power | RO | 4 bytes | Unit:0.1
7144 | Slave07 Outlet Port23 Active Power | RO | 4 bytes | Unit:0.1
7146 | Slave07 Outlet Port24 Active Power | RO | 4 bytes | Unit:0.1
7148 | Slave07 Outlet Port25 Active Power | RO | 4 bytes | Unit:0.1
7150 | Slave07 Outlet Port26 Active Power | RO | 4 bytes | Unit:0.1
7152 | Slave07 Outlet Port27 Active Power | RO | 4 bytes | Unit:0.1
7154 | Slave07 Outlet Port28 Active Power | RO | 4 bytes | Unit:0.1
7156 | Slave07 Outlet Port29 Active Power | RO | 4 bytes | Unit:0.1
7158 | Slave07 Outlet Port30 Active Power | RO | 4 bytes | Unit:0.1
7160 | Slave07 Outlet Port31 Active Power | RO | 4 bytes | Unit:0.1
7162 | Slave07 Outlet Port32 Active Power | RO | 4 bytes | Unit:0.1
7164 | Slave07 Outlet Port33 Active Power | RO | 4 bytes | Unit:0.1
7166 | Slave07 Outlet Port34 Active Power | RO | 4 bytes | Unit:0.1
7168 | Slave07 Outlet Port35 Active Power | RO | 4 bytes | Unit:0.1
7170 | Slave07 Outlet Port36 Active Power | RO | 4 bytes | Unit:0.1
7172 | Slave07 Outlet Port37 Active Power | RO | 4 bytes | Unit:0.1
7174 | Slave07 Outlet Port38 Active Power | RO | 4 bytes | Unit:0.1
7176 | Slave07 Outlet Port39 Active Power | RO | 4 bytes | Unit:0.1
7178 | Slave07 Outlet Port40 Active Power | RO | 4 bytes | Unit:0.1
7180 | Slave07 Outlet Port41 Active Power | RO | 4 bytes | Unit:0.1
7182 | Slave07 Outlet Port42 Active Power | RO | 4 bytes | Unit:0.1
7184 | Slave08 Outlet Port01 Active Power | RO | 4 bytes | Unit:0.1
7186 | Slave08 Outlet Port02 Active Power | RO | 4 bytes | Unit:0.1
7188 | Slave08 Outlet Port03 Active Power | RO | 4 bytes | Unit:0.1
7190 | Slave08 Outlet Port04 Active Power | RO | 4 bytes | Unit:0.1
7192 | Slave08 Outlet Port05 Active Power | RO | 4 bytes | Unit:0.1
7194 | Slave08 Outlet Port06 Active Power | RO | 4 bytes | Unit:0.1
7196 | Slave08 Outlet Port07 Active Power | RO | 4 bytes | Unit:0.1
7198 | Slave08 Outlet Port08 Active Power | RO | 4 bytes | Unit:0.1
7200 | Slave08 Outlet Port09 Active Power | RO | 4 bytes | Unit:0.1
7202 | Slave08 Outlet Port10 Active Power | RO | 4 bytes | Unit:0.1
7204 | Slave08 Outlet Port11 Active Power | RO | 4 bytes | Unit:0.1
7206 | Slave08 Outlet Port12 Active Power | RO | 4 bytes | Unit:0.1
7208 | Slave08 Outlet Port13 Active Power | RO | 4 bytes | Unit:0.1
7210 | Slave08 Outlet Port14 Active Power | RO | 4 bytes | Unit:0.1
7212 | Slave08 Outlet Port15 Active Power | RO | 4 bytes | Unit:0.1
7214 | Slave08 Outlet Port16 Active Power | RO | 4 bytes | Unit:0.1
7216 | Slave08 Outlet Port17 Active Power | RO | 4 bytes | Unit:0.1
7218 | Slave08 Outlet Port18 Active Power | RO | 4 bytes | Unit:0.1
7220 | Slave08 Outlet Port19 Active Power | RO | 4 bytes | Unit:0.1
7222 | Slave08 Outlet Port20 Active Power | RO | 4 bytes | Unit:0.1
7224 | Slave08 Outlet Port21 Active Power | RO | 4 bytes | Unit:0.1
7226 | Slave08 Outlet Port22 Active Power | RO | 4 bytes | Unit:0.1
7228 | Slave08 Outlet Port23 Active Power | RO | 4 bytes | Unit:0.1
7230 | Slave08 Outlet Port24 Active Power | RO | 4 bytes | Unit:0.1
7232 | Slave08 Outlet Port25 Active Power | RO | 4 bytes | Unit:0.1
7234 | Slave08 Outlet Port26 Active Power | RO | 4 bytes | Unit:0.1
7236 | Slave08 Outlet Port27 Active Power | RO | 4 bytes | Unit:0.1
7238 | Slave08 Outlet Port28 Active Power | RO | 4 bytes | Unit:0.1
7240 | Slave08 Outlet Port29 Active Power | RO | 4 bytes | Unit:0.1
7242 | Slave08 Outlet Port30 Active Power | RO | 4 bytes | Unit:0.1
7244 | Slave08 Outlet Port31 Active Power | RO | 4 bytes | Unit:0.1
7246 | Slave08 Outlet Port32 Active Power | RO | 4 bytes | Unit:0.1
7248 | Slave08 Outlet Port33 Active Power | RO | 4 bytes | Unit:0.1
7250 | Slave08 Outlet Port34 Active Power | RO | 4 bytes | Unit:0.1
7252 | Slave08 Outlet Port35 Active Power | RO | 4 bytes | Unit:0.1
7254 | Slave08 Outlet Port36 Active Power | RO | 4 bytes | Unit:0.1
7256 | Slave08 Outlet Port37 Active Power | RO | 4 bytes | Unit:0.1
7258 | Slave08 Outlet Port38 Active Power | RO | 4 bytes | Unit:0.1
7260 | Slave08 Outlet Port39 Active Power | RO | 4 bytes | Unit:0.1
7262 | Slave08 Outlet Port40 Active Power | RO | 4 bytes | Unit:0.1
7264 | Slave08 Outlet Port41 Active Power | RO | 4 bytes | Unit:0.1
7266 | Slave08 Outlet Port42 Active Power | RO | 4 bytes | Unit:0.1
7268 | Slave09 Outlet Port01 Active Power | RO | 4 bytes | Unit:0.1
7270 | Slave09 Outlet Port02 Active Power | RO | 4 bytes | Unit:0.1
7272 | Slave09 Outlet Port03 Active Power | RO | 4 bytes | Unit:0.1
7274 | Slave09 Outlet Port04 Active Power | RO | 4 bytes | Unit:0.1
7276 | Slave09 Outlet Port05 Active Power | RO | 4 bytes | Unit:0.1
7278 | Slave09 Outlet Port06 Active Power | RO | 4 bytes | Unit:0.1
7280 | Slave09 Outlet Port07 Active Power | RO | 4 bytes | Unit:0.1
7282 | Slave09 Outlet Port08 Active Power | RO | 4 bytes | Unit:0.1
7284 | Slave09 Outlet Port09 Active Power | RO | 4 bytes | Unit:0.1
7286 | Slave09 Outlet Port10 Active Power | RO | 4 bytes | Unit:0.1
7288 | Slave09 Outlet Port11 Active Power | RO | 4 bytes | Unit:0.1
7290 | Slave09 Outlet Port12 Active Power | RO | 4 bytes | Unit:0.1
7292 | Slave09 Outlet Port13 Active Power | RO | 4 bytes | Unit:0.1
7294 | Slave09 Outlet Port14 Active Power | RO | 4 bytes | Unit:0.1
7296 | Slave09 Outlet Port15 Active Power | RO | 4 bytes | Unit:0.1
7298 | Slave09 Outlet Port16 Active Power | RO | 4 bytes | Unit:0.1
7300 | Slave09 Outlet Port17 Active Power | RO | 4 bytes | Unit:0.1
7302 | Slave09 Outlet Port18 Active Power | RO | 4 bytes | Unit:0.1
7304 | Slave09 Outlet Port19 Active Power | RO | 4 bytes | Unit:0.1
7306 | Slave09 Outlet Port20 Active Power | RO | 4 bytes | Unit:0.1
7308 | Slave09 Outlet Port21 Active Power | RO | 4 bytes | Unit:0.1
7310 | Slave09 Outlet Port22 Active Power | RO | 4 bytes | Unit:0.1
7312 | Slave09 Outlet Port23 Active Power | RO | 4 bytes | Unit:0.1
7314 | Slave09 Outlet Port24 Active Power | RO | 4 bytes | Unit:0.1
7316 | Slave09 Outlet Port25 Active Power | RO | 4 bytes | Unit:0.1
7318 | Slave09 Outlet Port26 Active Power | RO | 4 bytes | Unit:0.1
7320 | Slave09 Outlet Port27 Active Power | RO | 4 bytes | Unit:0.1
7322 | Slave09 Outlet Port28 Active Power | RO | 4 bytes | Unit:0.1
7324 | Slave09 Outlet Port29 Active Power | RO | 4 bytes | Unit:0.1
7326 | Slave09 Outlet Port30 Active Power | RO | 4 bytes | Unit:0.1
7328 | Slave09 Outlet Port31 Active Power | RO | 4 bytes | Unit:0.1
7330 | Slave09 Outlet Port32 Active Power | RO | 4 bytes | Unit:0.1
7332 | Slave09 Outlet Port33 Active Power | RO | 4 bytes | Unit:0.1
7334 | Slave09 Outlet Port34 Active Power | RO | 4 bytes | Unit:0.1
7336 | Slave09 Outlet Port35 Active Power | RO | 4 bytes | Unit:0.1
7338 | Slave09 Outlet Port36 Active Power | RO | 4 bytes | Unit:0.1
7340 | Slave09 Outlet Port37 Active Power | RO | 4 bytes | Unit:0.1
7342 | Slave09 Outlet Port38 Active Power | RO | 4 bytes | Unit:0.1
7344 | Slave09 Outlet Port39 Active Power | RO | 4 bytes | Unit:0.1
7346 | Slave09 Outlet Port40 Active Power | RO | 4 bytes | Unit:0.1
7348 | Slave09 Outlet Port41 Active Power | RO | 4 bytes | Unit:0.1
7350 | Slave09 Outlet Port42 Active Power | RO | 4 bytes | Unit:0.1
7352 | Slave10 Outlet Port01 Active Power | RO | 4 bytes | Unit:0.1
7354 | Slave10 Outlet Port02 Active Power | RO | 4 bytes | Unit:0.1
7356 | Slave10 Outlet Port03 Active Power | RO | 4 bytes | Unit:0.1
7358 | Slave10 Outlet Port04 Active Power | RO | 4 bytes | Unit:0.1
7360 | Slave10 Outlet Port05 Active Power | RO | 4 bytes | Unit:0.1
7362 | Slave10 Outlet Port06 Active Power | RO | 4 bytes | Unit:0.1
7364 | Slave10 Outlet Port07 Active Power | RO | 4 bytes | Unit:0.1
7366 | Slave10 Outlet Port08 Active Power | RO | 4 bytes | Unit:0.1
7368 | Slave10 Outlet Port09 Active Power | RO | 4 bytes | Unit:0.1
7370 | Slave10 Outlet Port10 Active Power | RO | 4 bytes | Unit:0.1
7372 | Slave10 Outlet Port11 Active Power | RO | 4 bytes | Unit:0.1
7374 | Slave10 Outlet Port12 Active Power | RO | 4 bytes | Unit:0.1
7376 | Slave10 Outlet Port13 Active Power | RO | 4 bytes | Unit:0.1
7378 | Slave10 Outlet Port14 Active Power | RO | 4 bytes | Unit:0.1
7380 | Slave10 Outlet Port15 Active Power | RO | 4 bytes | Unit:0.1
7382 | Slave10 Outlet Port16 Active Power | RO | 4 bytes | Unit:0.1
7384 | Slave10 Outlet Port17 Active Power | RO | 4 bytes | Unit:0.1
7386 | Slave10 Outlet Port18 Active Power | RO | 4 bytes | Unit:0.1
7388 | Slave10 Outlet Port19 Active Power | RO | 4 bytes | Unit:0.1
7390 | Slave10 Outlet Port20 Active Power | RO | 4 bytes | Unit:0.1
7392 | Slave10 Outlet Port21 Active Power | RO | 4 bytes | Unit:0.1
7394 | Slave10 Outlet Port22 Active Power | RO | 4 bytes | Unit:0.1
7396 | Slave10 Outlet Port23 Active Power | RO | 4 bytes | Unit:0.1
7398 | Slave10 Outlet Port24 Active Power | RO | 4 bytes | Unit:0.1
7400 | Slave10 Outlet Port25 Active Power | RO | 4 bytes | Unit:0.1
7402 | Slave10 Outlet Port26 Active Power | RO | 4 bytes | Unit:0.1
7404 | Slave10 Outlet Port27 Active Power | RO | 4 bytes | Unit:0.1
7406 | Slave10 Outlet Port28 Active Power | RO | 4 bytes | Unit:0.1
7408 | Slave10 Outlet Port29 Active Power | RO | 4 bytes | Unit:0.1
7410 | Slave10 Outlet Port30 Active Power | RO | 4 bytes | Unit:0.1
7412 | Slave10 Outlet Port31 Active Power | RO | 4 bytes | Unit:0.1
7414 | Slave10 Outlet Port32 Active Power | RO | 4 bytes | Unit:0.1
7416 | Slave10 Outlet Port33 Active Power | RO | 4 bytes | Unit:0.1
7418 | Slave10 Outlet Port34 Active Power | RO | 4 bytes | Unit:0.1
7420 | Slave10 Outlet Port35 Active Power | RO | 4 bytes | Unit:0.1
7422 | Slave10 Outlet Port36 Active Power | RO | 4 bytes | Unit:0.1
7424 | Slave10 Outlet Port37 Active Power | RO | 4 bytes | Unit:0.1
7426 | Slave10 Outlet Port38 Active Power | RO | 4 bytes | Unit:0.1
7428 | Slave10 Outlet Port39 Active Power | RO | 4 bytes | Unit:0.1
7430 | Slave10 Outlet Port40 Active Power | RO | 4 bytes | Unit:0.1
7432 | Slave10 Outlet Port41 Active Power | RO | 4 bytes | Unit:0.1
7434 | Slave10 Outlet Port42 Active Power | RO | 4 bytes | Unit:0.1
7436 | Slave11 Outlet Port01 Active Power | RO | 4 bytes | Unit:0.1
7438 | Slave11 Outlet Port02 Active Power | RO | 4 bytes | Unit:0.1
7440 | Slave11 Outlet Port03 Active Power | RO | 4 bytes | Unit:0.1
7442 | Slave11 Outlet Port04 Active Power | RO | 4 bytes | Unit:0.1
7444 | Slave11 Outlet Port05 Active Power | RO | 4 bytes | Unit:0.1
7446 | Slave11 Outlet Port06 Active Power | RO | 4 bytes | Unit:0.1
7448 | Slave11 Outlet Port07 Active Power | RO | 4 bytes | Unit:0.1
7450 | Slave11 Outlet Port08 Active Power | RO | 4 bytes | Unit:0.1
7452 | Slave11 Outlet Port09 Active Power | RO | 4 bytes | Unit:0.1
7454 | Slave11 Outlet Port10 Active Power | RO | 4 bytes | Unit:0.1
7456 | Slave11 Outlet Port11 Active Power | RO | 4 bytes | Unit:0.1
7458 | Slave11 Outlet Port12 Active Power | RO | 4 bytes | Unit:0.1
7460 | Slave11 Outlet Port13 Active Power | RO | 4 bytes | Unit:0.1
7462 | Slave11 Outlet Port14 Active Power | RO | 4 bytes | Unit:0.1
7464 | Slave11 Outlet Port15 Active Power | RO | 4 bytes | Unit:0.1
7466 | Slave11 Outlet Port16 Active Power | RO | 4 bytes | Unit:0.1
7468 | Slave11 Outlet Port17 Active Power | RO | 4 bytes | Unit:0.1
7470 | Slave11 Outlet Port18 Active Power | RO | 4 bytes | Unit:0.1
7472 | Slave11 Outlet Port19 Active Power | RO | 4 bytes | Unit:0.1
7474 | Slave11 Outlet Port20 Active Power | RO | 4 bytes | Unit:0.1
7476 | Slave11 Outlet Port21 Active Power | RO | 4 bytes | Unit:0.1
7478 | Slave11 Outlet Port22 Active Power | RO | 4 bytes | Unit:0.1
7480 | Slave11 Outlet Port23 Active Power | RO | 4 bytes | Unit:0.1
7482 | Slave11 Outlet Port24 Active Power | RO | 4 bytes | Unit:0.1
7484 | Slave11 Outlet Port25 Active Power | RO | 4 bytes | Unit:0.1
7486 | Slave11 Outlet Port26 Active Power | RO | 4 bytes | Unit:0.1
7488 | Slave11 Outlet Port27 Active Power | RO | 4 bytes | Unit:0.1
7490 | Slave11 Outlet Port28 Active Power | RO | 4 bytes | Unit:0.1
7492 | Slave11 Outlet Port29 Active Power | RO | 4 bytes | Unit:0.1
7494 | Slave11 Outlet Port30 Active Power | RO | 4 bytes | Unit:0.1
7496 | Slave11 Outlet Port31 Active Power | RO | 4 bytes | Unit:0.1
7498 | Slave11 Outlet Port32 Active Power | RO | 4 bytes | Unit:0.1
7500 | Slave11 Outlet Port33 Active Power | RO | 4 bytes | Unit:0.1
7502 | Slave11 Outlet Port34 Active Power | RO | 4 bytes | Unit:0.1
7504 | Slave11 Outlet Port35 Active Power | RO | 4 bytes | Unit:0.1
7506 | Slave11 Outlet Port36 Active Power | RO | 4 bytes | Unit:0.1
7508 | Slave11 Outlet Port37 Active Power | RO | 4 bytes | Unit:0.1
7510 | Slave11 Outlet Port38 Active Power | RO | 4 bytes | Unit:0.1
7512 | Slave11 Outlet Port39 Active Power | RO | 4 bytes | Unit:0.1
7514 | Slave11 Outlet Port40 Active Power | RO | 4 bytes | Unit:0.1
7516 | Slave11 Outlet Port41 Active Power | RO | 4 bytes | Unit:0.1
7518 | Slave11 Outlet Port42 Active Power | RO | 4 bytes | Unit:0.1
7520 | Slave12 Outlet Port01 Active Power | RO | 4 bytes | Unit:0.1
7522 | Slave12 Outlet Port02 Active Power | RO | 4 bytes | Unit:0.1
7524 | Slave12 Outlet Port03 Active Power | RO | 4 bytes | Unit:0.1
7526 | Slave12 Outlet Port04 Active Power | RO | 4 bytes | Unit:0.1
7528 | Slave12 Outlet Port05 Active Power | RO | 4 bytes | Unit:0.1
7530 | Slave12 Outlet Port06 Active Power | RO | 4 bytes | Unit:0.1
7532 | Slave12 Outlet Port07 Active Power | RO | 4 bytes | Unit:0.1
7534 | Slave12 Outlet Port08 Active Power | RO | 4 bytes | Unit:0.1
7536 | Slave12 Outlet Port09 Active Power | RO | 4 bytes | Unit:0.1
7538 | Slave12 Outlet Port10 Active Power | RO | 4 bytes | Unit:0.1
7540 | Slave12 Outlet Port11 Active Power | RO | 4 bytes | Unit:0.1
7542 | Slave12 Outlet Port12 Active Power | RO | 4 bytes | Unit:0.1
7544 | Slave12 Outlet Port13 Active Power | RO | 4 bytes | Unit:0.1
7546 | Slave12 Outlet Port14 Active Power | RO | 4 bytes | Unit:0.1
7548 | Slave12 Outlet Port15 Active Power | RO | 4 bytes | Unit:0.1
7550 | Slave12 Outlet Port16 Active Power | RO | 4 bytes | Unit:0.1
7552 | Slave12 Outlet Port17 Active Power | RO | 4 bytes | Unit:0.1
7554 | Slave12 Outlet Port18 Active Power | RO | 4 bytes | Unit:0.1
7556 | Slave12 Outlet Port19 Active Power | RO | 4 bytes | Unit:0.1
7558 | Slave12 Outlet Port20 Active Power | RO | 4 bytes | Unit:0.1
7560 | Slave12 Outlet Port21 Active Power | RO | 4 bytes | Unit:0.1
7562 | Slave12 Outlet Port22 Active Power | RO | 4 bytes | Unit:0.1
7564 | Slave12 Outlet Port23 Active Power | RO | 4 bytes | Unit:0.1
7566 | Slave12 Outlet Port24 Active Power | RO | 4 bytes | Unit:0.1
7568 | Slave12 Outlet Port25 Active Power | RO | 4 bytes | Unit:0.1
7570 | Slave12 Outlet Port26 Active Power | RO | 4 bytes | Unit:0.1
7572 | Slave12 Outlet Port27 Active Power | RO | 4 bytes | Unit:0.1
7574 | Slave12 Outlet Port28 Active Power | RO | 4 bytes | Unit:0.1
7576 | Slave12 Outlet Port29 Active Power | RO | 4 bytes | Unit:0.1
7578 | Slave12 Outlet Port30 Active Power | RO | 4 bytes | Unit:0.1
7580 | Slave12 Outlet Port31 Active Power | RO | 4 bytes | Unit:0.1
7582 | Slave12 Outlet Port32 Active Power | RO | 4 bytes | Unit:0.1
7584 | Slave12 Outlet Port33 Active Power | RO | 4 bytes | Unit:0.1
7586 | Slave12 Outlet Port34 Active Power | RO | 4 bytes | Unit:0.1
7588 | Slave12 Outlet Port35 Active Power | RO | 4 bytes | Unit:0.1
7590 | Slave12 Outlet Port36 Active Power | RO | 4 bytes | Unit:0.1
7592 | Slave12 Outlet Port37 Active Power | RO | 4 bytes | Unit:0.1
7594 | Slave12 Outlet Port38 Active Power | RO | 4 bytes | Unit:0.1
7596 | Slave12 Outlet Port39 Active Power | RO | 4 bytes | Unit:0.1
7598 | Slave12 Outlet Port40 Active Power | RO | 4 bytes | Unit:0.1
7600 | Slave12 Outlet Port41 Active Power | RO | 4 bytes | Unit:0.1
7602 | Slave12 Outlet Port42 Active Power | RO | 4 bytes | Unit:0.1
7604 | Slave13 Outlet Port01 Active Power | RO | 4 bytes | Unit:0.1
7606 | Slave13 Outlet Port02 Active Power | RO | 4 bytes | Unit:0.1
7608 | Slave13 Outlet Port03 Active Power | RO | 4 bytes | Unit:0.1
7610 | Slave13 Outlet Port04 Active Power | RO | 4 bytes | Unit:0.1
7612 | Slave13 Outlet Port05 Active Power | RO | 4 bytes | Unit:0.1
7614 | Slave13 Outlet Port06 Active Power | RO | 4 bytes | Unit:0.1
7616 | Slave13 Outlet Port07 Active Power | RO | 4 bytes | Unit:0.1
7618 | Slave13 Outlet Port08 Active Power | RO | 4 bytes | Unit:0.1
7620 | Slave13 Outlet Port09 Active Power | RO | 4 bytes | Unit:0.1
7622 | Slave13 Outlet Port10 Active Power | RO | 4 bytes | Unit:0.1
7624 | Slave13 Outlet Port11 Active Power | RO | 4 bytes | Unit:0.1
7626 | Slave13 Outlet Port12 Active Power | RO | 4 bytes | Unit:0.1
7628 | Slave13 Outlet Port13 Active Power | RO | 4 bytes | Unit:0.1
7630 | Slave13 Outlet Port14 Active Power | RO | 4 bytes | Unit:0.1
7632 | Slave13 Outlet Port15 Active Power | RO | 4 bytes | Unit:0.1
7634 | Slave13 Outlet Port16 Active Power | RO | 4 bytes | Unit:0.1
7636 | Slave13 Outlet Port17 Active Power | RO | 4 bytes | Unit:0.1
7638 | Slave13 Outlet Port18 Active Power | RO | 4 bytes | Unit:0.1
7640 | Slave13 Outlet Port19 Active Power | RO | 4 bytes | Unit:0.1
7642 | Slave13 Outlet Port20 Active Power | RO | 4 bytes | Unit:0.1
7644 | Slave13 Outlet Port21 Active Power | RO | 4 bytes | Unit:0.1
7646 | Slave13 Outlet Port22 Active Power | RO | 4 bytes | Unit:0.1
7648 | Slave13 Outlet Port23 Active Power | RO | 4 bytes | Unit:0.1
7650 | Slave13 Outlet Port24 Active Power | RO | 4 bytes | Unit:0.1
7652 | Slave13 Outlet Port25 Active Power | RO | 4 bytes | Unit:0.1
7654 | Slave13 Outlet Port26 Active Power | RO | 4 bytes | Unit:0.1
7656 | Slave13 Outlet Port27 Active Power | RO | 4 bytes | Unit:0.1
7658 | Slave13 Outlet Port28 Active Power | RO | 4 bytes | Unit:0.1
7660 | Slave13 Outlet Port29 Active Power | RO | 4 bytes | Unit:0.1
7662 | Slave13 Outlet Port30 Active Power | RO | 4 bytes | Unit:0.1
7664 | Slave13 Outlet Port31 Active Power | RO | 4 bytes | Unit:0.1
7666 | Slave13 Outlet Port32 Active Power | RO | 4 bytes | Unit:0.1
7668 | Slave13 Outlet Port33 Active Power | RO | 4 bytes | Unit:0.1
7670 | Slave13 Outlet Port34 Active Power | RO | 4 bytes | Unit:0.1
7672 | Slave13 Outlet Port35 Active Power | RO | 4 bytes | Unit:0.1
7674 | Slave13 Outlet Port36 Active Power | RO | 4 bytes | Unit:0.1
7676 | Slave13 Outlet Port37 Active Power | RO | 4 bytes | Unit:0.1
7678 | Slave13 Outlet Port38 Active Power | RO | 4 bytes | Unit:0.1
7680 | Slave13 Outlet Port39 Active Power | RO | 4 bytes | Unit:0.1
7682 | Slave13 Outlet Port40 Active Power | RO | 4 bytes | Unit:0.1
7684 | Slave13 Outlet Port41 Active Power | RO | 4 bytes | Unit:0.1
7686 | Slave13 Outlet Port42 Active Power | RO | 4 bytes | Unit:0.1
7688 | Slave14 Outlet Port01 Active Power | RO | 4 bytes | Unit:0.1
7690 | Slave14 Outlet Port02 Active Power | RO | 4 bytes | Unit:0.1
7692 | Slave14 Outlet Port03 Active Power | RO | 4 bytes | Unit:0.1
7694 | Slave14 Outlet Port04 Active Power | RO | 4 bytes | Unit:0.1
7696 | Slave14 Outlet Port05 Active Power | RO | 4 bytes | Unit:0.1
7698 | Slave14 Outlet Port06 Active Power | RO | 4 bytes | Unit:0.1
7700 | Slave14 Outlet Port07 Active Power | RO | 4 bytes | Unit:0.1
7702 | Slave14 Outlet Port08 Active Power | RO | 4 bytes | Unit:0.1
7704 | Slave14 Outlet Port09 Active Power | RO | 4 bytes | Unit:0.1
7706 | Slave14 Outlet Port10 Active Power | RO | 4 bytes | Unit:0.1
7708 | Slave14 Outlet Port11 Active Power | RO | 4 bytes | Unit:0.1
7710 | Slave14 Outlet Port12 Active Power | RO | 4 bytes | Unit:0.1
7712 | Slave14 Outlet Port13 Active Power | RO | 4 bytes | Unit:0.1
7714 | Slave14 Outlet Port14 Active Power | RO | 4 bytes | Unit:0.1
7716 | Slave14 Outlet Port15 Active Power | RO | 4 bytes | Unit:0.1
7718 | Slave14 Outlet Port16 Active Power | RO | 4 bytes | Unit:0.1
7720 | Slave14 Outlet Port17 Active Power | RO | 4 bytes | Unit:0.1
7722 | Slave14 Outlet Port18 Active Power | RO | 4 bytes | Unit:0.1
7724 | Slave14 Outlet Port19 Active Power | RO | 4 bytes | Unit:0.1
7726 | Slave14 Outlet Port20 Active Power | RO | 4 bytes | Unit:0.1
7728 | Slave14 Outlet Port21 Active Power | RO | 4 bytes | Unit:0.1
7730 | Slave14 Outlet Port22 Active Power | RO | 4 bytes | Unit:0.1
7732 | Slave14 Outlet Port23 Active Power | RO | 4 bytes | Unit:0.1
7734 | Slave14 Outlet Port24 Active Power | RO | 4 bytes | Unit:0.1
7736 | Slave14 Outlet Port25 Active Power | RO | 4 bytes | Unit:0.1
7738 | Slave14 Outlet Port26 Active Power | RO | 4 bytes | Unit:0.1
7740 | Slave14 Outlet Port27 Active Power | RO | 4 bytes | Unit:0.1
7742 | Slave14 Outlet Port28 Active Power | RO | 4 bytes | Unit:0.1
7744 | Slave14 Outlet Port29 Active Power | RO | 4 bytes | Unit:0.1
7746 | Slave14 Outlet Port30 Active Power | RO | 4 bytes | Unit:0.1
7748 | Slave14 Outlet Port31 Active Power | RO | 4 bytes | Unit:0.1
7750 | Slave14 Outlet Port32 Active Power | RO | 4 bytes | Unit:0.1
7752 | Slave14 Outlet Port33 Active Power | RO | 4 bytes | Unit:0.1
7754 | Slave14 Outlet Port34 Active Power | RO | 4 bytes | Unit:0.1
7756 | Slave14 Outlet Port35 Active Power | RO | 4 bytes | Unit:0.1
7758 | Slave14 Outlet Port36 Active Power | RO | 4 bytes | Unit:0.1
7760 | Slave14 Outlet Port37 Active Power | RO | 4 bytes | Unit:0.1
7762 | Slave14 Outlet Port38 Active Power | RO | 4 bytes | Unit:0.1
7764 | Slave14 Outlet Port39 Active Power | RO | 4 bytes | Unit:0.1
7766 | Slave14 Outlet Port40 Active Power | RO | 4 bytes | Unit:0.1
7768 | Slave14 Outlet Port41 Active Power | RO | 4 bytes | Unit:0.1
7770 | Slave14 Outlet Port42 Active Power | RO | 4 bytes | Unit:0.1
7772 | Slave15 Outlet Port01 Active Power | RO | 4 bytes | Unit:0.1
7774 | Slave15 Outlet Port02 Active Power | RO | 4 bytes | Unit:0.1
7776 | Slave15 Outlet Port03 Active Power | RO | 4 bytes | Unit:0.1
7778 | Slave15 Outlet Port04 Active Power | RO | 4 bytes | Unit:0.1
7780 | Slave15 Outlet Port05 Active Power | RO | 4 bytes | Unit:0.1
7782 | Slave15 Outlet Port06 Active Power | RO | 4 bytes | Unit:0.1
7784 | Slave15 Outlet Port07 Active Power | RO | 4 bytes | Unit:0.1
7786 | Slave15 Outlet Port08 Active Power | RO | 4 bytes | Unit:0.1
7788 | Slave15 Outlet Port09 Active Power | RO | 4 bytes | Unit:0.1
7790 | Slave15 Outlet Port10 Active Power | RO | 4 bytes | Unit:0.1
7792 | Slave15 Outlet Port11 Active Power | RO | 4 bytes | Unit:0.1
7794 | Slave15 Outlet Port12 Active Power | RO | 4 bytes | Unit:0.1
7796 | Slave15 Outlet Port13 Active Power | RO | 4 bytes | Unit:0.1
7798 | Slave15 Outlet Port14 Active Power | RO | 4 bytes | Unit:0.1
7800 | Slave15 Outlet Port15 Active Power | RO | 4 bytes | Unit:0.1
7802 | Slave15 Outlet Port16 Active Power | RO | 4 bytes | Unit:0.1
7804 | Slave15 Outlet Port17 Active Power | RO | 4 bytes | Unit:0.1
7806 | Slave15 Outlet Port18 Active Power | RO | 4 bytes | Unit:0.1
7808 | Slave15 Outlet Port19 Active Power | RO | 4 bytes | Unit:0.1
7810 | Slave15 Outlet Port20 Active Power | RO | 4 bytes | Unit:0.1
7812 | Slave15 Outlet Port21 Active Power | RO | 4 bytes | Unit:0.1
7814 | Slave15 Outlet Port22 Active Power | RO | 4 bytes | Unit:0.1
7816 | Slave15 Outlet Port23 Active Power | RO | 4 bytes | Unit:0.1
7818 | Slave15 Outlet Port24 Active Power | RO | 4 bytes | Unit:0.1
7820 | Slave15 Outlet Port25 Active Power | RO | 4 bytes | Unit:0.1
7822 | Slave15 Outlet Port26 Active Power | RO | 4 bytes | Unit:0.1
7824 | Slave15 Outlet Port27 Active Power | RO | 4 bytes | Unit:0.1
7826 | Slave15 Outlet Port28 Active Power | RO | 4 bytes | Unit:0.1
7828 | Slave15 Outlet Port29 Active Power | RO | 4 bytes | Unit:0.1
7830 | Slave15 Outlet Port30 Active Power | RO | 4 bytes | Unit:0.1
7832 | Slave15 Outlet Port31 Active Power | RO | 4 bytes | Unit:0.1
7834 | Slave15 Outlet Port32 Active Power | RO | 4 bytes | Unit:0.1
7836 | Slave15 Outlet Port33 Active Power | RO | 4 bytes | Unit:0.1
7838 | Slave15 Outlet Port34 Active Power | RO | 4 bytes | Unit:0.1
7840 | Slave15 Outlet Port35 Active Power | RO | 4 bytes | Unit:0.1
7842 | Slave15 Outlet Port36 Active Power | RO | 4 bytes | Unit:0.1
7844 | Slave15 Outlet Port37 Active Power | RO | 4 bytes | Unit:0.1
7846 | Slave15 Outlet Port38 Active Power | RO | 4 bytes | Unit:0.1
7848 | Slave15 Outlet Port39 Active Power | RO | 4 bytes | Unit:0.1
7850 | Slave15 Outlet Port40 Active Power | RO | 4 bytes | Unit:0.1
7852 | Slave15 Outlet Port41 Active Power | RO | 4 bytes | Unit:0.1
7854 | Slave15 Outlet Port42 Active Power | RO | 4 bytes | Unit:0.1
7856 | Master Outlet Port01 Apparent Power | RO | 4 bytes | Unit:0.1
7858 | Master Outlet Port02 Apparent Power | RO | 4 bytes | Unit:0.1
7860 | Master Outlet Port03 Apparent Power | RO | 4 bytes | Unit:0.1
7862 | Master Outlet Port04 Apparent Power | RO | 4 bytes | Unit:0.1
7864 | Master Outlet Port05 Apparent Power | RO | 4 bytes | Unit:0.1
7866 | Master Outlet Port06 Apparent Power | RO | 4 bytes | Unit:0.1
7868 | Master Outlet Port07 Apparent Power | RO | 4 bytes | Unit:0.1
7870 | Master Outlet Port08 Apparent Power | RO | 4 bytes | Unit:0.1
7872 | Master Outlet Port09 Apparent Power | RO | 4 bytes | Unit:0.1
7874 | Master Outlet Port10 Apparent Power | RO | 4 bytes | Unit:0.1
7876 | Master Outlet Port11 Apparent Power | RO | 4 bytes | Unit:0.1
7878 | Master Outlet Port12 Apparent Power | RO | 4 bytes | Unit:0.1
7880 | Master Outlet Port13 Apparent Power | RO | 4 bytes | Unit:0.1
7882 | Master Outlet Port14 Apparent Power | RO | 4 bytes | Unit:0.1
7884 | Master Outlet Port15 Apparent Power | RO | 4 bytes | Unit:0.1
7886 | Master Outlet Port16 Apparent Power | RO | 4 bytes | Unit:0.1
7888 | Master Outlet Port17 Apparent Power | RO | 4 bytes | Unit:0.1
7890 | Master Outlet Port18 Apparent Power | RO | 4 bytes | Unit:0.1
7892 | Master Outlet Port19 Apparent Power | RO | 4 bytes | Unit:0.1
7894 | Master Outlet Port20 Apparent Power | RO | 4 bytes | Unit:0.1
7896 | Master Outlet Port21 Apparent Power | RO | 4 bytes | Unit:0.1
7898 | Master Outlet Port22 Apparent Power | RO | 4 bytes | Unit:0.1
7900 | Master Outlet Port23 Apparent Power | RO | 4 bytes | Unit:0.1
7902 | Master Outlet Port24 Apparent Power | RO | 4 bytes | Unit:0.1
7904 | Master Outlet Port25 Apparent Power | RO | 4 bytes | Unit:0.1
7906 | Master Outlet Port26 Apparent Power | RO | 4 bytes | Unit:0.1
7908 | Master Outlet Port27 Apparent Power | RO | 4 bytes | Unit:0.1
7910 | Master Outlet Port28 Apparent Power | RO | 4 bytes | Unit:0.1
7912 | Master Outlet Port29 Apparent Power | RO | 4 bytes | Unit:0.1
7914 | Master Outlet Port30 Apparent Power | RO | 4 bytes | Unit:0.1
7916 | Master Outlet Port31 Apparent Power | RO | 4 bytes | Unit:0.1
7918 | Master Outlet Port32 Apparent Power | RO | 4 bytes | Unit:0.1
7920 | Master Outlet Port33 Apparent Power | RO | 4 bytes | Unit:0.1
7922 | Master Outlet Port34 Apparent Power | RO | 4 bytes | Unit:0.1
7924 | Master Outlet Port35 Apparent Power | RO | 4 bytes | Unit:0.1
7926 | Master Outlet Port36 Apparent Power | RO | 4 bytes | Unit:0.1
7928 | Master Outlet Port37 Apparent Power | RO | 4 bytes | Unit:0.1
7930 | Master Outlet Port38 Apparent Power | RO | 4 bytes | Unit:0.1
7932 | Master Outlet Port39 Apparent Power | RO | 4 bytes | Unit:0.1
7934 | Master Outlet Port40 Apparent Power | RO | 4 bytes | Unit:0.1
7936 | Master Outlet Port41 Apparent Power | RO | 4 bytes | Unit:0.1
7938 | Master Outlet Port42 Apparent Power | RO | 4 bytes | Unit:0.1
7940 | Slave01 Outlet Port01 Apparent Power | RO | 4 bytes | Unit:0.1
7942 | Slave01 Outlet Port02 Apparent Power | RO | 4 bytes | Unit:0.1
7944 | Slave01 Outlet Port03 Apparent Power | RO | 4 bytes | Unit:0.1
7946 | Slave01 Outlet Port04 Apparent Power | RO | 4 bytes | Unit:0.1
7948 | Slave01 Outlet Port05 Apparent Power | RO | 4 bytes | Unit:0.1
7950 | Slave01 Outlet Port06 Apparent Power | RO | 4 bytes | Unit:0.1
7952 | Slave01 Outlet Port07 Apparent Power | RO | 4 bytes | Unit:0.1
7954 | Slave01 Outlet Port08 Apparent Power | RO | 4 bytes | Unit:0.1
7956 | Slave01 Outlet Port09 Apparent Power | RO | 4 bytes | Unit:0.1
7958 | Slave01 Outlet Port10 Apparent Power | RO | 4 bytes | Unit:0.1
7960 | Slave01 Outlet Port11 Apparent Power | RO | 4 bytes | Unit:0.1
7962 | Slave01 Outlet Port12 Apparent Power | RO | 4 bytes | Unit:0.1
7964 | Slave01 Outlet Port13 Apparent Power | RO | 4 bytes | Unit:0.1
7966 | Slave01 Outlet Port14 Apparent Power | RO | 4 bytes | Unit:0.1
7968 | Slave01 Outlet Port15 Apparent Power | RO | 4 bytes | Unit:0.1
7970 | Slave01 Outlet Port16 Apparent Power | RO | 4 bytes | Unit:0.1
7972 | Slave01 Outlet Port17 Apparent Power | RO | 4 bytes | Unit:0.1
7974 | Slave01 Outlet Port18 Apparent Power | RO | 4 bytes | Unit:0.1
7976 | Slave01 Outlet Port19 Apparent Power | RO | 4 bytes | Unit:0.1
7978 | Slave01 Outlet Port20 Apparent Power | RO | 4 bytes | Unit:0.1
7980 | Slave01 Outlet Port21 Apparent Power | RO | 4 bytes | Unit:0.1
7982 | Slave01 Outlet Port22 Apparent Power | RO | 4 bytes | Unit:0.1
7984 | Slave01 Outlet Port23 Apparent Power | RO | 4 bytes | Unit:0.1
7986 | Slave01 Outlet Port24 Apparent Power | RO | 4 bytes | Unit:0.1
7988 | Slave01 Outlet Port25 Apparent Power | RO | 4 bytes | Unit:0.1
7990 | Slave01 Outlet Port26 Apparent Power | RO | 4 bytes | Unit:0.1
7992 | Slave01 Outlet Port27 Apparent Power | RO | 4 bytes | Unit:0.1
7994 | Slave01 Outlet Port28 Apparent Power | RO | 4 bytes | Unit:0.1
7996 | Slave01 Outlet Port29 Apparent Power | RO | 4 bytes | Unit:0.1
7998 | Slave01 Outlet Port30 Apparent Power | RO | 4 bytes | Unit:0.1
8000 | Slave01 Outlet Port31 Apparent Power | RO | 4 bytes | Unit:0.1
8002 | Slave01 Outlet Port32 Apparent Power | RO | 4 bytes | Unit:0.1
8004 | Slave01 Outlet Port33 Apparent Power | RO | 4 bytes | Unit:0.1
8006 | Slave01 Outlet Port34 Apparent Power | RO | 4 bytes | Unit:0.1
8008 | Slave01 Outlet Port35 Apparent Power | RO | 4 bytes | Unit:0.1
8010 | Slave01 Outlet Port36 Apparent Power | RO | 4 bytes | Unit:0.1
8012 | Slave01 Outlet Port37 Apparent Power | RO | 4 bytes | Unit:0.1
8014 | Slave01 Outlet Port38 Apparent Power | RO | 4 bytes | Unit:0.1
8016 | Slave01 Outlet Port39 Apparent Power | RO | 4 bytes | Unit:0.1
8018 | Slave01 Outlet Port40 Apparent Power | RO | 4 bytes | Unit:0.1
8020 | Slave01 Outlet Port41 Apparent Power | RO | 4 bytes | Unit:0.1
8022 | Slave01 Outlet Port42 Apparent Power | RO | 4 bytes | Unit:0.1
8024 | Slave02 Outlet Port01 Apparent Power | RO | 4 bytes | Unit:0.1
8026 | Slave02 Outlet Port02 Apparent Power | RO | 4 bytes | Unit:0.1
8028 | Slave02 Outlet Port03 Apparent Power | RO | 4 bytes | Unit:0.1
8030 | Slave02 Outlet Port04 Apparent Power | RO | 4 bytes | Unit:0.1
8032 | Slave02 Outlet Port05 Apparent Power | RO | 4 bytes | Unit:0.1
8034 | Slave02 Outlet Port06 Apparent Power | RO | 4 bytes | Unit:0.1
8036 | Slave02 Outlet Port07 Apparent Power | RO | 4 bytes | Unit:0.1
8038 | Slave02 Outlet Port08 Apparent Power | RO | 4 bytes | Unit:0.1
8040 | Slave02 Outlet Port09 Apparent Power | RO | 4 bytes | Unit:0.1
8042 | Slave02 Outlet Port10 Apparent Power | RO | 4 bytes | Unit:0.1
8044 | Slave02 Outlet Port11 Apparent Power | RO | 4 bytes | Unit:0.1
8046 | Slave02 Outlet Port12 Apparent Power | RO | 4 bytes | Unit:0.1
8048 | Slave02 Outlet Port13 Apparent Power | RO | 4 bytes | Unit:0.1
8050 | Slave02 Outlet Port14 Apparent Power | RO | 4 bytes | Unit:0.1
8052 | Slave02 Outlet Port15 Apparent Power | RO | 4 bytes | Unit:0.1
8054 | Slave02 Outlet Port16 Apparent Power | RO | 4 bytes | Unit:0.1
8056 | Slave02 Outlet Port17 Apparent Power | RO | 4 bytes | Unit:0.1
8058 | Slave02 Outlet Port18 Apparent Power | RO | 4 bytes | Unit:0.1
8060 | Slave02 Outlet Port19 Apparent Power | RO | 4 bytes | Unit:0.1
8062 | Slave02 Outlet Port20 Apparent Power | RO | 4 bytes | Unit:0.1
8064 | Slave02 Outlet Port21 Apparent Power | RO | 4 bytes | Unit:0.1
8066 | Slave02 Outlet Port22 Apparent Power | RO | 4 bytes | Unit:0.1
8068 | Slave02 Outlet Port23 Apparent Power | RO | 4 bytes | Unit:0.1
8070 | Slave02 Outlet Port24 Apparent Power | RO | 4 bytes | Unit:0.1
8072 | Slave02 Outlet Port25 Apparent Power | RO | 4 bytes | Unit:0.1
8074 | Slave02 Outlet Port26 Apparent Power | RO | 4 bytes | Unit:0.1
8076 | Slave02 Outlet Port27 Apparent Power | RO | 4 bytes | Unit:0.1
8078 | Slave02 Outlet Port28 Apparent Power | RO | 4 bytes | Unit:0.1
8080 | Slave02 Outlet Port29 Apparent Power | RO | 4 bytes | Unit:0.1
8082 | Slave02 Outlet Port30 Apparent Power | RO | 4 bytes | Unit:0.1
8084 | Slave02 Outlet Port31 Apparent Power | RO | 4 bytes | Unit:0.1
8086 | Slave02 Outlet Port32 Apparent Power | RO | 4 bytes | Unit:0.1
8088 | Slave02 Outlet Port33 Apparent Power | RO | 4 bytes | Unit:0.1
8090 | Slave02 Outlet Port34 Apparent Power | RO | 4 bytes | Unit:0.1
8092 | Slave02 Outlet Port35 Apparent Power | RO | 4 bytes | Unit:0.1
8094 | Slave02 Outlet Port36 Apparent Power | RO | 4 bytes | Unit:0.1
8096 | Slave02 Outlet Port37 Apparent Power | RO | 4 bytes | Unit:0.1
8098 | Slave02 Outlet Port38 Apparent Power | RO | 4 bytes | Unit:0.1
8100 | Slave02 Outlet Port39 Apparent Power | RO | 4 bytes | Unit:0.1
8102 | Slave02 Outlet Port40 Apparent Power | RO | 4 bytes | Unit:0.1
8104 | Slave02 Outlet Port41 Apparent Power | RO | 4 bytes | Unit:0.1
8106 | Slave02 Outlet Port42 Apparent Power | RO | 4 bytes | Unit:0.1
8108 | Slave03 Outlet Port01 Apparent Power | RO | 4 bytes | Unit:0.1
8110 | Slave03 Outlet Port02 Apparent Power | RO | 4 bytes | Unit:0.1
8112 | Slave03 Outlet Port03 Apparent Power | RO | 4 bytes | Unit:0.1
8114 | Slave03 Outlet Port04 Apparent Power | RO | 4 bytes | Unit:0.1
8116 | Slave03 Outlet Port05 Apparent Power | RO | 4 bytes | Unit:0.1
8118 | Slave03 Outlet Port06 Apparent Power | RO | 4 bytes | Unit:0.1
8120 | Slave03 Outlet Port07 Apparent Power | RO | 4 bytes | Unit:0.1
8122 | Slave03 Outlet Port08 Apparent Power | RO | 4 bytes | Unit:0.1
8124 | Slave03 Outlet Port09 Apparent Power | RO | 4 bytes | Unit:0.1
8126 | Slave03 Outlet Port10 Apparent Power | RO | 4 bytes | Unit:0.1
8128 | Slave03 Outlet Port11 Apparent Power | RO | 4 bytes | Unit:0.1
8130 | Slave03 Outlet Port12 Apparent Power | RO | 4 bytes | Unit:0.1
8132 | Slave03 Outlet Port13 Apparent Power | RO | 4 bytes | Unit:0.1
8134 | Slave03 Outlet Port14 Apparent Power | RO | 4 bytes | Unit:0.1
8136 | Slave03 Outlet Port15 Apparent Power | RO | 4 bytes | Unit:0.1
8138 | Slave03 Outlet Port16 Apparent Power | RO | 4 bytes | Unit:0.1
8140 | Slave03 Outlet Port17 Apparent Power | RO | 4 bytes | Unit:0.1
8142 | Slave03 Outlet Port18 Apparent Power | RO | 4 bytes | Unit:0.1
8144 | Slave03 Outlet Port19 Apparent Power | RO | 4 bytes | Unit:0.1
8146 | Slave03 Outlet Port20 Apparent Power | RO | 4 bytes | Unit:0.1
8148 | Slave03 Outlet Port21 Apparent Power | RO | 4 bytes | Unit:0.1
8150 | Slave03 Outlet Port22 Apparent Power | RO | 4 bytes | Unit:0.1
8152 | Slave03 Outlet Port23 Apparent Power | RO | 4 bytes | Unit:0.1
8154 | Slave03 Outlet Port24 Apparent Power | RO | 4 bytes | Unit:0.1
8156 | Slave03 Outlet Port25 Apparent Power | RO | 4 bytes | Unit:0.1
8158 | Slave03 Outlet Port26 Apparent Power | RO | 4 bytes | Unit:0.1
8160 | Slave03 Outlet Port27 Apparent Power | RO | 4 bytes | Unit:0.1
8162 | Slave03 Outlet Port28 Apparent Power | RO | 4 bytes | Unit:0.1
8164 | Slave03 Outlet Port29 Apparent Power | RO | 4 bytes | Unit:0.1
8166 | Slave03 Outlet Port30 Apparent Power | RO | 4 bytes | Unit:0.1
8168 | Slave03 Outlet Port31 Apparent Power | RO | 4 bytes | Unit:0.1
8170 | Slave03 Outlet Port32 Apparent Power | RO | 4 bytes | Unit:0.1
8172 | Slave03 Outlet Port33 Apparent Power | RO | 4 bytes | Unit:0.1
8174 | Slave03 Outlet Port34 Apparent Power | RO | 4 bytes | Unit:0.1
8176 | Slave03 Outlet Port35 Apparent Power | RO | 4 bytes | Unit:0.1
8178 | Slave03 Outlet Port36 Apparent Power | RO | 4 bytes | Unit:0.1
8180 | Slave03 Outlet Port37 Apparent Power | RO | 4 bytes | Unit:0.1
8182 | Slave03 Outlet Port38 Apparent Power | RO | 4 bytes | Unit:0.1
8184 | Slave03 Outlet Port39 Apparent Power | RO | 4 bytes | Unit:0.1
8186 | Slave03 Outlet Port40 Apparent Power | RO | 4 bytes | Unit:0.1
8188 | Slave03 Outlet Port41 Apparent Power | RO | 4 bytes | Unit:0.1
8190 | Slave03 Outlet Port42 Apparent Power | RO | 4 bytes | Unit:0.1
8192 | Slave04 Outlet Port01 Apparent Power | RO | 4 bytes | Unit:0.1
8194 | Slave04 Outlet Port02 Apparent Power | RO | 4 bytes | Unit:0.1
8196 | Slave04 Outlet Port03 Apparent Power | RO | 4 bytes | Unit:0.1
8198 | Slave04 Outlet Port04 Apparent Power | RO | 4 bytes | Unit:0.1
8200 | Slave04 Outlet Port05 Apparent Power | RO | 4 bytes | Unit:0.1
8202 | Slave04 Outlet Port06 Apparent Power | RO | 4 bytes | Unit:0.1
8204 | Slave04 Outlet Port07 Apparent Power | RO | 4 bytes | Unit:0.1
8206 | Slave04 Outlet Port08 Apparent Power | RO | 4 bytes | Unit:0.1
8208 | Slave04 Outlet Port09 Apparent Power | RO | 4 bytes | Unit:0.1
8210 | Slave04 Outlet Port10 Apparent Power | RO | 4 bytes | Unit:0.1
8212 | Slave04 Outlet Port11 Apparent Power | RO | 4 bytes | Unit:0.1
8214 | Slave04 Outlet Port12 Apparent Power | RO | 4 bytes | Unit:0.1
8216 | Slave04 Outlet Port13 Apparent Power | RO | 4 bytes | Unit:0.1
8218 | Slave04 Outlet Port14 Apparent Power | RO | 4 bytes | Unit:0.1
8220 | Slave04 Outlet Port15 Apparent Power | RO | 4 bytes | Unit:0.1
8222 | Slave04 Outlet Port16 Apparent Power | RO | 4 bytes | Unit:0.1
8224 | Slave04 Outlet Port17 Apparent Power | RO | 4 bytes | Unit:0.1
8226 | Slave04 Outlet Port18 Apparent Power | RO | 4 bytes | Unit:0.1
8228 | Slave04 Outlet Port19 Apparent Power | RO | 4 bytes | Unit:0.1
8230 | Slave04 Outlet Port20 Apparent Power | RO | 4 bytes | Unit:0.1
8232 | Slave04 Outlet Port21 Apparent Power | RO | 4 bytes | Unit:0.1
8234 | Slave04 Outlet Port22 Apparent Power | RO | 4 bytes | Unit:0.1
8236 | Slave04 Outlet Port23 Apparent Power | RO | 4 bytes | Unit:0.1
8238 | Slave04 Outlet Port24 Apparent Power | RO | 4 bytes | Unit:0.1
8240 | Slave04 Outlet Port25 Apparent Power | RO | 4 bytes | Unit:0.1
8242 | Slave04 Outlet Port26 Apparent Power | RO | 4 bytes | Unit:0.1
8244 | Slave04 Outlet Port27 Apparent Power | RO | 4 bytes | Unit:0.1
8246 | Slave04 Outlet Port28 Apparent Power | RO | 4 bytes | Unit:0.1
8248 | Slave04 Outlet Port29 Apparent Power | RO | 4 bytes | Unit:0.1
8250 | Slave04 Outlet Port30 Apparent Power | RO | 4 bytes | Unit:0.1
8252 | Slave04 Outlet Port31 Apparent Power | RO | 4 bytes | Unit:0.1
8254 | Slave04 Outlet Port32 Apparent Power | RO | 4 bytes | Unit:0.1
8256 | Slave04 Outlet Port33 Apparent Power | RO | 4 bytes | Unit:0.1
8258 | Slave04 Outlet Port34 Apparent Power | RO | 4 bytes | Unit:0.1
8260 | Slave04 Outlet Port35 Apparent Power | RO | 4 bytes | Unit:0.1
8262 | Slave04 Outlet Port36 Apparent Power | RO | 4 bytes | Unit:0.1
8264 | Slave04 Outlet Port37 Apparent Power | RO | 4 bytes | Unit:0.1
8266 | Slave04 Outlet Port38 Apparent Power | RO | 4 bytes | Unit:0.1
8268 | Slave04 Outlet Port39 Apparent Power | RO | 4 bytes | Unit:0.1
8270 | Slave04 Outlet Port40 Apparent Power | RO | 4 bytes | Unit:0.1
8272 | Slave04 Outlet Port41 Apparent Power | RO | 4 bytes | Unit:0.1
8274 | Slave04 Outlet Port42 Apparent Power | RO | 4 bytes | Unit:0.1
8276 | Slave05 Outlet Port01 Apparent Power | RO | 4 bytes | Unit:0.1
8278 | Slave05 Outlet Port02 Apparent Power | RO | 4 bytes | Unit:0.1
8280 | Slave05 Outlet Port03 Apparent Power | RO | 4 bytes | Unit:0.1
8282 | Slave05 Outlet Port04 Apparent Power | RO | 4 bytes | Unit:0.1
8284 | Slave05 Outlet Port05 Apparent Power | RO | 4 bytes | Unit:0.1
8286 | Slave05 Outlet Port06 Apparent Power | RO | 4 bytes | Unit:0.1
8288 | Slave05 Outlet Port07 Apparent Power | RO | 4 bytes | Unit:0.1
8290 | Slave05 Outlet Port08 Apparent Power | RO | 4 bytes | Unit:0.1
8292 | Slave05 Outlet Port09 Apparent Power | RO | 4 bytes | Unit:0.1
8294 | Slave05 Outlet Port10 Apparent Power | RO | 4 bytes | Unit:0.1
8296 | Slave05 Outlet Port11 Apparent Power | RO | 4 bytes | Unit:0.1
8298 | Slave05 Outlet Port12 Apparent Power | RO | 4 bytes | Unit:0.1
8300 | Slave05 Outlet Port13 Apparent Power | RO | 4 bytes | Unit:0.1
8302 | Slave05 Outlet Port14 Apparent Power | RO | 4 bytes | Unit:0.1
8304 | Slave05 Outlet Port15 Apparent Power | RO | 4 bytes | Unit:0.1
8306 | Slave05 Outlet Port16 Apparent Power | RO | 4 bytes | Unit:0.1
8308 | Slave05 Outlet Port17 Apparent Power | RO | 4 bytes | Unit:0.1
8310 | Slave05 Outlet Port18 Apparent Power | RO | 4 bytes | Unit:0.1
8312 | Slave05 Outlet Port19 Apparent Power | RO | 4 bytes | Unit:0.1
8314 | Slave05 Outlet Port20 Apparent Power | RO | 4 bytes | Unit:0.1
8316 | Slave05 Outlet Port21 Apparent Power | RO | 4 bytes | Unit:0.1
8318 | Slave05 Outlet Port22 Apparent Power | RO | 4 bytes | Unit:0.1
8320 | Slave05 Outlet Port23 Apparent Power | RO | 4 bytes | Unit:0.1
8322 | Slave05 Outlet Port24 Apparent Power | RO | 4 bytes | Unit:0.1
8324 | Slave05 Outlet Port25 Apparent Power | RO | 4 bytes | Unit:0.1
8326 | Slave05 Outlet Port26 Apparent Power | RO | 4 bytes | Unit:0.1
8328 | Slave05 Outlet Port27 Apparent Power | RO | 4 bytes | Unit:0.1
8330 | Slave05 Outlet Port28 Apparent Power | RO | 4 bytes | Unit:0.1
8332 | Slave05 Outlet Port29 Apparent Power | RO | 4 bytes | Unit:0.1
8334 | Slave05 Outlet Port30 Apparent Power | RO | 4 bytes | Unit:0.1
8336 | Slave05 Outlet Port31 Apparent Power | RO | 4 bytes | Unit:0.1
8338 | Slave05 Outlet Port32 Apparent Power | RO | 4 bytes | Unit:0.1
8340 | Slave05 Outlet Port33 Apparent Power | RO | 4 bytes | Unit:0.1
8342 | Slave05 Outlet Port34 Apparent Power | RO | 4 bytes | Unit:0.1
8344 | Slave05 Outlet Port35 Apparent Power | RO | 4 bytes | Unit:0.1
8346 | Slave05 Outlet Port36 Apparent Power | RO | 4 bytes | Unit:0.1
8348 | Slave05 Outlet Port37 Apparent Power | RO | 4 bytes | Unit:0.1
8350 | Slave05 Outlet Port38 Apparent Power | RO | 4 bytes | Unit:0.1
8352 | Slave05 Outlet Port39 Apparent Power | RO | 4 bytes | Unit:0.1
8354 | Slave05 Outlet Port40 Apparent Power | RO | 4 bytes | Unit:0.1
8356 | Slave05 Outlet Port41 Apparent Power | RO | 4 bytes | Unit:0.1
8358 | Slave05 Outlet Port42 Apparent Power | RO | 4 bytes | Unit:0.1
8360 | Slave06 Outlet Port01 Apparent Power | RO | 4 bytes | Unit:0.1
8362 | Slave06 Outlet Port02 Apparent Power | RO | 4 bytes | Unit:0.1
8364 | Slave06 Outlet Port03 Apparent Power | RO | 4 bytes | Unit:0.1
8366 | Slave06 Outlet Port04 Apparent Power | RO | 4 bytes | Unit:0.1
8368 | Slave06 Outlet Port05 Apparent Power | RO | 4 bytes | Unit:0.1
8370 | Slave06 Outlet Port06 Apparent Power | RO | 4 bytes | Unit:0.1
8372 | Slave06 Outlet Port07 Apparent Power | RO | 4 bytes | Unit:0.1
8374 | Slave06 Outlet Port08 Apparent Power | RO | 4 bytes | Unit:0.1
8376 | Slave06 Outlet Port09 Apparent Power | RO | 4 bytes | Unit:0.1
8378 | Slave06 Outlet Port10 Apparent Power | RO | 4 bytes | Unit:0.1
8380 | Slave06 Outlet Port11 Apparent Power | RO | 4 bytes | Unit:0.1
8382 | Slave06 Outlet Port12 Apparent Power | RO | 4 bytes | Unit:0.1
8384 | Slave06 Outlet Port13 Apparent Power | RO | 4 bytes | Unit:0.1
8386 | Slave06 Outlet Port14 Apparent Power | RO | 4 bytes | Unit:0.1
8388 | Slave06 Outlet Port15 Apparent Power | RO | 4 bytes | Unit:0.1
8390 | Slave06 Outlet Port16 Apparent Power | RO | 4 bytes | Unit:0.1
8392 | Slave06 Outlet Port17 Apparent Power | RO | 4 bytes | Unit:0.1
8394 | Slave06 Outlet Port18 Apparent Power | RO | 4 bytes | Unit:0.1
8396 | Slave06 Outlet Port19 Apparent Power | RO | 4 bytes | Unit:0.1
8398 | Slave06 Outlet Port20 Apparent Power | RO | 4 bytes | Unit:0.1
8400 | Slave06 Outlet Port21 Apparent Power | RO | 4 bytes | Unit:0.1
8402 | Slave06 Outlet Port22 Apparent Power | RO | 4 bytes | Unit:0.1
8404 | Slave06 Outlet Port23 Apparent Power | RO | 4 bytes | Unit:0.1
8406 | Slave06 Outlet Port24 Apparent Power | RO | 4 bytes | Unit:0.1
8408 | Slave06 Outlet Port25 Apparent Power | RO | 4 bytes | Unit:0.1
8410 | Slave06 Outlet Port26 Apparent Power | RO | 4 bytes | Unit:0.1
8412 | Slave06 Outlet Port27 Apparent Power | RO | 4 bytes | Unit:0.1
8414 | Slave06 Outlet Port28 Apparent Power | RO | 4 bytes | Unit:0.1
8416 | Slave06 Outlet Port29 Apparent Power | RO | 4 bytes | Unit:0.1
8418 | Slave06 Outlet Port30 Apparent Power | RO | 4 bytes | Unit:0.1
8420 | Slave06 Outlet Port31 Apparent Power | RO | 4 bytes | Unit:0.1
8422 | Slave06 Outlet Port32 Apparent Power | RO | 4 bytes | Unit:0.1
8424 | Slave06 Outlet Port33 Apparent Power | RO | 4 bytes | Unit:0.1
8426 | Slave06 Outlet Port34 Apparent Power | RO | 4 bytes | Unit:0.1
8428 | Slave06 Outlet Port35 Apparent Power | RO | 4 bytes | Unit:0.1
8430 | Slave06 Outlet Port36 Apparent Power | RO | 4 bytes | Unit:0.1
8432 | Slave06 Outlet Port37 Apparent Power | RO | 4 bytes | Unit:0.1
8434 | Slave06 Outlet Port38 Apparent Power | RO | 4 bytes | Unit:0.1
8436 | Slave06 Outlet Port39 Apparent Power | RO | 4 bytes | Unit:0.1
8438 | Slave06 Outlet Port40 Apparent Power | RO | 4 bytes | Unit:0.1
8440 | Slave06 Outlet Port41 Apparent Power | RO | 4 bytes | Unit:0.1
8442 | Slave06 Outlet Port42 Apparent Power | RO | 4 bytes | Unit:0.1
8444 | Slave07 Outlet Port01 Apparent Power | RO | 4 bytes | Unit:0.1
8446 | Slave07 Outlet Port02 Apparent Power | RO | 4 bytes | Unit:0.1
8448 | Slave07 Outlet Port03 Apparent Power | RO | 4 bytes | Unit:0.1
8450 | Slave07 Outlet Port04 Apparent Power | RO | 4 bytes | Unit:0.1
8452 | Slave07 Outlet Port05 Apparent Power | RO | 4 bytes | Unit:0.1
8454 | Slave07 Outlet Port06 Apparent Power | RO | 4 bytes | Unit:0.1
8456 | Slave07 Outlet Port07 Apparent Power | RO | 4 bytes | Unit:0.1
8458 | Slave07 Outlet Port08 Apparent Power | RO | 4 bytes | Unit:0.1
8460 | Slave07 Outlet Port09 Apparent Power | RO | 4 bytes | Unit:0.1
8462 | Slave07 Outlet Port10 Apparent Power | RO | 4 bytes | Unit:0.1
8464 | Slave07 Outlet Port11 Apparent Power | RO | 4 bytes | Unit:0.1
8466 | Slave07 Outlet Port12 Apparent Power | RO | 4 bytes | Unit:0.1
8468 | Slave07 Outlet Port13 Apparent Power | RO | 4 bytes | Unit:0.1
8470 | Slave07 Outlet Port14 Apparent Power | RO | 4 bytes | Unit:0.1
8472 | Slave07 Outlet Port15 Apparent Power | RO | 4 bytes | Unit:0.1
8474 | Slave07 Outlet Port16 Apparent Power | RO | 4 bytes | Unit:0.1
8476 | Slave07 Outlet Port17 Apparent Power | RO | 4 bytes | Unit:0.1
8478 | Slave07 Outlet Port18 Apparent Power | RO | 4 bytes | Unit:0.1
8480 | Slave07 Outlet Port19 Apparent Power | RO | 4 bytes | Unit:0.1
8482 | Slave07 Outlet Port20 Apparent Power | RO | 4 bytes | Unit:0.1
8484 | Slave07 Outlet Port21 Apparent Power | RO | 4 bytes | Unit:0.1
8486 | Slave07 Outlet Port22 Apparent Power | RO | 4 bytes | Unit:0.1
8488 | Slave07 Outlet Port23 Apparent Power | RO | 4 bytes | Unit:0.1
8490 | Slave07 Outlet Port24 Apparent Power | RO | 4 bytes | Unit:0.1
8492 | Slave07 Outlet Port25 Apparent Power | RO | 4 bytes | Unit:0.1
8494 | Slave07 Outlet Port26 Apparent Power | RO | 4 bytes | Unit:0.1
8496 | Slave07 Outlet Port27 Apparent Power | RO | 4 bytes | Unit:0.1
8498 | Slave07 Outlet Port28 Apparent Power | RO | 4 bytes | Unit:0.1
8500 | Slave07 Outlet Port29 Apparent Power | RO | 4 bytes | Unit:0.1
8502 | Slave07 Outlet Port30 Apparent Power | RO | 4 bytes | Unit:0.1
8504 | Slave07 Outlet Port31 Apparent Power | RO | 4 bytes | Unit:0.1
8506 | Slave07 Outlet Port32 Apparent Power | RO | 4 bytes | Unit:0.1
8508 | Slave07 Outlet Port33 Apparent Power | RO | 4 bytes | Unit:0.1
8510 | Slave07 Outlet Port34 Apparent Power | RO | 4 bytes | Unit:0.1
8512 | Slave07 Outlet Port35 Apparent Power | RO | 4 bytes | Unit:0.1
8514 | Slave07 Outlet Port36 Apparent Power | RO | 4 bytes | Unit:0.1
8516 | Slave07 Outlet Port37 Apparent Power | RO | 4 bytes | Unit:0.1
8518 | Slave07 Outlet Port38 Apparent Power | RO | 4 bytes | Unit:0.1
8520 | Slave07 Outlet Port39 Apparent Power | RO | 4 bytes | Unit:0.1
8522 | Slave07 Outlet Port40 Apparent Power | RO | 4 bytes | Unit:0.1
8524 | Slave07 Outlet Port41 Apparent Power | RO | 4 bytes | Unit:0.1
8526 | Slave07 Outlet Port42 Apparent Power | RO | 4 bytes | Unit:0.1
8528 | Slave08 Outlet Port01 Apparent Power | RO | 4 bytes | Unit:0.1
8530 | Slave08 Outlet Port02 Apparent Power | RO | 4 bytes | Unit:0.1
8532 | Slave08 Outlet Port03 Apparent Power | RO | 4 bytes | Unit:0.1
8534 | Slave08 Outlet Port04 Apparent Power | RO | 4 bytes | Unit:0.1
8536 | Slave08 Outlet Port05 Apparent Power | RO | 4 bytes | Unit:0.1
8538 | Slave08 Outlet Port06 Apparent Power | RO | 4 bytes | Unit:0.1
8540 | Slave08 Outlet Port07 Apparent Power | RO | 4 bytes | Unit:0.1
8542 | Slave08 Outlet Port08 Apparent Power | RO | 4 bytes | Unit:0.1
8544 | Slave08 Outlet Port09 Apparent Power | RO | 4 bytes | Unit:0.1
8546 | Slave08 Outlet Port10 Apparent Power | RO | 4 bytes | Unit:0.1
8548 | Slave08 Outlet Port11 Apparent Power | RO | 4 bytes | Unit:0.1
8550 | Slave08 Outlet Port12 Apparent Power | RO | 4 bytes | Unit:0.1
8552 | Slave08 Outlet Port13 Apparent Power | RO | 4 bytes | Unit:0.1
8554 | Slave08 Outlet Port14 Apparent Power | RO | 4 bytes | Unit:0.1
8556 | Slave08 Outlet Port15 Apparent Power | RO | 4 bytes | Unit:0.1
8558 | Slave08 Outlet Port16 Apparent Power | RO | 4 bytes | Unit:0.1
8560 | Slave08 Outlet Port17 Apparent Power | RO | 4 bytes | Unit:0.1
8562 | Slave08 Outlet Port18 Apparent Power | RO | 4 bytes | Unit:0.1
8564 | Slave08 Outlet Port19 Apparent Power | RO | 4 bytes | Unit:0.1
8566 | Slave08 Outlet Port20 Apparent Power | RO | 4 bytes | Unit:0.1
8568 | Slave08 Outlet Port21 Apparent Power | RO | 4 bytes | Unit:0.1
8570 | Slave08 Outlet Port22 Apparent Power | RO | 4 bytes | Unit:0.1
8572 | Slave08 Outlet Port23 Apparent Power | RO | 4 bytes | Unit:0.1
8574 | Slave08 Outlet Port24 Apparent Power | RO | 4 bytes | Unit:0.1
8576 | Slave08 Outlet Port25 Apparent Power | RO | 4 bytes | Unit:0.1
8578 | Slave08 Outlet Port26 Apparent Power | RO | 4 bytes | Unit:0.1
8580 | Slave08 Outlet Port27 Apparent Power | RO | 4 bytes | Unit:0.1
8582 | Slave08 Outlet Port28 Apparent Power | RO | 4 bytes | Unit:0.1
8584 | Slave08 Outlet Port29 Apparent Power | RO | 4 bytes | Unit:0.1
8586 | Slave08 Outlet Port30 Apparent Power | RO | 4 bytes | Unit:0.1
8588 | Slave08 Outlet Port31 Apparent Power | RO | 4 bytes | Unit:0.1
8590 | Slave08 Outlet Port32 Apparent Power | RO | 4 bytes | Unit:0.1
8592 | Slave08 Outlet Port33 Apparent Power | RO | 4 bytes | Unit:0.1
8594 | Slave08 Outlet Port34 Apparent Power | RO | 4 bytes | Unit:0.1
8596 | Slave08 Outlet Port35 Apparent Power | RO | 4 bytes | Unit:0.1
8598 | Slave08 Outlet Port36 Apparent Power | RO | 4 bytes | Unit:0.1
8600 | Slave08 Outlet Port37 Apparent Power | RO | 4 bytes | Unit:0.1
8602 | Slave08 Outlet Port38 Apparent Power | RO | 4 bytes | Unit:0.1
8604 | Slave08 Outlet Port39 Apparent Power | RO | 4 bytes | Unit:0.1
8606 | Slave08 Outlet Port40 Apparent Power | RO | 4 bytes | Unit:0.1
8608 | Slave08 Outlet Port41 Apparent Power | RO | 4 bytes | Unit:0.1
8610 | Slave08 Outlet Port42 Apparent Power | RO | 4 bytes | Unit:0.1
8612 | Slave09 Outlet Port01 Apparent Power | RO | 4 bytes | Unit:0.1
8614 | Slave09 Outlet Port02 Apparent Power | RO | 4 bytes | Unit:0.1
8616 | Slave09 Outlet Port03 Apparent Power | RO | 4 bytes | Unit:0.1
8618 | Slave09 Outlet Port04 Apparent Power | RO | 4 bytes | Unit:0.1
8620 | Slave09 Outlet Port05 Apparent Power | RO | 4 bytes | Unit:0.1
8622 | Slave09 Outlet Port06 Apparent Power | RO | 4 bytes | Unit:0.1
8624 | Slave09 Outlet Port07 Apparent Power | RO | 4 bytes | Unit:0.1
8626 | Slave09 Outlet Port08 Apparent Power | RO | 4 bytes | Unit:0.1
8628 | Slave09 Outlet Port09 Apparent Power | RO | 4 bytes | Unit:0.1
8630 | Slave09 Outlet Port10 Apparent Power | RO | 4 bytes | Unit:0.1
8632 | Slave09 Outlet Port11 Apparent Power | RO | 4 bytes | Unit:0.1
8634 | Slave09 Outlet Port12 Apparent Power | RO | 4 bytes | Unit:0.1
8636 | Slave09 Outlet Port13 Apparent Power | RO | 4 bytes | Unit:0.1
8638 | Slave09 Outlet Port14 Apparent Power | RO | 4 bytes | Unit:0.1
8640 | Slave09 Outlet Port15 Apparent Power | RO | 4 bytes | Unit:0.1
8642 | Slave09 Outlet Port16 Apparent Power | RO | 4 bytes | Unit:0.1
8644 | Slave09 Outlet Port17 Apparent Power | RO | 4 bytes | Unit:0.1
8646 | Slave09 Outlet Port18 Apparent Power | RO | 4 bytes | Unit:0.1
8648 | Slave09 Outlet Port19 Apparent Power | RO | 4 bytes | Unit:0.1
8650 | Slave09 Outlet Port20 Apparent Power | RO | 4 bytes | Unit:0.1
8652 | Slave09 Outlet Port21 Apparent Power | RO | 4 bytes | Unit:0.1
8654 | Slave09 Outlet Port22 Apparent Power | RO | 4 bytes | Unit:0.1
8656 | Slave09 Outlet Port23 Apparent Power | RO | 4 bytes | Unit:0.1
8658 | Slave09 Outlet Port24 Apparent Power | RO | 4 bytes | Unit:0.1
8660 | Slave09 Outlet Port25 Apparent Power | RO | 4 bytes | Unit:0.1
8662 | Slave09 Outlet Port26 Apparent Power | RO | 4 bytes | Unit:0.1
8664 | Slave09 Outlet Port27 Apparent Power | RO | 4 bytes | Unit:0.1
8666 | Slave09 Outlet Port28 Apparent Power | RO | 4 bytes | Unit:0.1
8668 | Slave09 Outlet Port29 Apparent Power | RO | 4 bytes | Unit:0.1
8670 | Slave09 Outlet Port30 Apparent Power | RO | 4 bytes | Unit:0.1
8672 | Slave09 Outlet Port31 Apparent Power | RO | 4 bytes | Unit:0.1
8674 | Slave09 Outlet Port32 Apparent Power | RO | 4 bytes | Unit:0.1
8676 | Slave09 Outlet Port33 Apparent Power | RO | 4 bytes | Unit:0.1
8678 | Slave09 Outlet Port34 Apparent Power | RO | 4 bytes | Unit:0.1
8680 | Slave09 Outlet Port35 Apparent Power | RO | 4 bytes | Unit:0.1
8682 | Slave09 Outlet Port36 Apparent Power | RO | 4 bytes | Unit:0.1
8684 | Slave09 Outlet Port37 Apparent Power | RO | 4 bytes | Unit:0.1
8686 | Slave09 Outlet Port38 Apparent Power | RO | 4 bytes | Unit:0.1
8688 | Slave09 Outlet Port39 Apparent Power | RO | 4 bytes | Unit:0.1
8690 | Slave09 Outlet Port40 Apparent Power | RO | 4 bytes | Unit:0.1
8692 | Slave09 Outlet Port41 Apparent Power | RO | 4 bytes | Unit:0.1
8694 | Slave09 Outlet Port42 Apparent Power | RO | 4 bytes | Unit:0.1
8696 | Slave10 Outlet Port01 Apparent Power | RO | 4 bytes | Unit:0.1
8698 | Slave10 Outlet Port02 Apparent Power | RO | 4 bytes | Unit:0.1
8700 | Slave10 Outlet Port03 Apparent Power | RO | 4 bytes | Unit:0.1
8702 | Slave10 Outlet Port04 Apparent Power | RO | 4 bytes | Unit:0.1
8704 | Slave10 Outlet Port05 Apparent Power | RO | 4 bytes | Unit:0.1
8706 | Slave10 Outlet Port06 Apparent Power | RO | 4 bytes | Unit:0.1
8708 | Slave10 Outlet Port07 Apparent Power | RO | 4 bytes | Unit:0.1
8710 | Slave10 Outlet Port08 Apparent Power | RO | 4 bytes | Unit:0.1
8712 | Slave10 Outlet Port09 Apparent Power | RO | 4 bytes | Unit:0.1
8714 | Slave10 Outlet Port10 Apparent Power | RO | 4 bytes | Unit:0.1
8716 | Slave10 Outlet Port11 Apparent Power | RO | 4 bytes | Unit:0.1
8718 | Slave10 Outlet Port12 Apparent Power | RO | 4 bytes | Unit:0.1
8720 | Slave10 Outlet Port13 Apparent Power | RO | 4 bytes | Unit:0.1
8722 | Slave10 Outlet Port14 Apparent Power | RO | 4 bytes | Unit:0.1
8724 | Slave10 Outlet Port15 Apparent Power | RO | 4 bytes | Unit:0.1
8726 | Slave10 Outlet Port16 Apparent Power | RO | 4 bytes | Unit:0.1
8728 | Slave10 Outlet Port17 Apparent Power | RO | 4 bytes | Unit:0.1
8730 | Slave10 Outlet Port18 Apparent Power | RO | 4 bytes | Unit:0.1
8732 | Slave10 Outlet Port19 Apparent Power | RO | 4 bytes | Unit:0.1
8734 | Slave10 Outlet Port20 Apparent Power | RO | 4 bytes | Unit:0.1
8736 | Slave10 Outlet Port21 Apparent Power | RO | 4 bytes | Unit:0.1
8738 | Slave10 Outlet Port22 Apparent Power | RO | 4 bytes | Unit:0.1
8740 | Slave10 Outlet Port23 Apparent Power | RO | 4 bytes | Unit:0.1
8742 | Slave10 Outlet Port24 Apparent Power | RO | 4 bytes | Unit:0.1
8744 | Slave10 Outlet Port25 Apparent Power | RO | 4 bytes | Unit:0.1
8746 | Slave10 Outlet Port26 Apparent Power | RO | 4 bytes | Unit:0.1
8748 | Slave10 Outlet Port27 Apparent Power | RO | 4 bytes | Unit:0.1
8750 | Slave10 Outlet Port28 Apparent Power | RO | 4 bytes | Unit:0.1
8752 | Slave10 Outlet Port29 Apparent Power | RO | 4 bytes | Unit:0.1
8754 | Slave10 Outlet Port30 Apparent Power | RO | 4 bytes | Unit:0.1
8756 | Slave10 Outlet Port31 Apparent Power | RO | 4 bytes | Unit:0.1
8758 | Slave10 Outlet Port32 Apparent Power | RO | 4 bytes | Unit:0.1
8760 | Slave10 Outlet Port33 Apparent Power | RO | 4 bytes | Unit:0.1
8762 | Slave10 Outlet Port34 Apparent Power | RO | 4 bytes | Unit:0.1
8764 | Slave10 Outlet Port35 Apparent Power | RO | 4 bytes | Unit:0.1
8766 | Slave10 Outlet Port36 Apparent Power | RO | 4 bytes | Unit:0.1
8768 | Slave10 Outlet Port37 Apparent Power | RO | 4 bytes | Unit:0.1
8770 | Slave10 Outlet Port38 Apparent Power | RO | 4 bytes | Unit:0.1
8772 | Slave10 Outlet Port39 Apparent Power | RO | 4 bytes | Unit:0.1
8774 | Slave10 Outlet Port40 Apparent Power | RO | 4 bytes | Unit:0.1
8776 | Slave10 Outlet Port41 Apparent Power | RO | 4 bytes | Unit:0.1
8778 | Slave10 Outlet Port42 Apparent Power | RO | 4 bytes | Unit:0.1
8780 | Slave11 Outlet Port01 Apparent Power | RO | 4 bytes | Unit:0.1
8782 | Slave11 Outlet Port02 Apparent Power | RO | 4 bytes | Unit:0.1
8784 | Slave11 Outlet Port03 Apparent Power | RO | 4 bytes | Unit:0.1
8786 | Slave11 Outlet Port04 Apparent Power | RO | 4 bytes | Unit:0.1
8788 | Slave11 Outlet Port05 Apparent Power | RO | 4 bytes | Unit:0.1
8790 | Slave11 Outlet Port06 Apparent Power | RO | 4 bytes | Unit:0.1
8792 | Slave11 Outlet Port07 Apparent Power | RO | 4 bytes | Unit:0.1
8794 | Slave11 Outlet Port08 Apparent Power | RO | 4 bytes | Unit:0.1
8796 | Slave11 Outlet Port09 Apparent Power | RO | 4 bytes | Unit:0.1
8798 | Slave11 Outlet Port10 Apparent Power | RO | 4 bytes | Unit:0.1
8800 | Slave11 Outlet Port11 Apparent Power | RO | 4 bytes | Unit:0.1
8802 | Slave11 Outlet Port12 Apparent Power | RO | 4 bytes | Unit:0.1
8804 | Slave11 Outlet Port13 Apparent Power | RO | 4 bytes | Unit:0.1
8806 | Slave11 Outlet Port14 Apparent Power | RO | 4 bytes | Unit:0.1
8808 | Slave11 Outlet Port15 Apparent Power | RO | 4 bytes | Unit:0.1
8810 | Slave11 Outlet Port16 Apparent Power | RO | 4 bytes | Unit:0.1
8812 | Slave11 Outlet Port17 Apparent Power | RO | 4 bytes | Unit:0.1
8814 | Slave11 Outlet Port18 Apparent Power | RO | 4 bytes | Unit:0.1
8816 | Slave11 Outlet Port19 Apparent Power | RO | 4 bytes | Unit:0.1
8818 | Slave11 Outlet Port20 Apparent Power | RO | 4 bytes | Unit:0.1
8820 | Slave11 Outlet Port21 Apparent Power | RO | 4 bytes | Unit:0.1
8822 | Slave11 Outlet Port22 Apparent Power | RO | 4 bytes | Unit:0.1
8824 | Slave11 Outlet Port23 Apparent Power | RO | 4 bytes | Unit:0.1
8826 | Slave11 Outlet Port24 Apparent Power | RO | 4 bytes | Unit:0.1
8828 | Slave11 Outlet Port25 Apparent Power | RO | 4 bytes | Unit:0.1
8830 | Slave11 Outlet Port26 Apparent Power | RO | 4 bytes | Unit:0.1
8832 | Slave11 Outlet Port27 Apparent Power | RO | 4 bytes | Unit:0.1
8834 | Slave11 Outlet Port28 Apparent Power | RO | 4 bytes | Unit:0.1
8836 | Slave11 Outlet Port29 Apparent Power | RO | 4 bytes | Unit:0.1
8838 | Slave11 Outlet Port30 Apparent Power | RO | 4 bytes | Unit:0.1
8840 | Slave11 Outlet Port31 Apparent Power | RO | 4 bytes | Unit:0.1
8842 | Slave11 Outlet Port32 Apparent Power | RO | 4 bytes | Unit:0.1
8844 | Slave11 Outlet Port33 Apparent Power | RO | 4 bytes | Unit:0.1
8846 | Slave11 Outlet Port34 Apparent Power | RO | 4 bytes | Unit:0.1
8848 | Slave11 Outlet Port35 Apparent Power | RO | 4 bytes | Unit:0.1
8850 | Slave11 Outlet Port36 Apparent Power | RO | 4 bytes | Unit:0.1
8852 | Slave11 Outlet Port37 Apparent Power | RO | 4 bytes | Unit:0.1
8854 | Slave11 Outlet Port38 Apparent Power | RO | 4 bytes | Unit:0.1
8856 | Slave11 Outlet Port39 Apparent Power | RO | 4 bytes | Unit:0.1
8858 | Slave11 Outlet Port40 Apparent Power | RO | 4 bytes | Unit:0.1
8860 | Slave11 Outlet Port41 Apparent Power | RO | 4 bytes | Unit:0.1
8862 | Slave11 Outlet Port42 Apparent Power | RO | 4 bytes | Unit:0.1
8864 | Slave12 Outlet Port01 Apparent Power | RO | 4 bytes | Unit:0.1
8866 | Slave12 Outlet Port02 Apparent Power | RO | 4 bytes | Unit:0.1
8868 | Slave12 Outlet Port03 Apparent Power | RO | 4 bytes | Unit:0.1
8870 | Slave12 Outlet Port04 Apparent Power | RO | 4 bytes | Unit:0.1
8872 | Slave12 Outlet Port05 Apparent Power | RO | 4 bytes | Unit:0.1
8874 | Slave12 Outlet Port06 Apparent Power | RO | 4 bytes | Unit:0.1
8876 | Slave12 Outlet Port07 Apparent Power | RO | 4 bytes | Unit:0.1
8878 | Slave12 Outlet Port08 Apparent Power | RO | 4 bytes | Unit:0.1
8880 | Slave12 Outlet Port09 Apparent Power | RO | 4 bytes | Unit:0.1
8882 | Slave12 Outlet Port10 Apparent Power | RO | 4 bytes | Unit:0.1
8884 | Slave12 Outlet Port11 Apparent Power | RO | 4 bytes | Unit:0.1
8886 | Slave12 Outlet Port12 Apparent Power | RO | 4 bytes | Unit:0.1
8888 | Slave12 Outlet Port13 Apparent Power | RO | 4 bytes | Unit:0.1
8890 | Slave12 Outlet Port14 Apparent Power | RO | 4 bytes | Unit:0.1
8892 | Slave12 Outlet Port15 Apparent Power | RO | 4 bytes | Unit:0.1
8894 | Slave12 Outlet Port16 Apparent Power | RO | 4 bytes | Unit:0.1
8896 | Slave12 Outlet Port17 Apparent Power | RO | 4 bytes | Unit:0.1
8898 | Slave12 Outlet Port18 Apparent Power | RO | 4 bytes | Unit:0.1
8900 | Slave12 Outlet Port19 Apparent Power | RO | 4 bytes | Unit:0.1
8902 | Slave12 Outlet Port20 Apparent Power | RO | 4 bytes | Unit:0.1
8904 | Slave12 Outlet Port21 Apparent Power | RO | 4 bytes | Unit:0.1
8906 | Slave12 Outlet Port22 Apparent Power | RO | 4 bytes | Unit:0.1
8908 | Slave12 Outlet Port23 Apparent Power | RO | 4 bytes | Unit:0.1
8910 | Slave12 Outlet Port24 Apparent Power | RO | 4 bytes | Unit:0.1
8912 | Slave12 Outlet Port25 Apparent Power | RO | 4 bytes | Unit:0.1
8914 | Slave12 Outlet Port26 Apparent Power | RO | 4 bytes | Unit:0.1
8916 | Slave12 Outlet Port27 Apparent Power | RO | 4 bytes | Unit:0.1
8918 | Slave12 Outlet Port28 Apparent Power | RO | 4 bytes | Unit:0.1
8920 | Slave12 Outlet Port29 Apparent Power | RO | 4 bytes | Unit:0.1
8922 | Slave12 Outlet Port30 Apparent Power | RO | 4 bytes | Unit:0.1
8924 | Slave12 Outlet Port31 Apparent Power | RO | 4 bytes | Unit:0.1
8926 | Slave12 Outlet Port32 Apparent Power | RO | 4 bytes | Unit:0.1
8928 | Slave12 Outlet Port33 Apparent Power | RO | 4 bytes | Unit:0.1
8930 | Slave12 Outlet Port34 Apparent Power | RO | 4 bytes | Unit:0.1
8932 | Slave12 Outlet Port35 Apparent Power | RO | 4 bytes | Unit:0.1
8934 | Slave12 Outlet Port36 Apparent Power | RO | 4 bytes | Unit:0.1
8936 | Slave12 Outlet Port37 Apparent Power | RO | 4 bytes | Unit:0.1
8938 | Slave12 Outlet Port38 Apparent Power | RO | 4 bytes | Unit:0.1
8940 | Slave12 Outlet Port39 Apparent Power | RO | 4 bytes | Unit:0.1
8942 | Slave12 Outlet Port40 Apparent Power | RO | 4 bytes | Unit:0.1
8944 | Slave12 Outlet Port41 Apparent Power | RO | 4 bytes | Unit:0.1
8946 | Slave12 Outlet Port42 Apparent Power | RO | 4 bytes | Unit:0.1
8948 | Slave13 Outlet Port01 Apparent Power | RO | 4 bytes | Unit:0.1
8950 | Slave13 Outlet Port02 Apparent Power | RO | 4 bytes | Unit:0.1
8952 | Slave13 Outlet Port03 Apparent Power | RO | 4 bytes | Unit:0.1
8954 | Slave13 Outlet Port04 Apparent Power | RO | 4 bytes | Unit:0.1
8956 | Slave13 Outlet Port05 Apparent Power | RO | 4 bytes | Unit:0.1
8958 | Slave13 Outlet Port06 Apparent Power | RO | 4 bytes | Unit:0.1
8960 | Slave13 Outlet Port07 Apparent Power | RO | 4 bytes | Unit:0.1
8962 | Slave13 Outlet Port08 Apparent Power | RO | 4 bytes | Unit:0.1
8964 | Slave13 Outlet Port09 Apparent Power | RO | 4 bytes | Unit:0.1
8966 | Slave13 Outlet Port10 Apparent Power | RO | 4 bytes | Unit:0.1
8968 | Slave13 Outlet Port11 Apparent Power | RO | 4 bytes | Unit:0.1
8970 | Slave13 Outlet Port12 Apparent Power | RO | 4 bytes | Unit:0.1
8972 | Slave13 Outlet Port13 Apparent Power | RO | 4 bytes | Unit:0.1
8974 | Slave13 Outlet Port14 Apparent Power | RO | 4 bytes | Unit:0.1
8976 | Slave13 Outlet Port15 Apparent Power | RO | 4 bytes | Unit:0.1
8978 | Slave13 Outlet Port16 Apparent Power | RO | 4 bytes | Unit:0.1
8980 | Slave13 Outlet Port17 Apparent Power | RO | 4 bytes | Unit:0.1
8982 | Slave13 Outlet Port18 Apparent Power | RO | 4 bytes | Unit:0.1
8984 | Slave13 Outlet Port19 Apparent Power | RO | 4 bytes | Unit:0.1
8986 | Slave13 Outlet Port20 Apparent Power | RO | 4 bytes | Unit:0.1
8988 | Slave13 Outlet Port21 Apparent Power | RO | 4 bytes | Unit:0.1
8990 | Slave13 Outlet Port22 Apparent Power | RO | 4 bytes | Unit:0.1
8992 | Slave13 Outlet Port23 Apparent Power | RO | 4 bytes | Unit:0.1
8994 | Slave13 Outlet Port24 Apparent Power | RO | 4 bytes | Unit:0.1
8996 | Slave13 Outlet Port25 Apparent Power | RO | 4 bytes | Unit:0.1
8998 | Slave13 Outlet Port26 Apparent Power | RO | 4 bytes | Unit:0.1
9000 | Slave13 Outlet Port27 Apparent Power | RO | 4 bytes | Unit:0.1
9002 | Slave13 Outlet Port28 Apparent Power | RO | 4 bytes | Unit:0.1
9004 | Slave13 Outlet Port29 Apparent Power | RO | 4 bytes | Unit:0.1
9006 | Slave13 Outlet Port30 Apparent Power | RO | 4 bytes | Unit:0.1
9008 | Slave13 Outlet Port31 Apparent Power | RO | 4 bytes | Unit:0.1
9010 | Slave13 Outlet Port32 Apparent Power | RO | 4 bytes | Unit:0.1
9012 | Slave13 Outlet Port33 Apparent Power | RO | 4 bytes | Unit:0.1
9014 | Slave13 Outlet Port34 Apparent Power | RO | 4 bytes | Unit:0.1
9016 | Slave13 Outlet Port35 Apparent Power | RO | 4 bytes | Unit:0.1
9018 | Slave13 Outlet Port36 Apparent Power | RO | 4 bytes | Unit:0.1
9020 | Slave13 Outlet Port37 Apparent Power | RO | 4 bytes | Unit:0.1
9022 | Slave13 Outlet Port38 Apparent Power | RO | 4 bytes | Unit:0.1
9024 | Slave13 Outlet Port39 Apparent Power | RO | 4 bytes | Unit:0.1
9026 | Slave13 Outlet Port40 Apparent Power | RO | 4 bytes | Unit:0.1
9028 | Slave13 Outlet Port41 Apparent Power | RO | 4 bytes | Unit:0.1
9030 | Slave13 Outlet Port42 Apparent Power | RO | 4 bytes | Unit:0.1
9032 | Slave14 Outlet Port01 Apparent Power | RO | 4 bytes | Unit:0.1
9034 | Slave14 Outlet Port02 Apparent Power | RO | 4 bytes | Unit:0.1
9036 | Slave14 Outlet Port03 Apparent Power | RO | 4 bytes | Unit:0.1
9038 | Slave14 Outlet Port04 Apparent Power | RO | 4 bytes | Unit:0.1
9040 | Slave14 Outlet Port05 Apparent Power | RO | 4 bytes | Unit:0.1
9042 | Slave14 Outlet Port06 Apparent Power | RO | 4 bytes | Unit:0.1
9044 | Slave14 Outlet Port07 Apparent Power | RO | 4 bytes | Unit:0.1
9046 | Slave14 Outlet Port08 Apparent Power | RO | 4 bytes | Unit:0.1
9048 | Slave14 Outlet Port09 Apparent Power | RO | 4 bytes | Unit:0.1
9050 | Slave14 Outlet Port10 Apparent Power | RO | 4 bytes | Unit:0.1
9052 | Slave14 Outlet Port11 Apparent Power | RO | 4 bytes | Unit:0.1
9054 | Slave14 Outlet Port12 Apparent Power | RO | 4 bytes | Unit:0.1
9056 | Slave14 Outlet Port13 Apparent Power | RO | 4 bytes | Unit:0.1
9058 | Slave14 Outlet Port14 Apparent Power | RO | 4 bytes | Unit:0.1
9060 | Slave14 Outlet Port15 Apparent Power | RO | 4 bytes | Unit:0.1
9062 | Slave14 Outlet Port16 Apparent Power | RO | 4 bytes | Unit:0.1
9064 | Slave14 Outlet Port17 Apparent Power | RO | 4 bytes | Unit:0.1
9066 | Slave14 Outlet Port18 Apparent Power | RO | 4 bytes | Unit:0.1
9068 | Slave14 Outlet Port19 Apparent Power | RO | 4 bytes | Unit:0.1
9070 | Slave14 Outlet Port20 Apparent Power | RO | 4 bytes | Unit:0.1
9072 | Slave14 Outlet Port21 Apparent Power | RO | 4 bytes | Unit:0.1
9074 | Slave14 Outlet Port22 Apparent Power | RO | 4 bytes | Unit:0.1
9076 | Slave14 Outlet Port23 Apparent Power | RO | 4 bytes | Unit:0.1
9078 | Slave14 Outlet Port24 Apparent Power | RO | 4 bytes | Unit:0.1
9080 | Slave14 Outlet Port25 Apparent Power | RO | 4 bytes | Unit:0.1
9082 | Slave14 Outlet Port26 Apparent Power | RO | 4 bytes | Unit:0.1
9084 | Slave14 Outlet Port27 Apparent Power | RO | 4 bytes | Unit:0.1
9086 | Slave14 Outlet Port28 Apparent Power | RO | 4 bytes | Unit:0.1
9088 | Slave14 Outlet Port29 Apparent Power | RO | 4 bytes | Unit:0.1
9090 | Slave14 Outlet Port30 Apparent Power | RO | 4 bytes | Unit:0.1
9092 | Slave14 Outlet Port31 Apparent Power | RO | 4 bytes | Unit:0.1
9094 | Slave14 Outlet Port32 Apparent Power | RO | 4 bytes | Unit:0.1
9096 | Slave14 Outlet Port33 Apparent Power | RO | 4 bytes | Unit:0.1
9098 | Slave14 Outlet Port34 Apparent Power | RO | 4 bytes | Unit:0.1
9100 | Slave14 Outlet Port35 Apparent Power | RO | 4 bytes | Unit:0.1
9102 | Slave14 Outlet Port36 Apparent Power | RO | 4 bytes | Unit:0.1
9104 | Slave14 Outlet Port37 Apparent Power | RO | 4 bytes | Unit:0.1
9106 | Slave14 Outlet Port38 Apparent Power | RO | 4 bytes | Unit:0.1
9108 | Slave14 Outlet Port39 Apparent Power | RO | 4 bytes | Unit:0.1
9110 | Slave14 Outlet Port40 Apparent Power | RO | 4 bytes | Unit:0.1
9112 | Slave14 Outlet Port41 Apparent Power | RO | 4 bytes | Unit:0.1
9114 | Slave14 Outlet Port42 Apparent Power | RO | 4 bytes | Unit:0.1
9116 | Slave15 Outlet Port01 Apparent Power | RO | 4 bytes | Unit:0.1
9118 | Slave15 Outlet Port02 Apparent Power | RO | 4 bytes | Unit:0.1
9120 | Slave15 Outlet Port03 Apparent Power | RO | 4 bytes | Unit:0.1
9122 | Slave15 Outlet Port04 Apparent Power | RO | 4 bytes | Unit:0.1
9124 | Slave15 Outlet Port05 Apparent Power | RO | 4 bytes | Unit:0.1
9126 | Slave15 Outlet Port06 Apparent Power | RO | 4 bytes | Unit:0.1
9128 | Slave15 Outlet Port07 Apparent Power | RO | 4 bytes | Unit:0.1
9130 | Slave15 Outlet Port08 Apparent Power | RO | 4 bytes | Unit:0.1
9132 | Slave15 Outlet Port09 Apparent Power | RO | 4 bytes | Unit:0.1
9134 | Slave15 Outlet Port10 Apparent Power | RO | 4 bytes | Unit:0.1
9136 | Slave15 Outlet Port11 Apparent Power | RO | 4 bytes | Unit:0.1
9138 | Slave15 Outlet Port12 Apparent Power | RO | 4 bytes | Unit:0.1
9140 | Slave15 Outlet Port13 Apparent Power | RO | 4 bytes | Unit:0.1
9142 | Slave15 Outlet Port14 Apparent Power | RO | 4 bytes | Unit:0.1
9144 | Slave15 Outlet Port15 Apparent Power | RO | 4 bytes | Unit:0.1
9146 | Slave15 Outlet Port16 Apparent Power | RO | 4 bytes | Unit:0.1
9148 | Slave15 Outlet Port17 Apparent Power | RO | 4 bytes | Unit:0.1
9150 | Slave15 Outlet Port18 Apparent Power | RO | 4 bytes | Unit:0.1
9152 | Slave15 Outlet Port19 Apparent Power | RO | 4 bytes | Unit:0.1
9154 | Slave15 Outlet Port20 Apparent Power | RO | 4 bytes | Unit:0.1
9156 | Slave15 Outlet Port21 Apparent Power | RO | 4 bytes | Unit:0.1
9158 | Slave15 Outlet Port22 Apparent Power | RO | 4 bytes | Unit:0.1
9160 | Slave15 Outlet Port23 Apparent Power | RO | 4 bytes | Unit:0.1
9162 | Slave15 Outlet Port24 Apparent Power | RO | 4 bytes | Unit:0.1
9164 | Slave15 Outlet Port25 Apparent Power | RO | 4 bytes | Unit:0.1
9166 | Slave15 Outlet Port26 Apparent Power | RO | 4 bytes | Unit:0.1
9168 | Slave15 Outlet Port27 Apparent Power | RO | 4 bytes | Unit:0.1
9170 | Slave15 Outlet Port28 Apparent Power | RO | 4 bytes | Unit:0.1
9172 | Slave15 Outlet Port29 Apparent Power | RO | 4 bytes | Unit:0.1
9174 | Slave15 Outlet Port30 Apparent Power | RO | 4 bytes | Unit:0.1
9176 | Slave15 Outlet Port31 Apparent Power | RO | 4 bytes | Unit:0.1
9178 | Slave15 Outlet Port32 Apparent Power | RO | 4 bytes | Unit:0.1
9180 | Slave15 Outlet Port33 Apparent Power | RO | 4 bytes | Unit:0.1
9182 | Slave15 Outlet Port34 Apparent Power | RO | 4 bytes | Unit:0.1
9184 | Slave15 Outlet Port35 Apparent Power | RO | 4 bytes | Unit:0.1
9186 | Slave15 Outlet Port36 Apparent Power | RO | 4 bytes | Unit:0.1
9188 | Slave15 Outlet Port37 Apparent Power | RO | 4 bytes | Unit:0.1
9190 | Slave15 Outlet Port38 Apparent Power | RO | 4 bytes | Unit:0.1
9192 | Slave15 Outlet Port39 Apparent Power | RO | 4 bytes | Unit:0.1
9194 | Slave15 Outlet Port40 Apparent Power | RO | 4 bytes | Unit:0.1
9196 | Slave15 Outlet Port41 Apparent Power | RO | 4 bytes | Unit:0.1
9198 | Slave15 Outlet Port42 Apparent Power | RO | 4 bytes | Unit:0.1
9200 | Master Outlet Port01 Energy | RO | 4 bytes | Unit:0.001KW
9202 | Master Outlet Port02 Energy | RO | 4 bytes | Unit:0.001KW
9204 | Master Outlet Port03 Energy | RO | 4 bytes | Unit:0.001KW
9206 | Master Outlet Port04 Energy | RO | 4 bytes | Unit:0.001KW
9208 | Master Outlet Port05 Energy | RO | 4 bytes | Unit:0.001KW
9210 | Master Outlet Port06 Energy | RO | 4 bytes | Unit:0.001KW
9212 | Master Outlet Port07 Energy | RO | 4 bytes | Unit:0.001KW
9214 | Master Outlet Port08 Energy | RO | 4 bytes | Unit:0.001KW
9216 | Master Outlet Port09 Energy | RO | 4 bytes | Unit:0.001KW
9218 | Master Outlet Port10 Energy | RO | 4 bytes | Unit:0.001KW
9220 | Master Outlet Port11 Energy | RO | 4 bytes | Unit:0.001KW
9222 | Master Outlet Port12 Energy | RO | 4 bytes | Unit:0.001KW
9224 | Master Outlet Port13 Energy | RO | 4 bytes | Unit:0.001KW
9226 | Master Outlet Port14 Energy | RO | 4 bytes | Unit:0.001KW
9228 | Master Outlet Port15 Energy | RO | 4 bytes | Unit:0.001KW
9230 | Master Outlet Port16 Energy | RO | 4 bytes | Unit:0.001KW
9232 | Master Outlet Port17 Energy | RO | 4 bytes | Unit:0.001KW
9234 | Master Outlet Port18 Energy | RO | 4 bytes | Unit:0.001KW
9236 | Master Outlet Port19 Energy | RO | 4 bytes | Unit:0.001KW
9238 | Master Outlet Port20 Energy | RO | 4 bytes | Unit:0.001KW
9240 | Master Outlet Port21 Energy | RO | 4 bytes | Unit:0.001KW
9242 | Master Outlet Port22 Energy | RO | 4 bytes | Unit:0.001KW
9244 | Master Outlet Port23 Energy | RO | 4 bytes | Unit:0.001KW
9246 | Master Outlet Port24 Energy | RO | 4 bytes | Unit:0.001KW
9248 | Master Outlet Port25 Energy | RO | 4 bytes | Unit:0.001KW
9250 | Master Outlet Port26 Energy | RO | 4 bytes | Unit:0.001KW
9252 | Master Outlet Port27 Energy | RO | 4 bytes | Unit:0.001KW
9254 | Master Outlet Port28 Energy | RO | 4 bytes | Unit:0.001KW
9256 | Master Outlet Port29 Energy | RO | 4 bytes | Unit:0.001KW
9258 | Master Outlet Port30 Energy | RO | 4 bytes | Unit:0.001KW
9260 | Master Outlet Port31 Energy | RO | 4 bytes | Unit:0.001KW
9262 | Master Outlet Port32 Energy | RO | 4 bytes | Unit:0.001KW
9264 | Master Outlet Port33 Energy | RO | 4 bytes | Unit:0.001KW
9266 | Master Outlet Port34 Energy | RO | 4 bytes | Unit:0.001KW
9268 | Master Outlet Port35 Energy | RO | 4 bytes | Unit:0.001KW
9270 | Master Outlet Port36 Energy | RO | 4 bytes | Unit:0.001KW
9272 | Master Outlet Port37 Energy | RO | 4 bytes | Unit:0.001KW
9274 | Master Outlet Port38 Energy | RO | 4 bytes | Unit:0.001KW
9276 | Master Outlet Port39 Energy | RO | 4 bytes | Unit:0.001KW
9278 | Master Outlet Port40 Energy | RO | 4 bytes | Unit:0.001KW
9280 | Master Outlet Port41 Energy | RO | 4 bytes | Unit:0.001KW
9282 | Master Outlet Port42 Energy | RO | 4 bytes | Unit:0.001KW
9284 | Slave01 Outlet Port01 Energy | RO | 4 bytes | Unit:0.001KW
9286 | Slave01 Outlet Port02 Energy | RO | 4 bytes | Unit:0.001KW
9288 | Slave01 Outlet Port03 Energy | RO | 4 bytes | Unit:0.001KW
9290 | Slave01 Outlet Port04 Energy | RO | 4 bytes | Unit:0.001KW
9292 | Slave01 Outlet Port05 Energy | RO | 4 bytes | Unit:0.001KW
9294 | Slave01 Outlet Port06 Energy | RO | 4 bytes | Unit:0.001KW
9296 | Slave01 Outlet Port07 Energy | RO | 4 bytes | Unit:0.001KW
9298 | Slave01 Outlet Port08 Energy | RO | 4 bytes | Unit:0.001KW
9300 | Slave01 Outlet Port09 Energy | RO | 4 bytes | Unit:0.001KW
9302 | Slave01 Outlet Port10 Energy | RO | 4 bytes | Unit:0.001KW
9304 | Slave01 Outlet Port11 Energy | RO | 4 bytes | Unit:0.001KW
9306 | Slave01 Outlet Port12 Energy | RO | 4 bytes | Unit:0.001KW
9308 | Slave01 Outlet Port13 Energy | RO | 4 bytes | Unit:0.001KW
9310 | Slave01 Outlet Port14 Energy | RO | 4 bytes | Unit:0.001KW
9312 | Slave01 Outlet Port15 Energy | RO | 4 bytes | Unit:0.001KW
9314 | Slave01 Outlet Port16 Energy | RO | 4 bytes | Unit:0.001KW
9316 | Slave01 Outlet Port17 Energy | RO | 4 bytes | Unit:0.001KW
9318 | Slave01 Outlet Port18 Energy | RO | 4 bytes | Unit:0.001KW
9320 | Slave01 Outlet Port19 Energy | RO | 4 bytes | Unit:0.001KW
9322 | Slave01 Outlet Port20 Energy | RO | 4 bytes | Unit:0.001KW
9324 | Slave01 Outlet Port21 Energy | RO | 4 bytes | Unit:0.001KW
9326 | Slave01 Outlet Port22 Energy | RO | 4 bytes | Unit:0.001KW
9328 | Slave01 Outlet Port23 Energy | RO | 4 bytes | Unit:0.001KW
9330 | Slave01 Outlet Port24 Energy | RO | 4 bytes | Unit:0.001KW
9332 | Slave01 Outlet Port25 Energy | RO | 4 bytes | Unit:0.001KW
9334 | Slave01 Outlet Port26 Energy | RO | 4 bytes | Unit:0.001KW
9336 | Slave01 Outlet Port27 Energy | RO | 4 bytes | Unit:0.001KW
9338 | Slave01 Outlet Port28 Energy | RO | 4 bytes | Unit:0.001KW
9340 | Slave01 Outlet Port29 Energy | RO | 4 bytes | Unit:0.001KW
9342 | Slave01 Outlet Port30 Energy | RO | 4 bytes | Unit:0.001KW
9344 | Slave01 Outlet Port31 Energy | RO | 4 bytes | Unit:0.001KW
9346 | Slave01 Outlet Port32 Energy | RO | 4 bytes | Unit:0.001KW
9348 | Slave01 Outlet Port33 Energy | RO | 4 bytes | Unit:0.001KW
9350 | Slave01 Outlet Port34 Energy | RO | 4 bytes | Unit:0.001KW
9352 | Slave01 Outlet Port35 Energy | RO | 4 bytes | Unit:0.001KW
9354 | Slave01 Outlet Port36 Energy | RO | 4 bytes | Unit:0.001KW
9356 | Slave01 Outlet Port37 Energy | RO | 4 bytes | Unit:0.001KW
9358 | Slave01 Outlet Port38 Energy | RO | 4 bytes | Unit:0.001KW
9360 | Slave01 Outlet Port39 Energy | RO | 4 bytes | Unit:0.001KW
9362 | Slave01 Outlet Port40 Energy | RO | 4 bytes | Unit:0.001KW
9364 | Slave01 Outlet Port41 Energy | RO | 4 bytes | Unit:0.001KW
9366 | Slave01 Outlet Port42 Energy | RO | 4 bytes | Unit:0.001KW
9368 | Slave02 Outlet Port01 Energy | RO | 4 bytes | Unit:0.001KW
9370 | Slave02 Outlet Port02 Energy | RO | 4 bytes | Unit:0.001KW
9372 | Slave02 Outlet Port03 Energy | RO | 4 bytes | Unit:0.001KW
9374 | Slave02 Outlet Port04 Energy | RO | 4 bytes | Unit:0.001KW
9376 | Slave02 Outlet Port05 Energy | RO | 4 bytes | Unit:0.001KW
9378 | Slave02 Outlet Port06 Energy | RO | 4 bytes | Unit:0.001KW
9380 | Slave02 Outlet Port07 Energy | RO | 4 bytes | Unit:0.001KW
9382 | Slave02 Outlet Port08 Energy | RO | 4 bytes | Unit:0.001KW
9384 | Slave02 Outlet Port09 Energy | RO | 4 bytes | Unit:0.001KW
9386 | Slave02 Outlet Port10 Energy | RO | 4 bytes | Unit:0.001KW
9388 | Slave02 Outlet Port11 Energy | RO | 4 bytes | Unit:0.001KW
9390 | Slave02 Outlet Port12 Energy | RO | 4 bytes | Unit:0.001KW
9392 | Slave02 Outlet Port13 Energy | RO | 4 bytes | Unit:0.001KW
9394 | Slave02 Outlet Port14 Energy | RO | 4 bytes | Unit:0.001KW
9396 | Slave02 Outlet Port15 Energy | RO | 4 bytes | Unit:0.001KW
9398 | Slave02 Outlet Port16 Energy | RO | 4 bytes | Unit:0.001KW
9400 | Slave02 Outlet Port17 Energy | RO | 4 bytes | Unit:0.001KW
9402 | Slave02 Outlet Port18 Energy | RO | 4 bytes | Unit:0.001KW
9404 | Slave02 Outlet Port19 Energy | RO | 4 bytes | Unit:0.001KW
9406 | Slave02 Outlet Port20 Energy | RO | 4 bytes | Unit:0.001KW
9408 | Slave02 Outlet Port21 Energy | RO | 4 bytes | Unit:0.001KW
9410 | Slave02 Outlet Port22 Energy | RO | 4 bytes | Unit:0.001KW
9412 | Slave02 Outlet Port23 Energy | RO | 4 bytes | Unit:0.001KW
9414 | Slave02 Outlet Port24 Energy | RO | 4 bytes | Unit:0.001KW
9416 | Slave02 Outlet Port25 Energy | RO | 4 bytes | Unit:0.001KW
9418 | Slave02 Outlet Port26 Energy | RO | 4 bytes | Unit:0.001KW
9420 | Slave02 Outlet Port27 Energy | RO | 4 bytes | Unit:0.001KW
9422 | Slave02 Outlet Port28 Energy | RO | 4 bytes | Unit:0.001KW
9424 | Slave02 Outlet Port29 Energy | RO | 4 bytes | Unit:0.001KW
9426 | Slave02 Outlet Port30 Energy | RO | 4 bytes | Unit:0.001KW
9428 | Slave02 Outlet Port31 Energy | RO | 4 bytes | Unit:0.001KW
9430 | Slave02 Outlet Port32 Energy | RO | 4 bytes | Unit:0.001KW
9432 | Slave02 Outlet Port33 Energy | RO | 4 bytes | Unit:0.001KW
9434 | Slave02 Outlet Port34 Energy | RO | 4 bytes | Unit:0.001KW
9436 | Slave02 Outlet Port35 Energy | RO | 4 bytes | Unit:0.001KW
9438 | Slave02 Outlet Port36 Energy | RO | 4 bytes | Unit:0.001KW
9440 | Slave02 Outlet Port37 Energy | RO | 4 bytes | Unit:0.001KW
9442 | Slave02 Outlet Port38 Energy | RO | 4 bytes | Unit:0.001KW
9444 | Slave02 Outlet Port39 Energy | RO | 4 bytes | Unit:0.001KW
9446 | Slave02 Outlet Port40 Energy | RO | 4 bytes | Unit:0.001KW
9448 | Slave02 Outlet Port41 Energy | RO | 4 bytes | Unit:0.001KW
9450 | Slave02 Outlet Port42 Energy | RO | 4 bytes | Unit:0.001KW
9452 | Slave03 Outlet Port01 Energy | RO | 4 bytes | Unit:0.001KW
9454 | Slave03 Outlet Port02 Energy | RO | 4 bytes | Unit:0.001KW
9456 | Slave03 Outlet Port03 Energy | RO | 4 bytes | Unit:0.001KW
9458 | Slave03 Outlet Port04 Energy | RO | 4 bytes | Unit:0.001KW
9460 | Slave03 Outlet Port05 Energy | RO | 4 bytes | Unit:0.001KW
9462 | Slave03 Outlet Port06 Energy | RO | 4 bytes | Unit:0.001KW
9464 | Slave03 Outlet Port07 Energy | RO | 4 bytes | Unit:0.001KW
9466 | Slave03 Outlet Port08 Energy | RO | 4 bytes | Unit:0.001KW
9468 | Slave03 Outlet Port09 Energy | RO | 4 bytes | Unit:0.001KW
9470 | Slave03 Outlet Port10 Energy | RO | 4 bytes | Unit:0.001KW
9472 | Slave03 Outlet Port11 Energy | RO | 4 bytes | Unit:0.001KW
9474 | Slave03 Outlet Port12 Energy | RO | 4 bytes | Unit:0.001KW
9476 | Slave03 Outlet Port13 Energy | RO | 4 bytes | Unit:0.001KW
9478 | Slave03 Outlet Port14 Energy | RO | 4 bytes | Unit:0.001KW
9480 | Slave03 Outlet Port15 Energy | RO | 4 bytes | Unit:0.001KW
9482 | Slave03 Outlet Port16 Energy | RO | 4 bytes | Unit:0.001KW
9484 | Slave03 Outlet Port17 Energy | RO | 4 bytes | Unit:0.001KW
9486 | Slave03 Outlet Port18 Energy | RO | 4 bytes | Unit:0.001KW
9488 | Slave03 Outlet Port19 Energy | RO | 4 bytes | Unit:0.001KW
9490 | Slave03 Outlet Port20 Energy | RO | 4 bytes | Unit:0.001KW
9492 | Slave03 Outlet Port21 Energy | RO | 4 bytes | Unit:0.001KW
9494 | Slave03 Outlet Port22 Energy | RO | 4 bytes | Unit:0.001KW
9496 | Slave03 Outlet Port23 Energy | RO | 4 bytes | Unit:0.001KW
9498 | Slave03 Outlet Port24 Energy | RO | 4 bytes | Unit:0.001KW
9500 | Slave03 Outlet Port25 Energy | RO | 4 bytes | Unit:0.001KW
9502 | Slave03 Outlet Port26 Energy | RO | 4 bytes | Unit:0.001KW
9504 | Slave03 Outlet Port27 Energy | RO | 4 bytes | Unit:0.001KW
9506 | Slave03 Outlet Port28 Energy | RO | 4 bytes | Unit:0.001KW
9508 | Slave03 Outlet Port29 Energy | RO | 4 bytes | Unit:0.001KW
9510 | Slave03 Outlet Port30 Energy | RO | 4 bytes | Unit:0.001KW
9512 | Slave03 Outlet Port31 Energy | RO | 4 bytes | Unit:0.001KW
9514 | Slave03 Outlet Port32 Energy | RO | 4 bytes | Unit:0.001KW
9516 | Slave03 Outlet Port33 Energy | RO | 4 bytes | Unit:0.001KW
9518 | Slave03 Outlet Port34 Energy | RO | 4 bytes | Unit:0.001KW
9520 | Slave03 Outlet Port35 Energy | RO | 4 bytes | Unit:0.001KW
9522 | Slave03 Outlet Port36 Energy | RO | 4 bytes | Unit:0.001KW
9524 | Slave03 Outlet Port37 Energy | RO | 4 bytes | Unit:0.001KW
9526 | Slave03 Outlet Port38 Energy | RO | 4 bytes | Unit:0.001KW
9528 | Slave03 Outlet Port39 Energy | RO | 4 bytes | Unit:0.001KW
9530 | Slave03 Outlet Port40 Energy | RO | 4 bytes | Unit:0.001KW
9532 | Slave03 Outlet Port41 Energy | RO | 4 bytes | Unit:0.001KW
9534 | Slave03 Outlet Port42 Energy | RO | 4 bytes | Unit:0.001KW
9536 | Slave04 Outlet Port01 Energy | RO | 4 bytes | Unit:0.001KW
9538 | Slave04 Outlet Port02 Energy | RO | 4 bytes | Unit:0.001KW
9540 | Slave04 Outlet Port03 Energy | RO | 4 bytes | Unit:0.001KW
9542 | Slave04 Outlet Port04 Energy | RO | 4 bytes | Unit:0.001KW
9544 | Slave04 Outlet Port05 Energy | RO | 4 bytes | Unit:0.001KW
9546 | Slave04 Outlet Port06 Energy | RO | 4 bytes | Unit:0.001KW
9548 | Slave04 Outlet Port07 Energy | RO | 4 bytes | Unit:0.001KW
9550 | Slave04 Outlet Port08 Energy | RO | 4 bytes | Unit:0.001KW
9552 | Slave04 Outlet Port09 Energy | RO | 4 bytes | Unit:0.001KW
9554 | Slave04 Outlet Port10 Energy | RO | 4 bytes | Unit:0.001KW
9556 | Slave04 Outlet Port11 Energy | RO | 4 bytes | Unit:0.001KW
9558 | Slave04 Outlet Port12 Energy | RO | 4 bytes | Unit:0.001KW
9560 | Slave04 Outlet Port13 Energy | RO | 4 bytes | Unit:0.001KW
9562 | Slave04 Outlet Port14 Energy | RO | 4 bytes | Unit:0.001KW
9564 | Slave04 Outlet Port15 Energy | RO | 4 bytes | Unit:0.001KW
9566 | Slave04 Outlet Port16 Energy | RO | 4 bytes | Unit:0.001KW
9568 | Slave04 Outlet Port17 Energy | RO | 4 bytes | Unit:0.001KW
9570 | Slave04 Outlet Port18 Energy | RO | 4 bytes | Unit:0.001KW
9572 | Slave04 Outlet Port19 Energy | RO | 4 bytes | Unit:0.001KW
9574 | Slave04 Outlet Port20 Energy | RO | 4 bytes | Unit:0.001KW
9576 | Slave04 Outlet Port21 Energy | RO | 4 bytes | Unit:0.001KW
9578 | Slave04 Outlet Port22 Energy | RO | 4 bytes | Unit:0.001KW
9580 | Slave04 Outlet Port23 Energy | RO | 4 bytes | Unit:0.001KW
9582 | Slave04 Outlet Port24 Energy | RO | 4 bytes | Unit:0.001KW
9584 | Slave04 Outlet Port25 Energy | RO | 4 bytes | Unit:0.001KW
9586 | Slave04 Outlet Port26 Energy | RO | 4 bytes | Unit:0.001KW
9588 | Slave04 Outlet Port27 Energy | RO | 4 bytes | Unit:0.001KW
9590 | Slave04 Outlet Port28 Energy | RO | 4 bytes | Unit:0.001KW
9592 | Slave04 Outlet Port29 Energy | RO | 4 bytes | Unit:0.001KW
9594 | Slave04 Outlet Port30 Energy | RO | 4 bytes | Unit:0.001KW
9596 | Slave04 Outlet Port31 Energy | RO | 4 bytes | Unit:0.001KW
9598 | Slave04 Outlet Port32 Energy | RO | 4 bytes | Unit:0.001KW
9600 | Slave04 Outlet Port33 Energy | RO | 4 bytes | Unit:0.001KW
9602 | Slave04 Outlet Port34 Energy | RO | 4 bytes | Unit:0.001KW
9604 | Slave04 Outlet Port35 Energy | RO | 4 bytes | Unit:0.001KW
9606 | Slave04 Outlet Port36 Energy | RO | 4 bytes | Unit:0.001KW
9608 | Slave04 Outlet Port37 Energy | RO | 4 bytes | Unit:0.001KW
9610 | Slave04 Outlet Port38 Energy | RO | 4 bytes | Unit:0.001KW
9612 | Slave04 Outlet Port39 Energy | RO | 4 bytes | Unit:0.001KW
9614 | Slave04 Outlet Port40 Energy | RO | 4 bytes | Unit:0.001KW
9616 | Slave04 Outlet Port41 Energy | RO | 4 bytes | Unit:0.001KW
9618 | Slave04 Outlet Port42 Energy | RO | 4 bytes | Unit:0.001KW
9620 | Slave05 Outlet Port01 Energy | RO | 4 bytes | Unit:0.001KW
9622 | Slave05 Outlet Port02 Energy | RO | 4 bytes | Unit:0.001KW
9624 | Slave05 Outlet Port03 Energy | RO | 4 bytes | Unit:0.001KW
9626 | Slave05 Outlet Port04 Energy | RO | 4 bytes | Unit:0.001KW
9628 | Slave05 Outlet Port05 Energy | RO | 4 bytes | Unit:0.001KW
9630 | Slave05 Outlet Port06 Energy | RO | 4 bytes | Unit:0.001KW
9632 | Slave05 Outlet Port07 Energy | RO | 4 bytes | Unit:0.001KW
9634 | Slave05 Outlet Port08 Energy | RO | 4 bytes | Unit:0.001KW
9636 | Slave05 Outlet Port09 Energy | RO | 4 bytes | Unit:0.001KW
9638 | Slave05 Outlet Port10 Energy | RO | 4 bytes | Unit:0.001KW
9640 | Slave05 Outlet Port11 Energy | RO | 4 bytes | Unit:0.001KW
9642 | Slave05 Outlet Port12 Energy | RO | 4 bytes | Unit:0.001KW
9644 | Slave05 Outlet Port13 Energy | RO | 4 bytes | Unit:0.001KW
9646 | Slave05 Outlet Port14 Energy | RO | 4 bytes | Unit:0.001KW
9648 | Slave05 Outlet Port15 Energy | RO | 4 bytes | Unit:0.001KW
9650 | Slave05 Outlet Port16 Energy | RO | 4 bytes | Unit:0.001KW
9652 | Slave05 Outlet Port17 Energy | RO | 4 bytes | Unit:0.001KW
9654 | Slave05 Outlet Port18 Energy | RO | 4 bytes | Unit:0.001KW
9656 | Slave05 Outlet Port19 Energy | RO | 4 bytes | Unit:0.001KW
9658 | Slave05 Outlet Port20 Energy | RO | 4 bytes | Unit:0.001KW
9660 | Slave05 Outlet Port21 Energy | RO | 4 bytes | Unit:0.001KW
9662 | Slave05 Outlet Port22 Energy | RO | 4 bytes | Unit:0.001KW
9664 | Slave05 Outlet Port23 Energy | RO | 4 bytes | Unit:0.001KW
9666 | Slave05 Outlet Port24 Energy | RO | 4 bytes | Unit:0.001KW
9668 | Slave05 Outlet Port25 Energy | RO | 4 bytes | Unit:0.001KW
9670 | Slave05 Outlet Port26 Energy | RO | 4 bytes | Unit:0.001KW
9672 | Slave05 Outlet Port27 Energy | RO | 4 bytes | Unit:0.001KW
9674 | Slave05 Outlet Port28 Energy | RO | 4 bytes | Unit:0.001KW
9676 | Slave05 Outlet Port29 Energy | RO | 4 bytes | Unit:0.001KW
9678 | Slave05 Outlet Port30 Energy | RO | 4 bytes | Unit:0.001KW
9680 | Slave05 Outlet Port31 Energy | RO | 4 bytes | Unit:0.001KW
9682 | Slave05 Outlet Port32 Energy | RO | 4 bytes | Unit:0.001KW
9684 | Slave05 Outlet Port33 Energy | RO | 4 bytes | Unit:0.001KW
9686 | Slave05 Outlet Port34 Energy | RO | 4 bytes | Unit:0.001KW
9688 | Slave05 Outlet Port35 Energy | RO | 4 bytes | Unit:0.001KW
9690 | Slave05 Outlet Port36 Energy | RO | 4 bytes | Unit:0.001KW
9692 | Slave05 Outlet Port37 Energy | RO | 4 bytes | Unit:0.001KW
9694 | Slave05 Outlet Port38 Energy | RO | 4 bytes | Unit:0.001KW
9696 | Slave05 Outlet Port39 Energy | RO | 4 bytes | Unit:0.001KW
9698 | Slave05 Outlet Port40 Energy | RO | 4 bytes | Unit:0.001KW
9700 | Slave05 Outlet Port41 Energy | RO | 4 bytes | Unit:0.001KW
9702 | Slave05 Outlet Port42 Energy | RO | 4 bytes | Unit:0.001KW
9704 | Slave06 Outlet Port01 Energy | RO | 4 bytes | Unit:0.001KW
9706 | Slave06 Outlet Port02 Energy | RO | 4 bytes | Unit:0.001KW
9708 | Slave06 Outlet Port03 Energy | RO | 4 bytes | Unit:0.001KW
9710 | Slave06 Outlet Port04 Energy | RO | 4 bytes | Unit:0.001KW
9712 | Slave06 Outlet Port05 Energy | RO | 4 bytes | Unit:0.001KW
9714 | Slave06 Outlet Port06 Energy | RO | 4 bytes | Unit:0.001KW
9716 | Slave06 Outlet Port07 Energy | RO | 4 bytes | Unit:0.001KW
9718 | Slave06 Outlet Port08 Energy | RO | 4 bytes | Unit:0.001KW
9720 | Slave06 Outlet Port09 Energy | RO | 4 bytes | Unit:0.001KW
9722 | Slave06 Outlet Port10 Energy | RO | 4 bytes | Unit:0.001KW
9724 | Slave06 Outlet Port11 Energy | RO | 4 bytes | Unit:0.001KW
9726 | Slave06 Outlet Port12 Energy | RO | 4 bytes | Unit:0.001KW
9728 | Slave06 Outlet Port13 Energy | RO | 4 bytes | Unit:0.001KW
9730 | Slave06 Outlet Port14 Energy | RO | 4 bytes | Unit:0.001KW
9732 | Slave06 Outlet Port15 Energy | RO | 4 bytes | Unit:0.001KW
9734 | Slave06 Outlet Port16 Energy | RO | 4 bytes | Unit:0.001KW
9736 | Slave06 Outlet Port17 Energy | RO | 4 bytes | Unit:0.001KW
9738 | Slave06 Outlet Port18 Energy | RO | 4 bytes | Unit:0.001KW
9740 | Slave06 Outlet Port19 Energy | RO | 4 bytes | Unit:0.001KW
9742 | Slave06 Outlet Port20 Energy | RO | 4 bytes | Unit:0.001KW
9744 | Slave06 Outlet Port21 Energy | RO | 4 bytes | Unit:0.001KW
9746 | Slave06 Outlet Port22 Energy | RO | 4 bytes | Unit:0.001KW
9748 | Slave06 Outlet Port23 Energy | RO | 4 bytes | Unit:0.001KW
9750 | Slave06 Outlet Port24 Energy | RO | 4 bytes | Unit:0.001KW
9752 | Slave06 Outlet Port25 Energy | RO | 4 bytes | Unit:0.001KW
9754 | Slave06 Outlet Port26 Energy | RO | 4 bytes | Unit:0.001KW
9756 | Slave06 Outlet Port27 Energy | RO | 4 bytes | Unit:0.001KW
9758 | Slave06 Outlet Port28 Energy | RO | 4 bytes | Unit:0.001KW
9760 | Slave06 Outlet Port29 Energy | RO | 4 bytes | Unit:0.001KW
9762 | Slave06 Outlet Port30 Energy | RO | 4 bytes | Unit:0.001KW
9764 | Slave06 Outlet Port31 Energy | RO | 4 bytes | Unit:0.001KW
9766 | Slave06 Outlet Port32 Energy | RO | 4 bytes | Unit:0.001KW
9768 | Slave06 Outlet Port33 Energy | RO | 4 bytes | Unit:0.001KW
9770 | Slave06 Outlet Port34 Energy | RO | 4 bytes | Unit:0.001KW
9772 | Slave06 Outlet Port35 Energy | RO | 4 bytes | Unit:0.001KW
9774 | Slave06 Outlet Port36 Energy | RO | 4 bytes | Unit:0.001KW
9776 | Slave06 Outlet Port37 Energy | RO | 4 bytes | Unit:0.001KW
9778 | Slave06 Outlet Port38 Energy | RO | 4 bytes | Unit:0.001KW
9780 | Slave06 Outlet Port39 Energy | RO | 4 bytes | Unit:0.001KW
9782 | Slave06 Outlet Port40 Energy | RO | 4 bytes | Unit:0.001KW
9784 | Slave06 Outlet Port41 Energy | RO | 4 bytes | Unit:0.001KW
9786 | Slave06 Outlet Port42 Energy | RO | 4 bytes | Unit:0.001KW
9788 | Slave07 Outlet Port01 Energy | RO | 4 bytes | Unit:0.001KW
9790 | Slave07 Outlet Port02 Energy | RO | 4 bytes | Unit:0.001KW
9792 | Slave07 Outlet Port03 Energy | RO | 4 bytes | Unit:0.001KW
9794 | Slave07 Outlet Port04 Energy | RO | 4 bytes | Unit:0.001KW
9796 | Slave07 Outlet Port05 Energy | RO | 4 bytes | Unit:0.001KW
9798 | Slave07 Outlet Port06 Energy | RO | 4 bytes | Unit:0.001KW
9800 | Slave07 Outlet Port07 Energy | RO | 4 bytes | Unit:0.001KW
9802 | Slave07 Outlet Port08 Energy | RO | 4 bytes | Unit:0.001KW
9804 | Slave07 Outlet Port09 Energy | RO | 4 bytes | Unit:0.001KW
9806 | Slave07 Outlet Port10 Energy | RO | 4 bytes | Unit:0.001KW
9808 | Slave07 Outlet Port11 Energy | RO | 4 bytes | Unit:0.001KW
9810 | Slave07 Outlet Port12 Energy | RO | 4 bytes | Unit:0.001KW
9812 | Slave07 Outlet Port13 Energy | RO | 4 bytes | Unit:0.001KW
9814 | Slave07 Outlet Port14 Energy | RO | 4 bytes | Unit:0.001KW
9816 | Slave07 Outlet Port15 Energy | RO | 4 bytes | Unit:0.001KW
9818 | Slave07 Outlet Port16 Energy | RO | 4 bytes | Unit:0.001KW
9820 | Slave07 Outlet Port17 Energy | RO | 4 bytes | Unit:0.001KW
9822 | Slave07 Outlet Port18 Energy | RO | 4 bytes | Unit:0.001KW
9824 | Slave07 Outlet Port19 Energy | RO | 4 bytes | Unit:0.001KW
9826 | Slave07 Outlet Port20 Energy | RO | 4 bytes | Unit:0.001KW
9828 | Slave07 Outlet Port21 Energy | RO | 4 bytes | Unit:0.001KW
9830 | Slave07 Outlet Port22 Energy | RO | 4 bytes | Unit:0.001KW
9832 | Slave07 Outlet Port23 Energy | RO | 4 bytes | Unit:0.001KW
9834 | Slave07 Outlet Port24 Energy | RO | 4 bytes | Unit:0.001KW
9836 | Slave07 Outlet Port25 Energy | RO | 4 bytes | Unit:0.001KW
9838 | Slave07 Outlet Port26 Energy | RO | 4 bytes | Unit:0.001KW
9840 | Slave07 Outlet Port27 Energy | RO | 4 bytes | Unit:0.001KW
9842 | Slave07 Outlet Port28 Energy | RO | 4 bytes | Unit:0.001KW
9844 | Slave07 Outlet Port29 Energy | RO | 4 bytes | Unit:0.001KW
9846 | Slave07 Outlet Port30 Energy | RO | 4 bytes | Unit:0.001KW
9848 | Slave07 Outlet Port31 Energy | RO | 4 bytes | Unit:0.001KW
9850 | Slave07 Outlet Port32 Energy | RO | 4 bytes | Unit:0.001KW
9852 | Slave07 Outlet Port33 Energy | RO | 4 bytes | Unit:0.001KW
9854 | Slave07 Outlet Port34 Energy | RO | 4 bytes | Unit:0.001KW
9856 | Slave07 Outlet Port35 Energy | RO | 4 bytes | Unit:0.001KW
9858 | Slave07 Outlet Port36 Energy | RO | 4 bytes | Unit:0.001KW
9860 | Slave07 Outlet Port37 Energy | RO | 4 bytes | Unit:0.001KW
9862 | Slave07 Outlet Port38 Energy | RO | 4 bytes | Unit:0.001KW
9864 | Slave07 Outlet Port39 Energy | RO | 4 bytes | Unit:0.001KW
9866 | Slave07 Outlet Port40 Energy | RO | 4 bytes | Unit:0.001KW
9868 | Slave07 Outlet Port41 Energy | RO | 4 bytes | Unit:0.001KW
9870 | Slave07 Outlet Port42 Energy | RO | 4 bytes | Unit:0.001KW
9872 | Slave08 Outlet Port01 Energy | RO | 4 bytes | Unit:0.001KW
9874 | Slave08 Outlet Port02 Energy | RO | 4 bytes | Unit:0.001KW
9876 | Slave08 Outlet Port03 Energy | RO | 4 bytes | Unit:0.001KW
9878 | Slave08 Outlet Port04 Energy | RO | 4 bytes | Unit:0.001KW
9880 | Slave08 Outlet Port05 Energy | RO | 4 bytes | Unit:0.001KW
9882 | Slave08 Outlet Port06 Energy | RO | 4 bytes | Unit:0.001KW
9884 | Slave08 Outlet Port07 Energy | RO | 4 bytes | Unit:0.001KW
9886 | Slave08 Outlet Port08 Energy | RO | 4 bytes | Unit:0.001KW
9888 | Slave08 Outlet Port09 Energy | RO | 4 bytes | Unit:0.001KW
9890 | Slave08 Outlet Port10 Energy | RO | 4 bytes | Unit:0.001KW
9892 | Slave08 Outlet Port11 Energy | RO | 4 bytes | Unit:0.001KW
9894 | Slave08 Outlet Port12 Energy | RO | 4 bytes | Unit:0.001KW
9896 | Slave08 Outlet Port13 Energy | RO | 4 bytes | Unit:0.001KW
9898 | Slave08 Outlet Port14 Energy | RO | 4 bytes | Unit:0.001KW
9900 | Slave08 Outlet Port15 Energy | RO | 4 bytes | Unit:0.001KW
9902 | Slave08 Outlet Port16 Energy | RO | 4 bytes | Unit:0.001KW
9904 | Slave08 Outlet Port17 Energy | RO | 4 bytes | Unit:0.001KW
9906 | Slave08 Outlet Port18 Energy | RO | 4 bytes | Unit:0.001KW
9908 | Slave08 Outlet Port19 Energy | RO | 4 bytes | Unit:0.001KW
9910 | Slave08 Outlet Port20 Energy | RO | 4 bytes | Unit:0.001KW
9912 | Slave08 Outlet Port21 Energy | RO | 4 bytes | Unit:0.001KW
9914 | Slave08 Outlet Port22 Energy | RO | 4 bytes | Unit:0.001KW
9916 | Slave08 Outlet Port23 Energy | RO | 4 bytes | Unit:0.001KW
9918 | Slave08 Outlet Port24 Energy | RO | 4 bytes | Unit:0.001KW
9920 | Slave08 Outlet Port25 Energy | RO | 4 bytes | Unit:0.001KW
9922 | Slave08 Outlet Port26 Energy | RO | 4 bytes | Unit:0.001KW
9924 | Slave08 Outlet Port27 Energy | RO | 4 bytes | Unit:0.001KW
9926 | Slave08 Outlet Port28 Energy | RO | 4 bytes | Unit:0.001KW
9928 | Slave08 Outlet Port29 Energy | RO | 4 bytes | Unit:0.001KW
9930 | Slave08 Outlet Port30 Energy | RO | 4 bytes | Unit:0.001KW
9932 | Slave08 Outlet Port31 Energy | RO | 4 bytes | Unit:0.001KW
9934 | Slave08 Outlet Port32 Energy | RO | 4 bytes | Unit:0.001KW
9936 | Slave08 Outlet Port33 Energy | RO | 4 bytes | Unit:0.001KW
9938 | Slave08 Outlet Port34 Energy | RO | 4 bytes | Unit:0.001KW
9940 | Slave08 Outlet Port35 Energy | RO | 4 bytes | Unit:0.001KW
9942 | Slave08 Outlet Port36 Energy | RO | 4 bytes | Unit:0.001KW
9944 | Slave08 Outlet Port37 Energy | RO | 4 bytes | Unit:0.001KW
9946 | Slave08 Outlet Port38 Energy | RO | 4 bytes | Unit:0.001KW
9948 | Slave08 Outlet Port39 Energy | RO | 4 bytes | Unit:0.001KW
9950 | Slave08 Outlet Port40 Energy | RO | 4 bytes | Unit:0.001KW
9952 | Slave08 Outlet Port41 Energy | RO | 4 bytes | Unit:0.001KW
9954 | Slave08 Outlet Port42 Energy | RO | 4 bytes | Unit:0.001KW
9956 | Slave09 Outlet Port01 Energy | RO | 4 bytes | Unit:0.001KW
9958 | Slave09 Outlet Port02 Energy | RO | 4 bytes | Unit:0.001KW
9960 | Slave09 Outlet Port03 Energy | RO | 4 bytes | Unit:0.001KW
9962 | Slave09 Outlet Port04 Energy | RO | 4 bytes | Unit:0.001KW
9964 | Slave09 Outlet Port05 Energy | RO | 4 bytes | Unit:0.001KW
9966 | Slave09 Outlet Port06 Energy | RO | 4 bytes | Unit:0.001KW
9968 | Slave09 Outlet Port07 Energy | RO | 4 bytes | Unit:0.001KW
9970 | Slave09 Outlet Port08 Energy | RO | 4 bytes | Unit:0.001KW
9972 | Slave09 Outlet Port09 Energy | RO | 4 bytes | Unit:0.001KW
9974 | Slave09 Outlet Port10 Energy | RO | 4 bytes | Unit:0.001KW
9976 | Slave09 Outlet Port11 Energy | RO | 4 bytes | Unit:0.001KW
9978 | Slave09 Outlet Port12 Energy | RO | 4 bytes | Unit:0.001KW
9980 | Slave09 Outlet Port13 Energy | RO | 4 bytes | Unit:0.001KW
9982 | Slave09 Outlet Port14 Energy | RO | 4 bytes | Unit:0.001KW
9984 | Slave09 Outlet Port15 Energy | RO | 4 bytes | Unit:0.001KW
9986 | Slave09 Outlet Port16 Energy | RO | 4 bytes | Unit:0.001KW
9988 | Slave09 Outlet Port17 Energy | RO | 4 bytes | Unit:0.001KW
9990 | Slave09 Outlet Port18 Energy | RO | 4 bytes | Unit:0.001KW
9992 | Slave09 Outlet Port19 Energy | RO | 4 bytes | Unit:0.001KW
9994 | Slave09 Outlet Port20 Energy | RO | 4 bytes | Unit:0.001KW
9996 | Slave09 Outlet Port21 Energy | RO | 4 bytes | Unit:0.001KW
9998 | Slave09 Outlet Port22 Energy | RO | 4 bytes | Unit:0.001KW
10000 | Slave09 Outlet Port23 Energy | RO | 4 bytes | Unit:0.001KW
10002 | Slave09 Outlet Port24 Energy | RO | 4 bytes | Unit:0.001KW
10004 | Slave09 Outlet Port25 Energy | RO | 4 bytes | Unit:0.001KW
10006 | Slave09 Outlet Port26 Energy | RO | 4 bytes | Unit:0.001KW
10008 | Slave09 Outlet Port27 Energy | RO | 4 bytes | Unit:0.001KW
10010 | Slave09 Outlet Port28 Energy | RO | 4 bytes | Unit:0.001KW
10012 | Slave09 Outlet Port29 Energy | RO | 4 bytes | Unit:0.001KW
10014 | Slave09 Outlet Port30 Energy | RO | 4 bytes | Unit:0.001KW
10016 | Slave09 Outlet Port31 Energy | RO | 4 bytes | Unit:0.001KW
10018 | Slave09 Outlet Port32 Energy | RO | 4 bytes | Unit:0.001KW
10020 | Slave09 Outlet Port33 Energy | RO | 4 bytes | Unit:0.001KW
10022 | Slave09 Outlet Port34 Energy | RO | 4 bytes | Unit:0.001KW
10024 | Slave09 Outlet Port35 Energy | RO | 4 bytes | Unit:0.001KW
10026 | Slave09 Outlet Port36 Energy | RO | 4 bytes | Unit:0.001KW
10028 | Slave09 Outlet Port37 Energy | RO | 4 bytes | Unit:0.001KW
10030 | Slave09 Outlet Port38 Energy | RO | 4 bytes | Unit:0.001KW
10032 | Slave09 Outlet Port39 Energy | RO | 4 bytes | Unit:0.001KW
10034 | Slave09 Outlet Port40 Energy | RO | 4 bytes | Unit:0.001KW
10036 | Slave09 Outlet Port41 Energy | RO | 4 bytes | Unit:0.001KW
10038 | Slave09 Outlet Port42 Energy | RO | 4 bytes | Unit:0.001KW
10040 | Slave10 Outlet Port01 Energy | RO | 4 bytes | Unit:0.001KW
10042 | Slave10 Outlet Port02 Energy | RO | 4 bytes | Unit:0.001KW
10044 | Slave10 Outlet Port03 Energy | RO | 4 bytes | Unit:0.001KW
10046 | Slave10 Outlet Port04 Energy | RO | 4 bytes | Unit:0.001KW
10048 | Slave10 Outlet Port05 Energy | RO | 4 bytes | Unit:0.001KW
10050 | Slave10 Outlet Port06 Energy | RO | 4 bytes | Unit:0.001KW
10052 | Slave10 Outlet Port07 Energy | RO | 4 bytes | Unit:0.001KW
10054 | Slave10 Outlet Port08 Energy | RO | 4 bytes | Unit:0.001KW
10056 | Slave10 Outlet Port09 Energy | RO | 4 bytes | Unit:0.001KW
10058 | Slave10 Outlet Port10 Energy | RO | 4 bytes | Unit:0.001KW
10060 | Slave10 Outlet Port11 Energy | RO | 4 bytes | Unit:0.001KW
10062 | Slave10 Outlet Port12 Energy | RO | 4 bytes | Unit:0.001KW
10064 | Slave10 Outlet Port13 Energy | RO | 4 bytes | Unit:0.001KW
10066 | Slave10 Outlet Port14 Energy | RO | 4 bytes | Unit:0.001KW
10068 | Slave10 Outlet Port15 Energy | RO | 4 bytes | Unit:0.001KW
10070 | Slave10 Outlet Port16 Energy | RO | 4 bytes | Unit:0.001KW
10072 | Slave10 Outlet Port17 Energy | RO | 4 bytes | Unit:0.001KW
10074 | Slave10 Outlet Port18 Energy | RO | 4 bytes | Unit:0.001KW
10076 | Slave10 Outlet Port19 Energy | RO | 4 bytes | Unit:0.001KW
10078 | Slave10 Outlet Port20 Energy | RO | 4 bytes | Unit:0.001KW
10080 | Slave10 Outlet Port21 Energy | RO | 4 bytes | Unit:0.001KW
10082 | Slave10 Outlet Port22 Energy | RO | 4 bytes | Unit:0.001KW
10084 | Slave10 Outlet Port23 Energy | RO | 4 bytes | Unit:0.001KW
10086 | Slave10 Outlet Port24 Energy | RO | 4 bytes | Unit:0.001KW
10088 | Slave10 Outlet Port25 Energy | RO | 4 bytes | Unit:0.001KW
10090 | Slave10 Outlet Port26 Energy | RO | 4 bytes | Unit:0.001KW
10092 | Slave10 Outlet Port27 Energy | RO | 4 bytes | Unit:0.001KW
10094 | Slave10 Outlet Port28 Energy | RO | 4 bytes | Unit:0.001KW
10096 | Slave10 Outlet Port29 Energy | RO | 4 bytes | Unit:0.001KW
10098 | Slave10 Outlet Port30 Energy | RO | 4 bytes | Unit:0.001KW
10100 | Slave10 Outlet Port31 Energy | RO | 4 bytes | Unit:0.001KW
10102 | Slave10 Outlet Port32 Energy | RO | 4 bytes | Unit:0.001KW
10104 | Slave10 Outlet Port33 Energy | RO | 4 bytes | Unit:0.001KW
10106 | Slave10 Outlet Port34 Energy | RO | 4 bytes | Unit:0.001KW
10108 | Slave10 Outlet Port35 Energy | RO | 4 bytes | Unit:0.001KW
10110 | Slave10 Outlet Port36 Energy | RO | 4 bytes | Unit:0.001KW
10112 | Slave10 Outlet Port37 Energy | RO | 4 bytes | Unit:0.001KW
10114 | Slave10 Outlet Port38 Energy | RO | 4 bytes | Unit:0.001KW
10116 | Slave10 Outlet Port39 Energy | RO | 4 bytes | Unit:0.001KW
10118 | Slave10 Outlet Port40 Energy | RO | 4 bytes | Unit:0.001KW
10120 | Slave10 Outlet Port41 Energy | RO | 4 bytes | Unit:0.001KW
10122 | Slave10 Outlet Port42 Energy | RO | 4 bytes | Unit:0.001KW
10124 | Slave11 Outlet Port01 Energy | RO | 4 bytes | Unit:0.001KW
10126 | Slave11 Outlet Port02 Energy | RO | 4 bytes | Unit:0.001KW
10128 | Slave11 Outlet Port03 Energy | RO | 4 bytes | Unit:0.001KW
10130 | Slave11 Outlet Port04 Energy | RO | 4 bytes | Unit:0.001KW
10132 | Slave11 Outlet Port05 Energy | RO | 4 bytes | Unit:0.001KW
10134 | Slave11 Outlet Port06 Energy | RO | 4 bytes | Unit:0.001KW
10136 | Slave11 Outlet Port07 Energy | RO | 4 bytes | Unit:0.001KW
10138 | Slave11 Outlet Port08 Energy | RO | 4 bytes | Unit:0.001KW
10140 | Slave11 Outlet Port09 Energy | RO | 4 bytes | Unit:0.001KW
10142 | Slave11 Outlet Port10 Energy | RO | 4 bytes | Unit:0.001KW
10144 | Slave11 Outlet Port11 Energy | RO | 4 bytes | Unit:0.001KW
10146 | Slave11 Outlet Port12 Energy | RO | 4 bytes | Unit:0.001KW
10148 | Slave11 Outlet Port13 Energy | RO | 4 bytes | Unit:0.001KW
10150 | Slave11 Outlet Port14 Energy | RO | 4 bytes | Unit:0.001KW
10152 | Slave11 Outlet Port15 Energy | RO | 4 bytes | Unit:0.001KW
10154 | Slave11 Outlet Port16 Energy | RO | 4 bytes | Unit:0.001KW
10156 | Slave11 Outlet Port17 Energy | RO | 4 bytes | Unit:0.001KW
10158 | Slave11 Outlet Port18 Energy | RO | 4 bytes | Unit:0.001KW
10160 | Slave11 Outlet Port19 Energy | RO | 4 bytes | Unit:0.001KW
10162 | Slave11 Outlet Port20 Energy | RO | 4 bytes | Unit:0.001KW
10164 | Slave11 Outlet Port21 Energy | RO | 4 bytes | Unit:0.001KW
10166 | Slave11 Outlet Port22 Energy | RO | 4 bytes | Unit:0.001KW
10168 | Slave11 Outlet Port23 Energy | RO | 4 bytes | Unit:0.001KW
10170 | Slave11 Outlet Port24 Energy | RO | 4 bytes | Unit:0.001KW
10172 | Slave11 Outlet Port25 Energy | RO | 4 bytes | Unit:0.001KW
10174 | Slave11 Outlet Port26 Energy | RO | 4 bytes | Unit:0.001KW
10176 | Slave11 Outlet Port27 Energy | RO | 4 bytes | Unit:0.001KW
10178 | Slave11 Outlet Port28 Energy | RO | 4 bytes | Unit:0.001KW
10180 | Slave11 Outlet Port29 Energy | RO | 4 bytes | Unit:0.001KW
10182 | Slave11 Outlet Port30 Energy | RO | 4 bytes | Unit:0.001KW
10184 | Slave11 Outlet Port31 Energy | RO | 4 bytes | Unit:0.001KW
10186 | Slave11 Outlet Port32 Energy | RO | 4 bytes | Unit:0.001KW
10188 | Slave11 Outlet Port33 Energy | RO | 4 bytes | Unit:0.001KW
10190 | Slave11 Outlet Port34 Energy | RO | 4 bytes | Unit:0.001KW
10192 | Slave11 Outlet Port35 Energy | RO | 4 bytes | Unit:0.001KW
10194 | Slave11 Outlet Port36 Energy | RO | 4 bytes | Unit:0.001KW
10196 | Slave11 Outlet Port37 Energy | RO | 4 bytes | Unit:0.001KW
10198 | Slave11 Outlet Port38 Energy | RO | 4 bytes | Unit:0.001KW
10200 | Slave11 Outlet Port39 Energy | RO | 4 bytes | Unit:0.001KW
10202 | Slave11 Outlet Port40 Energy | RO | 4 bytes | Unit:0.001KW
10204 | Slave11 Outlet Port41 Energy | RO | 4 bytes | Unit:0.001KW
10206 | Slave11 Outlet Port42 Energy | RO | 4 bytes | Unit:0.001KW
10208 | Slave12 Outlet Port01 Energy | RO | 4 bytes | Unit:0.001KW
10210 | Slave12 Outlet Port02 Energy | RO | 4 bytes | Unit:0.001KW
10212 | Slave12 Outlet Port03 Energy | RO | 4 bytes | Unit:0.001KW
10214 | Slave12 Outlet Port04 Energy | RO | 4 bytes | Unit:0.001KW
10216 | Slave12 Outlet Port05 Energy | RO | 4 bytes | Unit:0.001KW
10218 | Slave12 Outlet Port06 Energy | RO | 4 bytes | Unit:0.001KW
10220 | Slave12 Outlet Port07 Energy | RO | 4 bytes | Unit:0.001KW
10222 | Slave12 Outlet Port08 Energy | RO | 4 bytes | Unit:0.001KW
10224 | Slave12 Outlet Port09 Energy | RO | 4 bytes | Unit:0.001KW
10226 | Slave12 Outlet Port10 Energy | RO | 4 bytes | Unit:0.001KW
10228 | Slave12 Outlet Port11 Energy | RO | 4 bytes | Unit:0.001KW
10230 | Slave12 Outlet Port12 Energy | RO | 4 bytes | Unit:0.001KW
10232 | Slave12 Outlet Port13 Energy | RO | 4 bytes | Unit:0.001KW
10234 | Slave12 Outlet Port14 Energy | RO | 4 bytes | Unit:0.001KW
10236 | Slave12 Outlet Port15 Energy | RO | 4 bytes | Unit:0.001KW
10238 | Slave12 Outlet Port16 Energy | RO | 4 bytes | Unit:0.001KW
10240 | Slave12 Outlet Port17 Energy | RO | 4 bytes | Unit:0.001KW
10242 | Slave12 Outlet Port18 Energy | RO | 4 bytes | Unit:0.001KW
10244 | Slave12 Outlet Port19 Energy | RO | 4 bytes | Unit:0.001KW
10246 | Slave12 Outlet Port20 Energy | RO | 4 bytes | Unit:0.001KW
10248 | Slave12 Outlet Port21 Energy | RO | 4 bytes | Unit:0.001KW
10250 | Slave12 Outlet Port22 Energy | RO | 4 bytes | Unit:0.001KW
10252 | Slave12 Outlet Port23 Energy | RO | 4 bytes | Unit:0.001KW
10254 | Slave12 Outlet Port24 Energy | RO | 4 bytes | Unit:0.001KW
10256 | Slave12 Outlet Port25 Energy | RO | 4 bytes | Unit:0.001KW
10258 | Slave12 Outlet Port26 Energy | RO | 4 bytes | Unit:0.001KW
10260 | Slave12 Outlet Port27 Energy | RO | 4 bytes | Unit:0.001KW
10262 | Slave12 Outlet Port28 Energy | RO | 4 bytes | Unit:0.001KW
10264 | Slave12 Outlet Port29 Energy | RO | 4 bytes | Unit:0.001KW
10266 | Slave12 Outlet Port30 Energy | RO | 4 bytes | Unit:0.001KW
10268 | Slave12 Outlet Port31 Energy | RO | 4 bytes | Unit:0.001KW
10270 | Slave12 Outlet Port32 Energy | RO | 4 bytes | Unit:0.001KW
10272 | Slave12 Outlet Port33 Energy | RO | 4 bytes | Unit:0.001KW
10274 | Slave12 Outlet Port34 Energy | RO | 4 bytes | Unit:0.001KW
10276 | Slave12 Outlet Port35 Energy | RO | 4 bytes | Unit:0.001KW
10278 | Slave12 Outlet Port36 Energy | RO | 4 bytes | Unit:0.001KW
10280 | Slave12 Outlet Port37 Energy | RO | 4 bytes | Unit:0.001KW
10282 | Slave12 Outlet Port38 Energy | RO | 4 bytes | Unit:0.001KW
10284 | Slave12 Outlet Port39 Energy | RO | 4 bytes | Unit:0.001KW
10286 | Slave12 Outlet Port40 Energy | RO | 4 bytes | Unit:0.001KW
10288 | Slave12 Outlet Port41 Energy | RO | 4 bytes | Unit:0.001KW
10290 | Slave12 Outlet Port42 Energy | RO | 4 bytes | Unit:0.001KW
10292 | Slave13 Outlet Port01 Energy | RO | 4 bytes | Unit:0.001KW
10294 | Slave13 Outlet Port02 Energy | RO | 4 bytes | Unit:0.001KW
10296 | Slave13 Outlet Port03 Energy | RO | 4 bytes | Unit:0.001KW
10298 | Slave13 Outlet Port04 Energy | RO | 4 bytes | Unit:0.001KW
10300 | Slave13 Outlet Port05 Energy | RO | 4 bytes | Unit:0.001KW
10302 | Slave13 Outlet Port06 Energy | RO | 4 bytes | Unit:0.001KW
10304 | Slave13 Outlet Port07 Energy | RO | 4 bytes | Unit:0.001KW
10306 | Slave13 Outlet Port08 Energy | RO | 4 bytes | Unit:0.001KW
10308 | Slave13 Outlet Port09 Energy | RO | 4 bytes | Unit:0.001KW
10310 | Slave13 Outlet Port10 Energy | RO | 4 bytes | Unit:0.001KW
10312 | Slave13 Outlet Port11 Energy | RO | 4 bytes | Unit:0.001KW
10314 | Slave13 Outlet Port12 Energy | RO | 4 bytes | Unit:0.001KW
10316 | Slave13 Outlet Port13 Energy | RO | 4 bytes | Unit:0.001KW
10318 | Slave13 Outlet Port14 Energy | RO | 4 bytes | Unit:0.001KW
10320 | Slave13 Outlet Port15 Energy | RO | 4 bytes | Unit:0.001KW
10322 | Slave13 Outlet Port16 Energy | RO | 4 bytes | Unit:0.001KW
10324 | Slave13 Outlet Port17 Energy | RO | 4 bytes | Unit:0.001KW
10326 | Slave13 Outlet Port18 Energy | RO | 4 bytes | Unit:0.001KW
10328 | Slave13 Outlet Port19 Energy | RO | 4 bytes | Unit:0.001KW
10330 | Slave13 Outlet Port20 Energy | RO | 4 bytes | Unit:0.001KW
10332 | Slave13 Outlet Port21 Energy | RO | 4 bytes | Unit:0.001KW
10334 | Slave13 Outlet Port22 Energy | RO | 4 bytes | Unit:0.001KW
10336 | Slave13 Outlet Port23 Energy | RO | 4 bytes | Unit:0.001KW
10338 | Slave13 Outlet Port24 Energy | RO | 4 bytes | Unit:0.001KW
10340 | Slave13 Outlet Port25 Energy | RO | 4 bytes | Unit:0.001KW
10342 | Slave13 Outlet Port26 Energy | RO | 4 bytes | Unit:0.001KW
10344 | Slave13 Outlet Port27 Energy | RO | 4 bytes | Unit:0.001KW
10346 | Slave13 Outlet Port28 Energy | RO | 4 bytes | Unit:0.001KW
10348 | Slave13 Outlet Port29 Energy | RO | 4 bytes | Unit:0.001KW
10350 | Slave13 Outlet Port30 Energy | RO | 4 bytes | Unit:0.001KW
10352 | Slave13 Outlet Port31 Energy | RO | 4 bytes | Unit:0.001KW
10354 | Slave13 Outlet Port32 Energy | RO | 4 bytes | Unit:0.001KW
10356 | Slave13 Outlet Port33 Energy | RO | 4 bytes | Unit:0.001KW
10358 | Slave13 Outlet Port34 Energy | RO | 4 bytes | Unit:0.001KW
10360 | Slave13 Outlet Port35 Energy | RO | 4 bytes | Unit:0.001KW
10362 | Slave13 Outlet Port36 Energy | RO | 4 bytes | Unit:0.001KW
10364 | Slave13 Outlet Port37 Energy | RO | 4 bytes | Unit:0.001KW
10366 | Slave13 Outlet Port38 Energy | RO | 4 bytes | Unit:0.001KW
10368 | Slave13 Outlet Port39 Energy | RO | 4 bytes | Unit:0.001KW
10370 | Slave13 Outlet Port40 Energy | RO | 4 bytes | Unit:0.001KW
10372 | Slave13 Outlet Port41 Energy | RO | 4 bytes | Unit:0.001KW
10374 | Slave13 Outlet Port42 Energy | RO | 4 bytes | Unit:0.001KW
10376 | Slave14 Outlet Port01 Energy | RO | 4 bytes | Unit:0.001KW
10378 | Slave14 Outlet Port02 Energy | RO | 4 bytes | Unit:0.001KW
10380 | Slave14 Outlet Port03 Energy | RO | 4 bytes | Unit:0.001KW
10382 | Slave14 Outlet Port04 Energy | RO | 4 bytes | Unit:0.001KW
10384 | Slave14 Outlet Port05 Energy | RO | 4 bytes | Unit:0.001KW
10386 | Slave14 Outlet Port06 Energy | RO | 4 bytes | Unit:0.001KW
10388 | Slave14 Outlet Port07 Energy | RO | 4 bytes | Unit:0.001KW
10390 | Slave14 Outlet Port08 Energy | RO | 4 bytes | Unit:0.001KW
10392 | Slave14 Outlet Port09 Energy | RO | 4 bytes | Unit:0.001KW
10394 | Slave14 Outlet Port10 Energy | RO | 4 bytes | Unit:0.001KW
10396 | Slave14 Outlet Port11 Energy | RO | 4 bytes | Unit:0.001KW
10398 | Slave14 Outlet Port12 Energy | RO | 4 bytes | Unit:0.001KW
10400 | Slave14 Outlet Port13 Energy | RO | 4 bytes | Unit:0.001KW
10402 | Slave14 Outlet Port14 Energy | RO | 4 bytes | Unit:0.001KW
10404 | Slave14 Outlet Port15 Energy | RO | 4 bytes | Unit:0.001KW
10406 | Slave14 Outlet Port16 Energy | RO | 4 bytes | Unit:0.001KW
10408 | Slave14 Outlet Port17 Energy | RO | 4 bytes | Unit:0.001KW
10410 | Slave14 Outlet Port18 Energy | RO | 4 bytes | Unit:0.001KW
10412 | Slave14 Outlet Port19 Energy | RO | 4 bytes | Unit:0.001KW
10414 | Slave14 Outlet Port20 Energy | RO | 4 bytes | Unit:0.001KW
10416 | Slave14 Outlet Port21 Energy | RO | 4 bytes | Unit:0.001KW
10418 | Slave14 Outlet Port22 Energy | RO | 4 bytes | Unit:0.001KW
10420 | Slave14 Outlet Port23 Energy | RO | 4 bytes | Unit:0.001KW
10422 | Slave14 Outlet Port24 Energy | RO | 4 bytes | Unit:0.001KW
10424 | Slave14 Outlet Port25 Energy | RO | 4 bytes | Unit:0.001KW
10426 | Slave14 Outlet Port26 Energy | RO | 4 bytes | Unit:0.001KW
10428 | Slave14 Outlet Port27 Energy | RO | 4 bytes | Unit:0.001KW
10430 | Slave14 Outlet Port28 Energy | RO | 4 bytes | Unit:0.001KW
10432 | Slave14 Outlet Port29 Energy | RO | 4 bytes | Unit:0.001KW
10434 | Slave14 Outlet Port30 Energy | RO | 4 bytes | Unit:0.001KW
10436 | Slave14 Outlet Port31 Energy | RO | 4 bytes | Unit:0.001KW
10438 | Slave14 Outlet Port32 Energy | RO | 4 bytes | Unit:0.001KW
10440 | Slave14 Outlet Port33 Energy | RO | 4 bytes | Unit:0.001KW
10442 | Slave14 Outlet Port34 Energy | RO | 4 bytes | Unit:0.001KW
10444 | Slave14 Outlet Port35 Energy | RO | 4 bytes | Unit:0.001KW
10446 | Slave14 Outlet Port36 Energy | RO | 4 bytes | Unit:0.001KW
10448 | Slave14 Outlet Port37 Energy | RO | 4 bytes | Unit:0.001KW
10450 | Slave14 Outlet Port38 Energy | RO | 4 bytes | Unit:0.001KW
10452 | Slave14 Outlet Port39 Energy | RO | 4 bytes | Unit:0.001KW
10454 | Slave14 Outlet Port40 Energy | RO | 4 bytes | Unit:0.001KW
10456 | Slave14 Outlet Port41 Energy | RO | 4 bytes | Unit:0.001KW
10458 | Slave14 Outlet Port42 Energy | RO | 4 bytes | Unit:0.001KW
10460 | Slave15 Outlet Port01 Energy | RO | 4 bytes | Unit:0.001KW
10462 | Slave15 Outlet Port02 Energy | RO | 4 bytes | Unit:0.001KW
10464 | Slave15 Outlet Port03 Energy | RO | 4 bytes | Unit:0.001KW
10466 | Slave15 Outlet Port04 Energy | RO | 4 bytes | Unit:0.001KW
10468 | Slave15 Outlet Port05 Energy | RO | 4 bytes | Unit:0.001KW
10470 | Slave15 Outlet Port06 Energy | RO | 4 bytes | Unit:0.001KW
10472 | Slave15 Outlet Port07 Energy | RO | 4 bytes | Unit:0.001KW
10474 | Slave15 Outlet Port08 Energy | RO | 4 bytes | Unit:0.001KW
10476 | Slave15 Outlet Port09 Energy | RO | 4 bytes | Unit:0.001KW
10478 | Slave15 Outlet Port10 Energy | RO | 4 bytes | Unit:0.001KW
10480 | Slave15 Outlet Port11 Energy | RO | 4 bytes | Unit:0.001KW
10482 | Slave15 Outlet Port12 Energy | RO | 4 bytes | Unit:0.001KW
10484 | Slave15 Outlet Port13 Energy | RO | 4 bytes | Unit:0.001KW
10486 | Slave15 Outlet Port14 Energy | RO | 4 bytes | Unit:0.001KW
10488 | Slave15 Outlet Port15 Energy | RO | 4 bytes | Unit:0.001KW
10490 | Slave15 Outlet Port16 Energy | RO | 4 bytes | Unit:0.001KW
10492 | Slave15 Outlet Port17 Energy | RO | 4 bytes | Unit:0.001KW
10494 | Slave15 Outlet Port18 Energy | RO | 4 bytes | Unit:0.001KW
10496 | Slave15 Outlet Port19 Energy | RO | 4 bytes | Unit:0.001KW
10498 | Slave15 Outlet Port20 Energy | RO | 4 bytes | Unit:0.001KW
10500 | Slave15 Outlet Port21 Energy | RO | 4 bytes | Unit:0.001KW
10502 | Slave15 Outlet Port22 Energy | RO | 4 bytes | Unit:0.001KW
10504 | Slave15 Outlet Port23 Energy | RO | 4 bytes | Unit:0.001KW
10506 | Slave15 Outlet Port24 Energy | RO | 4 bytes | Unit:0.001KW
10508 | Slave15 Outlet Port25 Energy | RO | 4 bytes | Unit:0.001KW
10510 | Slave15 Outlet Port26 Energy | RO | 4 bytes | Unit:0.001KW
10512 | Slave15 Outlet Port27 Energy | RO | 4 bytes | Unit:0.001KW
10514 | Slave15 Outlet Port28 Energy | RO | 4 bytes | Unit:0.001KW
10516 | Slave15 Outlet Port29 Energy | RO | 4 bytes | Unit:0.001KW
10518 | Slave15 Outlet Port30 Energy | RO | 4 bytes | Unit:0.001KW
10520 | Slave15 Outlet Port31 Energy | RO | 4 bytes | Unit:0.001KW
10522 | Slave15 Outlet Port32 Energy | RO | 4 bytes | Unit:0.001KW
10524 | Slave15 Outlet Port33 Energy | RO | 4 bytes | Unit:0.001KW
10526 | Slave15 Outlet Port34 Energy | RO | 4 bytes | Unit:0.001KW
10528 | Slave15 Outlet Port35 Energy | RO | 4 bytes | Unit:0.001KW
10530 | Slave15 Outlet Port36 Energy | RO | 4 bytes | Unit:0.001KW
10532 | Slave15 Outlet Port37 Energy | RO | 4 bytes | Unit:0.001KW
10534 | Slave15 Outlet Port38 Energy | RO | 4 bytes | Unit:0.001KW
10536 | Slave15 Outlet Port39 Energy | RO | 4 bytes | Unit:0.001KW
10538 | Slave15 Outlet Port40 Energy | RO | 4 bytes | Unit:0.001KW
10540 | Slave15 Outlet Port41 Energy | RO | 4 bytes | Unit:0.001KW
10542 | Slave15 Outlet Port42 Energy | RO | 4 bytes | Unit:0.001KW
10544 | Master Inlet Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
10545 | Slave01 Inlet Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
10546 | Slave02 Inlet Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
10547 | Slave03 Inlet Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
10548 | Slave04 Inlet Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
10549 | Slave05 Inlet Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
10550 | Slave06 Inlet Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
10551 | Slave07 Inlet Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
10552 | Slave08 Inlet Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
10553 | Slave09 Inlet Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
10554 | Slave10 Inlet Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
10555 | Slave11 Inlet Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
10556 | Slave12 Inlet Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
10557 | Slave13 Inlet Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
10558 | Slave14 Inlet Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
10559 | Slave15 Inlet Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
10560 | Master Inlet Over Load Warning | RW | 2 bytes | Unit:1
10561 | Slave01 Inlet Over Load Warning | RW | 2 bytes | Unit:1
10562 | Slave02 Inlet Over Load Warning | RW | 2 bytes | Unit:1
10563 | Slave03 Inlet Over Load Warning | RW | 2 bytes | Unit:1
10564 | Slave04 Inlet Over Load Warning | RW | 2 bytes | Unit:1
10565 | Slave05 Inlet Over Load Warning | RW | 2 bytes | Unit:1
10566 | Slave06 Inlet Over Load Warning | RW | 2 bytes | Unit:1
10567 | Slave07 Inlet Over Load Warning | RW | 2 bytes | Unit:1
10568 | Slave08 Inlet Over Load Warning | RW | 2 bytes | Unit:1
10569 | Slave09 Inlet Over Load Warning | RW | 2 bytes | Unit:1
10570 | Slave10 Inlet Over Load Warning | RW | 2 bytes | Unit:1
10571 | Slave11 Inlet Over Load Warning | RW | 2 bytes | Unit:1
10572 | Slave12 Inlet Over Load Warning | RW | 2 bytes | Unit:1
10573 | Slave13 Inlet Over Load Warning | RW | 2 bytes | Unit:1
10574 | Slave14 Inlet Over Load Warning | RW | 2 bytes | Unit:1
10575 | Slave15 Inlet Over Load Warning | RW | 2 bytes | Unit:1
10576 | Master Inlet Over Load Critical | RW | 2 bytes | Unit:1
10577 | Slave01 Inlet Over Load Critical | RW | 2 bytes | Unit:1
10578 | Slave02 Inlet Over Load Critical | RW | 2 bytes | Unit:1
10579 | Slave03 Inlet Over Load Critical | RW | 2 bytes | Unit:1
10580 | Slave04 Inlet Over Load Critical | RW | 2 bytes | Unit:1
10581 | Slave05 Inlet Over Load Critical | RW | 2 bytes | Unit:1
10582 | Slave06 Inlet Over Load Critical | RW | 2 bytes | Unit:1
10583 | Slave07 Inlet Over Load Critical | RW | 2 bytes | Unit:1
10584 | Slave08 Inlet Over Load Critical | RW | 2 bytes | Unit:1
10585 | Slave09 Inlet Over Load Critical | RW | 2 bytes | Unit:1
10586 | Slave10 Inlet Over Load Critical | RW | 2 bytes | Unit:1
10587 | Slave11 Inlet Over Load Critical | RW | 2 bytes | Unit:1
10588 | Slave12 Inlet Over Load Critical | RW | 2 bytes | Unit:1
10589 | Slave13 Inlet Over Load Critical | RW | 2 bytes | Unit:1
10590 | Slave14 Inlet Over Load Critical | RW | 2 bytes | Unit:1
10591 | Slave15 Inlet Over Load Critical | RW | 2 bytes | Unit:1
10592 | Master Inlet Load Balance Warning | RW | 2 bytes | Unit:1%
10593 | Slave01 Inlet Load Balance Warning | RW | 2 bytes | Unit:1%
10594 | Slave02 Inlet Load Balance Warning | RW | 2 bytes | Unit:1%
10595 | Slave03 Inlet Load Balance Warning | RW | 2 bytes | Unit:1%
10596 | Slave04 Inlet Load Balance Warning | RW | 2 bytes | Unit:1%
10597 | Slave05 Inlet Load Balance Warning | RW | 2 bytes | Unit:1%
10598 | Slave06 Inlet Load Balance Warning | RW | 2 bytes | Unit:1%
10599 | Slave07 Inlet Load Balance Warning | RW | 2 bytes | Unit:1%
10600 | Slave08 Inlet Load Balance Warning | RW | 2 bytes | Unit:1%
10601 | Slave09 Inlet Load Balance Warning | RW | 2 bytes | Unit:1%
10602 | Slave10 Inlet Load Balance Warning | RW | 2 bytes | Unit:1%
10603 | Slave11 Inlet Load Balance Warning | RW | 2 bytes | Unit:1%
10604 | Slave12 Inlet Load Balance Warning | RW | 2 bytes | Unit:1%
10605 | Slave13 Inlet Load Balance Warning | RW | 2 bytes | Unit:1%
10606 | Slave14 Inlet Load Balance Warning | RW | 2 bytes | Unit:1%
10607 | Slave15 Inlet Load Balance Warning | RW | 2 bytes | Unit:1%
10608 | Master Inlet Load Balance Critical | RW | 2 bytes | Unit:1%
10609 | Slave01 Inlet Load Balance Critical | RW | 2 bytes | Unit:1%
10610 | Slave02 Inlet Load Balance Critical | RW | 2 bytes | Unit:1%
10611 | Slave03 Inlet Load Balance Critical | RW | 2 bytes | Unit:1%
10612 | Slave04 Inlet Load Balance Critical | RW | 2 bytes | Unit:1%
10613 | Slave05 Inlet Load Balance Critical | RW | 2 bytes | Unit:1%
10614 | Slave06 Inlet Load Balance Critical | RW | 2 bytes | Unit:1%
10615 | Slave07 Inlet Load Balance Critical | RW | 2 bytes | Unit:1%
10616 | Slave08 Inlet Load Balance Critical | RW | 2 bytes | Unit:1%
10617 | Slave09 Inlet Load Balance Critical | RW | 2 bytes | Unit:1%
10618 | Slave10 Inlet Load Balance Critical | RW | 2 bytes | Unit:1%
10619 | Slave11 Inlet Load Balance Critical | RW | 2 bytes | Unit:1%
10620 | Slave12 Inlet Load Balance Critical | RW | 2 bytes | Unit:1%
10621 | Slave13 Inlet Load Balance Critical | RW | 2 bytes | Unit:1%
10622 | Slave14 Inlet Load Balance Critical | RW | 2 bytes | Unit:1%
10623 | Slave15 Inlet Load Balance Critical | RW | 2 bytes | Unit:1%
10624 | Master Inlet Phase1 Over Voltage Warning | RW | 2 bytes | Unit:0.1
10625 | Slave01 Inlet Phase1 Over Voltage Warning | RW | 2 bytes | Unit:0.1
10626 | Slave02 Inlet Phase1 Over Voltage Warning | RW | 2 bytes | Unit:0.1
10627 | Slave03 Inlet Phase1 Over Voltage Warning | RW | 2 bytes | Unit:0.1
10628 | Slave04 Inlet Phase1 Over Voltage Warning | RW | 2 bytes | Unit:0.1
10629 | Slave05 Inlet Phase1 Over Voltage Warning | RW | 2 bytes | Unit:0.1
10630 | Slave06 Inlet Phase1 Over Voltage Warning | RW | 2 bytes | Unit:0.1
10631 | Slave07 Inlet Phase1 Over Voltage Warning | RW | 2 bytes | Unit:0.1
10632 | Slave08 Inlet Phase1 Over Voltage Warning | RW | 2 bytes | Unit:0.1
10633 | Slave09 Inlet Phase1 Over Voltage Warning | RW | 2 bytes | Unit:0.1
10634 | Slave10 Inlet Phase1 Over Voltage Warning | RW | 2 bytes | Unit:0.1
10635 | Slave11 Inlet Phase1 Over Voltage Warning | RW | 2 bytes | Unit:0.1
10636 | Slave12 Inlet Phase1 Over Voltage Warning | RW | 2 bytes | Unit:0.1
10637 | Slave13 Inlet Phase1 Over Voltage Warning | RW | 2 bytes | Unit:0.1
10638 | Slave14 Inlet Phase1 Over Voltage Warning | RW | 2 bytes | Unit:0.1
10639 | Slave15 Inlet Phase1 Over Voltage Warning | RW | 2 bytes | Unit:0.1
10640 | Master Inlet Phase2 Over Voltage Warning | RW | 2 bytes | Unit:0.1
10641 | Slave01 Inlet Phase2 Over Voltage Warning | RW | 2 bytes | Unit:0.1
10642 | Slave02 Inlet Phase2 Over Voltage Warning | RW | 2 bytes | Unit:0.1
10643 | Slave03 Inlet Phase2 Over Voltage Warning | RW | 2 bytes | Unit:0.1
10644 | Slave04 Inlet Phase2 Over Voltage Warning | RW | 2 bytes | Unit:0.1
10645 | Slave05 Inlet Phase2 Over Voltage Warning | RW | 2 bytes | Unit:0.1
10646 | Slave06 Inlet Phase2 Over Voltage Warning | RW | 2 bytes | Unit:0.1
10647 | Slave07 Inlet Phase2 Over Voltage Warning | RW | 2 bytes | Unit:0.1
10648 | Slave08 Inlet Phase2 Over Voltage Warning | RW | 2 bytes | Unit:0.1
10649 | Slave09 Inlet Phase2 Over Voltage Warning | RW | 2 bytes | Unit:0.1
10650 | Slave10 Inlet Phase2 Over Voltage Warning | RW | 2 bytes | Unit:0.1
10651 | Slave11 Inlet Phase2 Over Voltage Warning | RW | 2 bytes | Unit:0.1
10652 | Slave12 Inlet Phase2 Over Voltage Warning | RW | 2 bytes | Unit:0.1
10653 | Slave13 Inlet Phase2 Over Voltage Warning | RW | 2 bytes | Unit:0.1
10654 | Slave14 Inlet Phase2 Over Voltage Warning | RW | 2 bytes | Unit:0.1
10655 | Slave15 Inlet Phase2 Over Voltage Warning | RW | 2 bytes | Unit:0.1
10656 | Master Inlet Phase3 Over Voltage Warning | RW | 2 bytes | Unit:0.1
10657 | Slave01 Inlet Phase3 Over Voltage Warning | RW | 2 bytes | Unit:0.1
10658 | Slave02 Inlet Phase3 Over Voltage Warning | RW | 2 bytes | Unit:0.1
10659 | Slave03 Inlet Phase3 Over Voltage Warning | RW | 2 bytes | Unit:0.1
10660 | Slave04 Inlet Phase3 Over Voltage Warning | RW | 2 bytes | Unit:0.1
10661 | Slave05 Inlet Phase3 Over Voltage Warning | RW | 2 bytes | Unit:0.1
10662 | Slave06 Inlet Phase3 Over Voltage Warning | RW | 2 bytes | Unit:0.1
10663 | Slave07 Inlet Phase3 Over Voltage Warning | RW | 2 bytes | Unit:0.1
10664 | Slave08 Inlet Phase3 Over Voltage Warning | RW | 2 bytes | Unit:0.1
10665 | Slave09 Inlet Phase3 Over Voltage Warning | RW | 2 bytes | Unit:0.1
10666 | Slave10 Inlet Phase3 Over Voltage Warning | RW | 2 bytes | Unit:0.1
10667 | Slave11 Inlet Phase3 Over Voltage Warning | RW | 2 bytes | Unit:0.1
10668 | Slave12 Inlet Phase3 Over Voltage Warning | RW | 2 bytes | Unit:0.1
10669 | Slave13 Inlet Phase3 Over Voltage Warning | RW | 2 bytes | Unit:0.1
10670 | Slave14 Inlet Phase3 Over Voltage Warning | RW | 2 bytes | Unit:0.1
10671 | Slave15 Inlet Phase3 Over Voltage Warning | RW | 2 bytes | Unit:0.1
10672 | Master Inlet Phase1 Over Voltage Critical | RW | 2 bytes | Unit:0.1
10673 | Slave01 Inlet Phase1 Over Voltage Critical | RW | 2 bytes | Unit:0.1
10674 | Slave02 Inlet Phase1 Over Voltage Critical | RW | 2 bytes | Unit:0.1
10675 | Slave03 Inlet Phase1 Over Voltage Critical | RW | 2 bytes | Unit:0.1
10676 | Slave04 Inlet Phase1 Over Voltage Critical | RW | 2 bytes | Unit:0.1
10677 | Slave05 Inlet Phase1 Over Voltage Critical | RW | 2 bytes | Unit:0.1
10678 | Slave06 Inlet Phase1 Over Voltage Critical | RW | 2 bytes | Unit:0.1
10679 | Slave07 Inlet Phase1 Over Voltage Critical | RW | 2 bytes | Unit:0.1
10680 | Slave08 Inlet Phase1 Over Voltage Critical | RW | 2 bytes | Unit:0.1
10681 | Slave09 Inlet Phase1 Over Voltage Critical | RW | 2 bytes | Unit:0.1
10682 | Slave10 Inlet Phase1 Over Voltage Critical | RW | 2 bytes | Unit:0.1
10683 | Slave11 Inlet Phase1 Over Voltage Critical | RW | 2 bytes | Unit:0.1
10684 | Slave12 Inlet Phase1 Over Voltage Critical | RW | 2 bytes | Unit:0.1
10685 | Slave13 Inlet Phase1 Over Voltage Critical | RW | 2 bytes | Unit:0.1
10686 | Slave14 Inlet Phase1 Over Voltage Critical | RW | 2 bytes | Unit:0.1
10687 | Slave15 Inlet Phase1 Over Voltage Critical | RW | 2 bytes | Unit:0.1
10688 | Master Inlet Phase2 Over Voltage Critical | RW | 2 bytes | Unit:0.1
10689 | Slave01 Inlet Phase2 Over Voltage Critical | RW | 2 bytes | Unit:0.1
10690 | Slave02 Inlet Phase2 Over Voltage Critical | RW | 2 bytes | Unit:0.1
10691 | Slave03 Inlet Phase2 Over Voltage Critical | RW | 2 bytes | Unit:0.1
10692 | Slave04 Inlet Phase2 Over Voltage Critical | RW | 2 bytes | Unit:0.1
10693 | Slave05 Inlet Phase2 Over Voltage Critical | RW | 2 bytes | Unit:0.1
10694 | Slave06 Inlet Phase2 Over Voltage Critical | RW | 2 bytes | Unit:0.1
10695 | Slave07 Inlet Phase2 Over Voltage Critical | RW | 2 bytes | Unit:0.1
10696 | Slave08 Inlet Phase2 Over Voltage Critical | RW | 2 bytes | Unit:0.1
10697 | Slave09 Inlet Phase2 Over Voltage Critical | RW | 2 bytes | Unit:0.1
10698 | Slave10 Inlet Phase2 Over Voltage Critical | RW | 2 bytes | Unit:0.1
10699 | Slave11 Inlet Phase2 Over Voltage Critical | RW | 2 bytes | Unit:0.1
10700 | Slave12 Inlet Phase2 Over Voltage Critical | RW | 2 bytes | Unit:0.1
10701 | Slave13 Inlet Phase2 Over Voltage Critical | RW | 2 bytes | Unit:0.1
10702 | Slave14 Inlet Phase2 Over Voltage Critical | RW | 2 bytes | Unit:0.1
10703 | Slave15 Inlet Phase2 Over Voltage Critical | RW | 2 bytes | Unit:0.1
10704 | Master Inlet Phase3 Over Voltage Critical | RW | 2 bytes | Unit:0.1
10705 | Slave01 Inlet Phase3 Over Voltage Critical | RW | 2 bytes | Unit:0.1
10706 | Slave02 Inlet Phase3 Over Voltage Critical | RW | 2 bytes | Unit:0.1
10707 | Slave03 Inlet Phase3 Over Voltage Critical | RW | 2 bytes | Unit:0.1
10708 | Slave04 Inlet Phase3 Over Voltage Critical | RW | 2 bytes | Unit:0.1
10709 | Slave05 Inlet Phase3 Over Voltage Critical | RW | 2 bytes | Unit:0.1
10710 | Slave06 Inlet Phase3 Over Voltage Critical | RW | 2 bytes | Unit:0.1
10711 | Slave07 Inlet Phase3 Over Voltage Critical | RW | 2 bytes | Unit:0.1
10712 | Slave08 Inlet Phase3 Over Voltage Critical | RW | 2 bytes | Unit:0.1
10713 | Slave09 Inlet Phase3 Over Voltage Critical | RW | 2 bytes | Unit:0.1
10714 | Slave10 Inlet Phase3 Over Voltage Critical | RW | 2 bytes | Unit:0.1
10715 | Slave11 Inlet Phase3 Over Voltage Critical | RW | 2 bytes | Unit:0.1
10716 | Slave12 Inlet Phase3 Over Voltage Critical | RW | 2 bytes | Unit:0.1
10717 | Slave13 Inlet Phase3 Over Voltage Critical | RW | 2 bytes | Unit:0.1
10718 | Slave14 Inlet Phase3 Over Voltage Critical | RW | 2 bytes | Unit:0.1
10719 | Slave15 Inlet Phase3 Over Voltage Critical | RW | 2 bytes | Unit:0.1
10720 | Master Inlet Phase1 Total Over Current Warning | RW | 2 bytes | Unit:0.01
10721 | Slave01 Inlet Phase1 Total Over Current Warning | RW | 2 bytes | Unit:0.01
10722 | Slave02 Inlet Phase1 Total Over Current Warning | RW | 2 bytes | Unit:0.01
10723 | Slave03 Inlet Phase1 Total Over Current Warning | RW | 2 bytes | Unit:0.01
10724 | Slave04 Inlet Phase1 Total Over Current Warning | RW | 2 bytes | Unit:0.01
10725 | Slave05 Inlet Phase1 Total Over Current Warning | RW | 2 bytes | Unit:0.01
10726 | Slave06 Inlet Phase1 Total Over Current Warning | RW | 2 bytes | Unit:0.01
10727 | Slave07 Inlet Phase1 Total Over Current Warning | RW | 2 bytes | Unit:0.01
10728 | Slave08 Inlet Phase1 Total Over Current Warning | RW | 2 bytes | Unit:0.01
10729 | Slave09 Inlet Phase1 Total Over Current Warning | RW | 2 bytes | Unit:0.01
10730 | Slave10 Inlet Phase1 Total Over Current Warning | RW | 2 bytes | Unit:0.01
10731 | Slave11 Inlet Phase1 Total Over Current Warning | RW | 2 bytes | Unit:0.01
10732 | Slave12 Inlet Phase1 Total Over Current Warning | RW | 2 bytes | Unit:0.01
10733 | Slave13 Inlet Phase1 Total Over Current Warning | RW | 2 bytes | Unit:0.01
10734 | Slave14 Inlet Phase1 Total Over Current Warning | RW | 2 bytes | Unit:0.01
10735 | Slave15 Inlet Phase1 Total Over Current Warning | RW | 2 bytes | Unit:0.01
10736 | Master Inlet Phase2 Total Over Current Warning | RW | 2 bytes | Unit:0.01
10737 | Slave01 Inlet Phase2 Total Over Current Warning | RW | 2 bytes | Unit:0.01
10738 | Slave02 Inlet Phase2 Total Over Current Warning | RW | 2 bytes | Unit:0.01
10739 | Slave03 Inlet Phase2 Total Over Current Warning | RW | 2 bytes | Unit:0.01
10740 | Slave04 Inlet Phase2 Total Over Current Warning | RW | 2 bytes | Unit:0.01
10741 | Slave05 Inlet Phase2 Total Over Current Warning | RW | 2 bytes | Unit:0.01
10742 | Slave06 Inlet Phase2 Total Over Current Warning | RW | 2 bytes | Unit:0.01
10743 | Slave07 Inlet Phase2 Total Over Current Warning | RW | 2 bytes | Unit:0.01
10744 | Slave08 Inlet Phase2 Total Over Current Warning | RW | 2 bytes | Unit:0.01
10745 | Slave09 Inlet Phase2 Total Over Current Warning | RW | 2 bytes | Unit:0.01
10746 | Slave10 Inlet Phase2 Total Over Current Warning | RW | 2 bytes | Unit:0.01
10747 | Slave11 Inlet Phase2 Total Over Current Warning | RW | 2 bytes | Unit:0.01
10748 | Slave12 Inlet Phase2 Total Over Current Warning | RW | 2 bytes | Unit:0.01
10749 | Slave13 Inlet Phase2 Total Over Current Warning | RW | 2 bytes | Unit:0.01
10750 | Slave14 Inlet Phase2 Total Over Current Warning | RW | 2 bytes | Unit:0.01
10751 | Slave15 Inlet Phase2 Total Over Current Warning | RW | 2 bytes | Unit:0.01
10752 | Master Inlet Phase3 Total Over Current Warning | RW | 2 bytes | Unit:0.01
10753 | Slave01 Inlet Phase3 Total Over Current Warning | RW | 2 bytes | Unit:0.01
10754 | Slave02 Inlet Phase3 Total Over Current Warning | RW | 2 bytes | Unit:0.01
10755 | Slave03 Inlet Phase3 Total Over Current Warning | RW | 2 bytes | Unit:0.01
10756 | Slave04 Inlet Phase3 Total Over Current Warning | RW | 2 bytes | Unit:0.01
10757 | Slave05 Inlet Phase3 Total Over Current Warning | RW | 2 bytes | Unit:0.01
10758 | Slave06 Inlet Phase3 Total Over Current Warning | RW | 2 bytes | Unit:0.01
10759 | Slave07 Inlet Phase3 Total Over Current Warning | RW | 2 bytes | Unit:0.01
10760 | Slave08 Inlet Phase3 Total Over Current Warning | RW | 2 bytes | Unit:0.01
10761 | Slave09 Inlet Phase3 Total Over Current Warning | RW | 2 bytes | Unit:0.01
10762 | Slave10 Inlet Phase3 Total Over Current Warning | RW | 2 bytes | Unit:0.01
10763 | Slave11 Inlet Phase3 Total Over Current Warning | RW | 2 bytes | Unit:0.01
10764 | Slave12 Inlet Phase3 Total Over Current Warning | RW | 2 bytes | Unit:0.01
10765 | Slave13 Inlet Phase3 Total Over Current Warning | RW | 2 bytes | Unit:0.01
10766 | Slave14 Inlet Phase3 Total Over Current Warning | RW | 2 bytes | Unit:0.01
10767 | Slave15 Inlet Phase3 Total Over Current Warning | RW | 2 bytes | Unit:0.01
10768 | Master Inlet Phase1 Total Over Current Critical | RW | 2 bytes | Unit:0.01
10769 | Slave01 Inlet Phase1 Total Over Current Critical | RW | 2 bytes | Unit:0.01
10770 | Slave02 Inlet Phase1 Total Over Current Critical | RW | 2 bytes | Unit:0.01
10771 | Slave03 Inlet Phase1 Total Over Current Critical | RW | 2 bytes | Unit:0.01
10772 | Slave04 Inlet Phase1 Total Over Current Critical | RW | 2 bytes | Unit:0.01
10773 | Slave05 Inlet Phase1 Total Over Current Critical | RW | 2 bytes | Unit:0.01
10774 | Slave06 Inlet Phase1 Total Over Current Critical | RW | 2 bytes | Unit:0.01
10775 | Slave07 Inlet Phase1 Total Over Current Critical | RW | 2 bytes | Unit:0.01
10776 | Slave08 Inlet Phase1 Total Over Current Critical | RW | 2 bytes | Unit:0.01
10777 | Slave09 Inlet Phase1 Total Over Current Critical | RW | 2 bytes | Unit:0.01
10778 | Slave10 Inlet Phase1 Total Over Current Critical | RW | 2 bytes | Unit:0.01
10779 | Slave11 Inlet Phase1 Total Over Current Critical | RW | 2 bytes | Unit:0.01
10780 | Slave12 Inlet Phase1 Total Over Current Critical | RW | 2 bytes | Unit:0.01
10781 | Slave13 Inlet Phase1 Total Over Current Critical | RW | 2 bytes | Unit:0.01
10782 | Slave14 Inlet Phase1 Total Over Current Critical | RW | 2 bytes | Unit:0.01
10783 | Slave15 Inlet Phase1 Total Over Current Critical | RW | 2 bytes | Unit:0.01
10784 | Master Inlet Phase2 Total Over Current Critical | RW | 2 bytes | Unit:0.01
10785 | Slave01 Inlet Phase2 Total Over Current Critical | RW | 2 bytes | Unit:0.01
10786 | Slave02 Inlet Phase2 Total Over Current Critical | RW | 2 bytes | Unit:0.01
10787 | Slave03 Inlet Phase2 Total Over Current Critical | RW | 2 bytes | Unit:0.01
10788 | Slave04 Inlet Phase2 Total Over Current Critical | RW | 2 bytes | Unit:0.01
10789 | Slave05 Inlet Phase2 Total Over Current Critical | RW | 2 bytes | Unit:0.01
10790 | Slave06 Inlet Phase2 Total Over Current Critical | RW | 2 bytes | Unit:0.01
10791 | Slave07 Inlet Phase2 Total Over Current Critical | RW | 2 bytes | Unit:0.01
10792 | Slave08 Inlet Phase2 Total Over Current Critical | RW | 2 bytes | Unit:0.01
10793 | Slave09 Inlet Phase2 Total Over Current Critical | RW | 2 bytes | Unit:0.01
10794 | Slave10 Inlet Phase2 Total Over Current Critical | RW | 2 bytes | Unit:0.01
10795 | Slave11 Inlet Phase2 Total Over Current Critical | RW | 2 bytes | Unit:0.01
10796 | Slave12 Inlet Phase2 Total Over Current Critical | RW | 2 bytes | Unit:0.01
10797 | Slave13 Inlet Phase2 Total Over Current Critical | RW | 2 bytes | Unit:0.01
10798 | Slave14 Inlet Phase2 Total Over Current Critical | RW | 2 bytes | Unit:0.01
10799 | Slave15 Inlet Phase2 Total Over Current Critical | RW | 2 bytes | Unit:0.01
10800 | Master Inlet Phase3 Total Over Current Critical | RW | 2 bytes | Unit:0.01
10801 | Slave01 Inlet Phase3 Total Over Current Critical | RW | 2 bytes | Unit:0.01
10802 | Slave02 Inlet Phase3 Total Over Current Critical | RW | 2 bytes | Unit:0.01
10803 | Slave03 Inlet Phase3 Total Over Current Critical | RW | 2 bytes | Unit:0.01
10804 | Slave04 Inlet Phase3 Total Over Current Critical | RW | 2 bytes | Unit:0.01
10805 | Slave05 Inlet Phase3 Total Over Current Critical | RW | 2 bytes | Unit:0.01
10806 | Slave06 Inlet Phase3 Total Over Current Critical | RW | 2 bytes | Unit:0.01
10807 | Slave07 Inlet Phase3 Total Over Current Critical | RW | 2 bytes | Unit:0.01
10808 | Slave08 Inlet Phase3 Total Over Current Critical | RW | 2 bytes | Unit:0.01
10809 | Slave09 Inlet Phase3 Total Over Current Critical | RW | 2 bytes | Unit:0.01
10810 | Slave10 Inlet Phase3 Total Over Current Critical | RW | 2 bytes | Unit:0.01
10811 | Slave11 Inlet Phase3 Total Over Current Critical | RW | 2 bytes | Unit:0.01
10812 | Slave12 Inlet Phase3 Total Over Current Critical | RW | 2 bytes | Unit:0.01
10813 | Slave13 Inlet Phase3 Total Over Current Critical | RW | 2 bytes | Unit:0.01
10814 | Slave14 Inlet Phase3 Total Over Current Critical | RW | 2 bytes | Unit:0.01
10815 | Slave15 Inlet Phase3 Total Over Current Critical | RW | 2 bytes | Unit:0.01
10816 | Master Inlet Phase1 Branch1 Over Current Warning | RW | 2 bytes | Unit:0.01
10817 | Slave01 Inlet Phase1 Branch1 Over Current Warning | RW | 2 bytes | Unit:0.01
10818 | Slave02 Inlet Phase1 Branch1 Over Current Warning | RW | 2 bytes | Unit:0.01
10819 | Slave03 Inlet Phase1 Branch1 Over Current Warning | RW | 2 bytes | Unit:0.01
10820 | Slave04 Inlet Phase1 Branch1 Over Current Warning | RW | 2 bytes | Unit:0.01
10821 | Slave05 Inlet Phase1 Branch1 Over Current Warning | RW | 2 bytes | Unit:0.01
10822 | Slave06 Inlet Phase1 Branch1 Over Current Warning | RW | 2 bytes | Unit:0.01
10823 | Slave07 Inlet Phase1 Branch1 Over Current Warning | RW | 2 bytes | Unit:0.01
10824 | Slave08 Inlet Phase1 Branch1 Over Current Warning | RW | 2 bytes | Unit:0.01
10825 | Slave09 Inlet Phase1 Branch1 Over Current Warning | RW | 2 bytes | Unit:0.01
10826 | Slave10 Inlet Phase1 Branch1 Over Current Warning | RW | 2 bytes | Unit:0.01
10827 | Slave11 Inlet Phase1 Branch1 Over Current Warning | RW | 2 bytes | Unit:0.01
10828 | Slave12 Inlet Phase1 Branch1 Over Current Warning | RW | 2 bytes | Unit:0.01
10829 | Slave13 Inlet Phase1 Branch1 Over Current Warning | RW | 2 bytes | Unit:0.01
10830 | Slave14 Inlet Phase1 Branch1 Over Current Warning | RW | 2 bytes | Unit:0.01
10831 | Slave15 Inlet Phase1 Branch1 Over Current Warning | RW | 2 bytes | Unit:0.01
10832 | Master Inlet Phase2 Branch1 Over Current Warning | RW | 2 bytes | Unit:0.01
10833 | Slave01 Inlet Phase2 Branch1 Over Current Warning | RW | 2 bytes | Unit:0.01
10834 | Slave02 Inlet Phase2 Branch1 Over Current Warning | RW | 2 bytes | Unit:0.01
10835 | Slave03 Inlet Phase2 Branch1 Over Current Warning | RW | 2 bytes | Unit:0.01
10836 | Slave04 Inlet Phase2 Branch1 Over Current Warning | RW | 2 bytes | Unit:0.01
10837 | Slave05 Inlet Phase2 Branch1 Over Current Warning | RW | 2 bytes | Unit:0.01
10838 | Slave06 Inlet Phase2 Branch1 Over Current Warning | RW | 2 bytes | Unit:0.01
10839 | Slave07 Inlet Phase2 Branch1 Over Current Warning | RW | 2 bytes | Unit:0.01
10840 | Slave08 Inlet Phase2 Branch1 Over Current Warning | RW | 2 bytes | Unit:0.01
10841 | Slave09 Inlet Phase2 Branch1 Over Current Warning | RW | 2 bytes | Unit:0.01
10842 | Slave10 Inlet Phase2 Branch1 Over Current Warning | RW | 2 bytes | Unit:0.01
10843 | Slave11 Inlet Phase2 Branch1 Over Current Warning | RW | 2 bytes | Unit:0.01
10844 | Slave12 Inlet Phase2 Branch1 Over Current Warning | RW | 2 bytes | Unit:0.01
10845 | Slave13 Inlet Phase2 Branch1 Over Current Warning | RW | 2 bytes | Unit:0.01
10846 | Slave14 Inlet Phase2 Branch1 Over Current Warning | RW | 2 bytes | Unit:0.01
10847 | Slave15 Inlet Phase2 Branch1 Over Current Warning | RW | 2 bytes | Unit:0.01
10848 | Master Inlet Phase3 Branch1 Over Current Warning | RW | 2 bytes | Unit:0.01
10849 | Slave01 Inlet Phase3 Branch1 Over Current Warning | RW | 2 bytes | Unit:0.01
10850 | Slave02 Inlet Phase3 Branch1 Over Current Warning | RW | 2 bytes | Unit:0.01
10851 | Slave03 Inlet Phase3 Branch1 Over Current Warning | RW | 2 bytes | Unit:0.01
10852 | Slave04 Inlet Phase3 Branch1 Over Current Warning | RW | 2 bytes | Unit:0.01
10853 | Slave05 Inlet Phase3 Branch1 Over Current Warning | RW | 2 bytes | Unit:0.01
10854 | Slave06 Inlet Phase3 Branch1 Over Current Warning | RW | 2 bytes | Unit:0.01
10855 | Slave07 Inlet Phase3 Branch1 Over Current Warning | RW | 2 bytes | Unit:0.01
10856 | Slave08 Inlet Phase3 Branch1 Over Current Warning | RW | 2 bytes | Unit:0.01
10857 | Slave09 Inlet Phase3 Branch1 Over Current Warning | RW | 2 bytes | Unit:0.01
10858 | Slave10 Inlet Phase3 Branch1 Over Current Warning | RW | 2 bytes | Unit:0.01
10859 | Slave11 Inlet Phase3 Branch1 Over Current Warning | RW | 2 bytes | Unit:0.01
10860 | Slave12 Inlet Phase3 Branch1 Over Current Warning | RW | 2 bytes | Unit:0.01
10861 | Slave13 Inlet Phase3 Branch1 Over Current Warning | RW | 2 bytes | Unit:0.01
10862 | Slave14 Inlet Phase3 Branch1 Over Current Warning | RW | 2 bytes | Unit:0.01
10863 | Slave15 Inlet Phase3 Branch1 Over Current Warning | RW | 2 bytes | Unit:0.01
10864 | Master Inlet Phase1 Branch1 Over Current Critical | RW | 2 bytes | Unit:0.01
10865 | Slave01 Inlet Phase1 Branch1 Over Current Critical | RW | 2 bytes | Unit:0.01
10866 | Slave02 Inlet Phase1 Branch1 Over Current Critical | RW | 2 bytes | Unit:0.01
10867 | Slave03 Inlet Phase1 Branch1 Over Current Critical | RW | 2 bytes | Unit:0.01
10868 | Slave04 Inlet Phase1 Branch1 Over Current Critical | RW | 2 bytes | Unit:0.01
10869 | Slave05 Inlet Phase1 Branch1 Over Current Critical | RW | 2 bytes | Unit:0.01
10870 | Slave06 Inlet Phase1 Branch1 Over Current Critical | RW | 2 bytes | Unit:0.01
10871 | Slave07 Inlet Phase1 Branch1 Over Current Critical | RW | 2 bytes | Unit:0.01
10872 | Slave08 Inlet Phase1 Branch1 Over Current Critical | RW | 2 bytes | Unit:0.01
10873 | Slave09 Inlet Phase1 Branch1 Over Current Critical | RW | 2 bytes | Unit:0.01
10874 | Slave10 Inlet Phase1 Branch1 Over Current Critical | RW | 2 bytes | Unit:0.01
10875 | Slave11 Inlet Phase1 Branch1 Over Current Critical | RW | 2 bytes | Unit:0.01
10876 | Slave12 Inlet Phase1 Branch1 Over Current Critical | RW | 2 bytes | Unit:0.01
10877 | Slave13 Inlet Phase1 Branch1 Over Current Critical | RW | 2 bytes | Unit:0.01
10878 | Slave14 Inlet Phase1 Branch1 Over Current Critical | RW | 2 bytes | Unit:0.01
10879 | Slave15 Inlet Phase1 Branch1 Over Current Critical | RW | 2 bytes | Unit:0.01
10880 | Master Inlet Phase2 Branch1 Over Current Critical | RW | 2 bytes | Unit:0.01
10881 | Slave01 Inlet Phase2 Branch1 Over Current Critical | RW | 2 bytes | Unit:0.01
10882 | Slave02 Inlet Phase2 Branch1 Over Current Critical | RW | 2 bytes | Unit:0.01
10883 | Slave03 Inlet Phase2 Branch1 Over Current Critical | RW | 2 bytes | Unit:0.01
10884 | Slave04 Inlet Phase2 Branch1 Over Current Critical | RW | 2 bytes | Unit:0.01
10885 | Slave05 Inlet Phase2 Branch1 Over Current Critical | RW | 2 bytes | Unit:0.01
10886 | Slave06 Inlet Phase2 Branch1 Over Current Critical | RW | 2 bytes | Unit:0.01
10887 | Slave07 Inlet Phase2 Branch1 Over Current Critical | RW | 2 bytes | Unit:0.01
10888 | Slave08 Inlet Phase2 Branch1 Over Current Critical | RW | 2 bytes | Unit:0.01
10889 | Slave09 Inlet Phase2 Branch1 Over Current Critical | RW | 2 bytes | Unit:0.01
10890 | Slave10 Inlet Phase2 Branch1 Over Current Critical | RW | 2 bytes | Unit:0.01
10891 | Slave11 Inlet Phase2 Branch1 Over Current Critical | RW | 2 bytes | Unit:0.01
10892 | Slave12 Inlet Phase2 Branch1 Over Current Critical | RW | 2 bytes | Unit:0.01
10893 | Slave13 Inlet Phase2 Branch1 Over Current Critical | RW | 2 bytes | Unit:0.01
10894 | Slave14 Inlet Phase2 Branch1 Over Current Critical | RW | 2 bytes | Unit:0.01
10895 | Slave15 Inlet Phase2 Branch1 Over Current Critical | RW | 2 bytes | Unit:0.01
10896 | Master Inlet Phase3 Branch1 Over Current Critical | RW | 2 bytes | Unit:0.01
10897 | Slave01 Inlet Phase3 Branch1 Over Current Critical | RW | 2 bytes | Unit:0.01
10898 | Slave02 Inlet Phase3 Branch1 Over Current Critical | RW | 2 bytes | Unit:0.01
10899 | Slave03 Inlet Phase3 Branch1 Over Current Critical | RW | 2 bytes | Unit:0.01
10900 | Slave04 Inlet Phase3 Branch1 Over Current Critical | RW | 2 bytes | Unit:0.01
10901 | Slave05 Inlet Phase3 Branch1 Over Current Critical | RW | 2 bytes | Unit:0.01
10902 | Slave06 Inlet Phase3 Branch1 Over Current Critical | RW | 2 bytes | Unit:0.01
10903 | Slave07 Inlet Phase3 Branch1 Over Current Critical | RW | 2 bytes | Unit:0.01
10904 | Slave08 Inlet Phase3 Branch1 Over Current Critical | RW | 2 bytes | Unit:0.01
10905 | Slave09 Inlet Phase3 Branch1 Over Current Critical | RW | 2 bytes | Unit:0.01
10906 | Slave10 Inlet Phase3 Branch1 Over Current Critical | RW | 2 bytes | Unit:0.01
10907 | Slave11 Inlet Phase3 Branch1 Over Current Critical | RW | 2 bytes | Unit:0.01
10908 | Slave12 Inlet Phase3 Branch1 Over Current Critical | RW | 2 bytes | Unit:0.01
10909 | Slave13 Inlet Phase3 Branch1 Over Current Critical | RW | 2 bytes | Unit:0.01
10910 | Slave14 Inlet Phase3 Branch1 Over Current Critical | RW | 2 bytes | Unit:0.01
10911 | Slave15 Inlet Phase3 Branch1 Over Current Critical | RW | 2 bytes | Unit:0.01
10912 | Master Inlet Phase1 Branch2 Over Current Warning | RW | 2 bytes | Unit:0.01
10913 | Slave01 Inlet Phase1 Branch2 Over Current Warning | RW | 2 bytes | Unit:0.01
10914 | Slave02 Inlet Phase1 Branch2 Over Current Warning | RW | 2 bytes | Unit:0.01
10915 | Slave03 Inlet Phase1 Branch2 Over Current Warning | RW | 2 bytes | Unit:0.01
10916 | Slave04 Inlet Phase1 Branch2 Over Current Warning | RW | 2 bytes | Unit:0.01
10917 | Slave05 Inlet Phase1 Branch2 Over Current Warning | RW | 2 bytes | Unit:0.01
10918 | Slave06 Inlet Phase1 Branch2 Over Current Warning | RW | 2 bytes | Unit:0.01
10919 | Slave07 Inlet Phase1 Branch2 Over Current Warning | RW | 2 bytes | Unit:0.01
10920 | Slave08 Inlet Phase1 Branch2 Over Current Warning | RW | 2 bytes | Unit:0.01
10921 | Slave09 Inlet Phase1 Branch2 Over Current Warning | RW | 2 bytes | Unit:0.01
10922 | Slave10 Inlet Phase1 Branch2 Over Current Warning | RW | 2 bytes | Unit:0.01
10923 | Slave11 Inlet Phase1 Branch2 Over Current Warning | RW | 2 bytes | Unit:0.01
10924 | Slave12 Inlet Phase1 Branch2 Over Current Warning | RW | 2 bytes | Unit:0.01
10925 | Slave13 Inlet Phase1 Branch2 Over Current Warning | RW | 2 bytes | Unit:0.01
10926 | Slave14 Inlet Phase1 Branch2 Over Current Warning | RW | 2 bytes | Unit:0.01
10927 | Slave15 Inlet Phase1 Branch2 Over Current Warning | RW | 2 bytes | Unit:0.01
10928 | Master Inlet Phase2 Branch2 Over Current Warning | RW | 2 bytes | Unit:0.01
10929 | Slave01 Inlet Phase2 Branch2 Over Current Warning | RW | 2 bytes | Unit:0.01
10930 | Slave02 Inlet Phase2 Branch2 Over Current Warning | RW | 2 bytes | Unit:0.01
10931 | Slave03 Inlet Phase2 Branch2 Over Current Warning | RW | 2 bytes | Unit:0.01
10932 | Slave04 Inlet Phase2 Branch2 Over Current Warning | RW | 2 bytes | Unit:0.01
10933 | Slave05 Inlet Phase2 Branch2 Over Current Warning | RW | 2 bytes | Unit:0.01
10934 | Slave06 Inlet Phase2 Branch2 Over Current Warning | RW | 2 bytes | Unit:0.01
10935 | Slave07 Inlet Phase2 Branch2 Over Current Warning | RW | 2 bytes | Unit:0.01
10936 | Slave08 Inlet Phase2 Branch2 Over Current Warning | RW | 2 bytes | Unit:0.01
10937 | Slave09 Inlet Phase2 Branch2 Over Current Warning | RW | 2 bytes | Unit:0.01
10938 | Slave10 Inlet Phase2 Branch2 Over Current Warning | RW | 2 bytes | Unit:0.01
10939 | Slave11 Inlet Phase2 Branch2 Over Current Warning | RW | 2 bytes | Unit:0.01
10940 | Slave12 Inlet Phase2 Branch2 Over Current Warning | RW | 2 bytes | Unit:0.01
10941 | Slave13 Inlet Phase2 Branch2 Over Current Warning | RW | 2 bytes | Unit:0.01
10942 | Slave14 Inlet Phase2 Branch2 Over Current Warning | RW | 2 bytes | Unit:0.01
10943 | Slave15 Inlet Phase2 Branch2 Over Current Warning | RW | 2 bytes | Unit:0.01
10944 | Master Inlet Phase3 Branch2 Over Current Warning | RW | 2 bytes | Unit:0.01
10945 | Slave01 Inlet Phase3 Branch2 Over Current Warning | RW | 2 bytes | Unit:0.01
10946 | Slave02 Inlet Phase3 Branch2 Over Current Warning | RW | 2 bytes | Unit:0.01
10947 | Slave03 Inlet Phase3 Branch2 Over Current Warning | RW | 2 bytes | Unit:0.01
10948 | Slave04 Inlet Phase3 Branch2 Over Current Warning | RW | 2 bytes | Unit:0.01
10949 | Slave05 Inlet Phase3 Branch2 Over Current Warning | RW | 2 bytes | Unit:0.01
10950 | Slave06 Inlet Phase3 Branch2 Over Current Warning | RW | 2 bytes | Unit:0.01
10951 | Slave07 Inlet Phase3 Branch2 Over Current Warning | RW | 2 bytes | Unit:0.01
10952 | Slave08 Inlet Phase3 Branch2 Over Current Warning | RW | 2 bytes | Unit:0.01
10953 | Slave09 Inlet Phase3 Branch2 Over Current Warning | RW | 2 bytes | Unit:0.01
10954 | Slave10 Inlet Phase3 Branch2 Over Current Warning | RW | 2 bytes | Unit:0.01
10955 | Slave11 Inlet Phase3 Branch2 Over Current Warning | RW | 2 bytes | Unit:0.01
10956 | Slave12 Inlet Phase3 Branch2 Over Current Warning | RW | 2 bytes | Unit:0.01
10957 | Slave13 Inlet Phase3 Branch2 Over Current Warning | RW | 2 bytes | Unit:0.01
10958 | Slave14 Inlet Phase3 Branch2 Over Current Warning | RW | 2 bytes | Unit:0.01
10959 | Slave15 Inlet Phase3 Branch2 Over Current Warning | RW | 2 bytes | Unit:0.01
10960 | Master Inlet Phase1 Branch2 Over Current Critical | RW | 2 bytes | Unit:0.01
10961 | Slave01 Inlet Phase1 Branch2 Over Current Critical | RW | 2 bytes | Unit:0.01
10962 | Slave02 Inlet Phase1 Branch2 Over Current Critical | RW | 2 bytes | Unit:0.01
10963 | Slave03 Inlet Phase1 Branch2 Over Current Critical | RW | 2 bytes | Unit:0.01
10964 | Slave04 Inlet Phase1 Branch2 Over Current Critical | RW | 2 bytes | Unit:0.01
10965 | Slave05 Inlet Phase1 Branch2 Over Current Critical | RW | 2 bytes | Unit:0.01
10966 | Slave06 Inlet Phase1 Branch2 Over Current Critical | RW | 2 bytes | Unit:0.01
10967 | Slave07 Inlet Phase1 Branch2 Over Current Critical | RW | 2 bytes | Unit:0.01
10968 | Slave08 Inlet Phase1 Branch2 Over Current Critical | RW | 2 bytes | Unit:0.01
10969 | Slave09 Inlet Phase1 Branch2 Over Current Critical | RW | 2 bytes | Unit:0.01
10970 | Slave10 Inlet Phase1 Branch2 Over Current Critical | RW | 2 bytes | Unit:0.01
10971 | Slave11 Inlet Phase1 Branch2 Over Current Critical | RW | 2 bytes | Unit:0.01
10972 | Slave12 Inlet Phase1 Branch2 Over Current Critical | RW | 2 bytes | Unit:0.01
10973 | Slave13 Inlet Phase1 Branch2 Over Current Critical | RW | 2 bytes | Unit:0.01
10974 | Slave14 Inlet Phase1 Branch2 Over Current Critical | RW | 2 bytes | Unit:0.01
10975 | Slave15 Inlet Phase1 Branch2 Over Current Critical | RW | 2 bytes | Unit:0.01
10976 | Master Inlet Phase2 Branch2 Over Current Critical | RW | 2 bytes | Unit:0.01
10977 | Slave01 Inlet Phase2 Branch2 Over Current Critical | RW | 2 bytes | Unit:0.01
10978 | Slave02 Inlet Phase2 Branch2 Over Current Critical | RW | 2 bytes | Unit:0.01
10979 | Slave03 Inlet Phase2 Branch2 Over Current Critical | RW | 2 bytes | Unit:0.01
10980 | Slave04 Inlet Phase2 Branch2 Over Current Critical | RW | 2 bytes | Unit:0.01
10981 | Slave05 Inlet Phase2 Branch2 Over Current Critical | RW | 2 bytes | Unit:0.01
10982 | Slave06 Inlet Phase2 Branch2 Over Current Critical | RW | 2 bytes | Unit:0.01
10983 | Slave07 Inlet Phase2 Branch2 Over Current Critical | RW | 2 bytes | Unit:0.01
10984 | Slave08 Inlet Phase2 Branch2 Over Current Critical | RW | 2 bytes | Unit:0.01
10985 | Slave09 Inlet Phase2 Branch2 Over Current Critical | RW | 2 bytes | Unit:0.01
10986 | Slave10 Inlet Phase2 Branch2 Over Current Critical | RW | 2 bytes | Unit:0.01
10987 | Slave11 Inlet Phase2 Branch2 Over Current Critical | RW | 2 bytes | Unit:0.01
10988 | Slave12 Inlet Phase2 Branch2 Over Current Critical | RW | 2 bytes | Unit:0.01
10989 | Slave13 Inlet Phase2 Branch2 Over Current Critical | RW | 2 bytes | Unit:0.01
10990 | Slave14 Inlet Phase2 Branch2 Over Current Critical | RW | 2 bytes | Unit:0.01
10991 | Slave15 Inlet Phase2 Branch2 Over Current Critical | RW | 2 bytes | Unit:0.01
10992 | Master Inlet Phase3 Branch2 Over Current Critical | RW | 2 bytes | Unit:0.01
10993 | Slave01 Inlet Phase3 Branch2 Over Current Critical | RW | 2 bytes | Unit:0.01
10994 | Slave02 Inlet Phase3 Branch2 Over Current Critical | RW | 2 bytes | Unit:0.01
10995 | Slave03 Inlet Phase3 Branch2 Over Current Critical | RW | 2 bytes | Unit:0.01
10996 | Slave04 Inlet Phase3 Branch2 Over Current Critical | RW | 2 bytes | Unit:0.01
10997 | Slave05 Inlet Phase3 Branch2 Over Current Critical | RW | 2 bytes | Unit:0.01
10998 | Slave06 Inlet Phase3 Branch2 Over Current Critical | RW | 2 bytes | Unit:0.01
10999 | Slave07 Inlet Phase3 Branch2 Over Current Critical | RW | 2 bytes | Unit:0.01
11000 | Slave08 Inlet Phase3 Branch2 Over Current Critical | RW | 2 bytes | Unit:0.01
11001 | Slave09 Inlet Phase3 Branch2 Over Current Critical | RW | 2 bytes | Unit:0.01
11002 | Slave10 Inlet Phase3 Branch2 Over Current Critical | RW | 2 bytes | Unit:0.01
11003 | Slave11 Inlet Phase3 Branch2 Over Current Critical | RW | 2 bytes | Unit:0.01
11004 | Slave12 Inlet Phase3 Branch2 Over Current Critical | RW | 2 bytes | Unit:0.01
11005 | Slave13 Inlet Phase3 Branch2 Over Current Critical | RW | 2 bytes | Unit:0.01
11006 | Slave14 Inlet Phase3 Branch2 Over Current Critical | RW | 2 bytes | Unit:0.01
11007 | Slave15 Inlet Phase3 Branch2 Over Current Critical | RW | 2 bytes | Unit:0.01
11008 | Master Inlet Leakage Current Threshold | RW | 2 bytes | Unit:1mA
11009 | Slave01 Inlet Leakage Current Threshold | RW | 2 bytes | Unit:1mA
11010 | Slave02 Inlet Leakage Current Threshold | RW | 2 bytes | Unit:1mA
11011 | Slave03 Inlet Leakage Current Threshold | RW | 2 bytes | Unit:1mA
11012 | Slave04 Inlet Leakage Current Threshold | RW | 2 bytes | Unit:1mA
11013 | Slave05 Inlet Leakage Current Threshold | RW | 2 bytes | Unit:1mA
11014 | Slave06 Inlet Leakage Current Threshold | RW | 2 bytes | Unit:1mA
11015 | Slave07 Inlet Leakage Current Threshold | RW | 2 bytes | Unit:1mA
11016 | Slave08 Inlet Leakage Current Threshold | RW | 2 bytes | Unit:1mA
11017 | Slave09 Inlet Leakage Current Threshold | RW | 2 bytes | Unit:1mA
11018 | Slave10 Inlet Leakage Current Threshold | RW | 2 bytes | Unit:1mA
11019 | Slave11 Inlet Leakage Current Threshold | RW | 2 bytes | Unit:1mA
11020 | Slave12 Inlet Leakage Current Threshold | RW | 2 bytes | Unit:1mA
11021 | Slave13 Inlet Leakage Current Threshold | RW | 2 bytes | Unit:1mA
11022 | Slave14 Inlet Leakage Current Threshold | RW | 2 bytes | Unit:1mA
11023 | Slave15 Inlet Leakage Current Threshold | RW | 2 bytes | Unit:1mA
11024 | Master Inlet Phase1 Branch1 Over PF Warning | RW | 2 bytes | Unit:0.01
11025 | Slave01 Inlet Phase1 Branch1 Over PF Warning | RW | 2 bytes | Unit:0.01
11026 | Slave02 Inlet Phase1 Branch1 Over PF Warning | RW | 2 bytes | Unit:0.01
11027 | Slave03 Inlet Phase1 Branch1 Over PF Warning | RW | 2 bytes | Unit:0.01
11028 | Slave04 Inlet Phase1 Branch1 Over PF Warning | RW | 2 bytes | Unit:0.01
11029 | Slave05 Inlet Phase1 Branch1 Over PF Warning | RW | 2 bytes | Unit:0.01
11030 | Slave06 Inlet Phase1 Branch1 Over PF Warning | RW | 2 bytes | Unit:0.01
11031 | Slave07 Inlet Phase1 Branch1 Over PF Warning | RW | 2 bytes | Unit:0.01
11032 | Slave08 Inlet Phase1 Branch1 Over PF Warning | RW | 2 bytes | Unit:0.01
11033 | Slave09 Inlet Phase1 Branch1 Over PF Warning | RW | 2 bytes | Unit:0.01
11034 | Slave10 Inlet Phase1 Branch1 Over PF Warning | RW | 2 bytes | Unit:0.01
11035 | Slave11 Inlet Phase1 Branch1 Over PF Warning | RW | 2 bytes | Unit:0.01
11036 | Slave12 Inlet Phase1 Branch1 Over PF Warning | RW | 2 bytes | Unit:0.01
11037 | Slave13 Inlet Phase1 Branch1 Over PF Warning | RW | 2 bytes | Unit:0.01
11038 | Slave14 Inlet Phase1 Branch1 Over PF Warning | RW | 2 bytes | Unit:0.01
11039 | Slave15 Inlet Phase1 Branch1 Over PF Warning | RW | 2 bytes | Unit:0.01
11040 | Master Inlet Phase2 Branch1 Over PF Warning | RW | 2 bytes | Unit:0.01
11041 | Slave01 Inlet Phase2 Branch1 Over PF Warning | RW | 2 bytes | Unit:0.01
11042 | Slave02 Inlet Phase2 Branch1 Over PF Warning | RW | 2 bytes | Unit:0.01
11043 | Slave03 Inlet Phase2 Branch1 Over PF Warning | RW | 2 bytes | Unit:0.01
11044 | Slave04 Inlet Phase2 Branch1 Over PF Warning | RW | 2 bytes | Unit:0.01
11045 | Slave05 Inlet Phase2 Branch1 Over PF Warning | RW | 2 bytes | Unit:0.01
11046 | Slave06 Inlet Phase2 Branch1 Over PF Warning | RW | 2 bytes | Unit:0.01
11047 | Slave07 Inlet Phase2 Branch1 Over PF Warning | RW | 2 bytes | Unit:0.01
11048 | Slave08 Inlet Phase2 Branch1 Over PF Warning | RW | 2 bytes | Unit:0.01
11049 | Slave09 Inlet Phase2 Branch1 Over PF Warning | RW | 2 bytes | Unit:0.01
11050 | Slave10 Inlet Phase2 Branch1 Over PF Warning | RW | 2 bytes | Unit:0.01
11051 | Slave11 Inlet Phase2 Branch1 Over PF Warning | RW | 2 bytes | Unit:0.01
11052 | Slave12 Inlet Phase2 Branch1 Over PF Warning | RW | 2 bytes | Unit:0.01
11053 | Slave13 Inlet Phase2 Branch1 Over PF Warning | RW | 2 bytes | Unit:0.01
11054 | Slave14 Inlet Phase2 Branch1 Over PF Warning | RW | 2 bytes | Unit:0.01
11055 | Slave15 Inlet Phase2 Branch1 Over PF Warning | RW | 2 bytes | Unit:0.01
11056 | Master Inlet Phase3 Branch1 Over PF Warning | RW | 2 bytes | Unit:0.01
11057 | Slave01 Inlet Phase3 Branch1 Over PF Warning | RW | 2 bytes | Unit:0.01
11058 | Slave02 Inlet Phase3 Branch1 Over PF Warning | RW | 2 bytes | Unit:0.01
11059 | Slave03 Inlet Phase3 Branch1 Over PF Warning | RW | 2 bytes | Unit:0.01
11060 | Slave04 Inlet Phase3 Branch1 Over PF Warning | RW | 2 bytes | Unit:0.01
11061 | Slave05 Inlet Phase3 Branch1 Over PF Warning | RW | 2 bytes | Unit:0.01
11062 | Slave06 Inlet Phase3 Branch1 Over PF Warning | RW | 2 bytes | Unit:0.01
11063 | Slave07 Inlet Phase3 Branch1 Over PF Warning | RW | 2 bytes | Unit:0.01
11064 | Slave08 Inlet Phase3 Branch1 Over PF Warning | RW | 2 bytes | Unit:0.01
11065 | Slave09 Inlet Phase3 Branch1 Over PF Warning | RW | 2 bytes | Unit:0.01
11066 | Slave10 Inlet Phase3 Branch1 Over PF Warning | RW | 2 bytes | Unit:0.01
11067 | Slave11 Inlet Phase3 Branch1 Over PF Warning | RW | 2 bytes | Unit:0.01
11068 | Slave12 Inlet Phase3 Branch1 Over PF Warning | RW | 2 bytes | Unit:0.01
11069 | Slave13 Inlet Phase3 Branch1 Over PF Warning | RW | 2 bytes | Unit:0.01
11070 | Slave14 Inlet Phase3 Branch1 Over PF Warning | RW | 2 bytes | Unit:0.01
11071 | Slave15 Inlet Phase3 Branch1 Over PF Warning | RW | 2 bytes | Unit:0.01
11072 | Master Inlet Phase1 Branch1 Over PF Critical | RW | 2 bytes | Unit:0.01
11073 | Slave01 Inlet Phase1 Branch1 Over PF Critical | RW | 2 bytes | Unit:0.01
11074 | Slave02 Inlet Phase1 Branch1 Over PF Critical | RW | 2 bytes | Unit:0.01
11075 | Slave03 Inlet Phase1 Branch1 Over PF Critical | RW | 2 bytes | Unit:0.01
11076 | Slave04 Inlet Phase1 Branch1 Over PF Critical | RW | 2 bytes | Unit:0.01
11077 | Slave05 Inlet Phase1 Branch1 Over PF Critical | RW | 2 bytes | Unit:0.01
11078 | Slave06 Inlet Phase1 Branch1 Over PF Critical | RW | 2 bytes | Unit:0.01
11079 | Slave07 Inlet Phase1 Branch1 Over PF Critical | RW | 2 bytes | Unit:0.01
11080 | Slave08 Inlet Phase1 Branch1 Over PF Critical | RW | 2 bytes | Unit:0.01
11081 | Slave09 Inlet Phase1 Branch1 Over PF Critical | RW | 2 bytes | Unit:0.01
11082 | Slave10 Inlet Phase1 Branch1 Over PF Critical | RW | 2 bytes | Unit:0.01
11083 | Slave11 Inlet Phase1 Branch1 Over PF Critical | RW | 2 bytes | Unit:0.01
11084 | Slave12 Inlet Phase1 Branch1 Over PF Critical | RW | 2 bytes | Unit:0.01
11085 | Slave13 Inlet Phase1 Branch1 Over PF Critical | RW | 2 bytes | Unit:0.01
11086 | Slave14 Inlet Phase1 Branch1 Over PF Critical | RW | 2 bytes | Unit:0.01
11087 | Slave15 Inlet Phase1 Branch1 Over PF Critical | RW | 2 bytes | Unit:0.01
11088 | Master Inlet Phase2 Branch1 Over PF Critical | RW | 2 bytes | Unit:0.01
11089 | Slave01 Inlet Phase2 Branch1 Over PF Critical | RW | 2 bytes | Unit:0.01
11090 | Slave02 Inlet Phase2 Branch1 Over PF Critical | RW | 2 bytes | Unit:0.01
11091 | Slave03 Inlet Phase2 Branch1 Over PF Critical | RW | 2 bytes | Unit:0.01
11092 | Slave04 Inlet Phase2 Branch1 Over PF Critical | RW | 2 bytes | Unit:0.01
11093 | Slave05 Inlet Phase2 Branch1 Over PF Critical | RW | 2 bytes | Unit:0.01
11094 | Slave06 Inlet Phase2 Branch1 Over PF Critical | RW | 2 bytes | Unit:0.01
11095 | Slave07 Inlet Phase2 Branch1 Over PF Critical | RW | 2 bytes | Unit:0.01
11096 | Slave08 Inlet Phase2 Branch1 Over PF Critical | RW | 2 bytes | Unit:0.01
11097 | Slave09 Inlet Phase2 Branch1 Over PF Critical | RW | 2 bytes | Unit:0.01
11098 | Slave10 Inlet Phase2 Branch1 Over PF Critical | RW | 2 bytes | Unit:0.01
11099 | Slave11 Inlet Phase2 Branch1 Over PF Critical | RW | 2 bytes | Unit:0.01
11100 | Slave12 Inlet Phase2 Branch1 Over PF Critical | RW | 2 bytes | Unit:0.01
11101 | Slave13 Inlet Phase2 Branch1 Over PF Critical | RW | 2 bytes | Unit:0.01
11102 | Slave14 Inlet Phase2 Branch1 Over PF Critical | RW | 2 bytes | Unit:0.01
11103 | Slave15 Inlet Phase2 Branch1 Over PF Critical | RW | 2 bytes | Unit:0.01
11104 | Master Inlet Phase3 Branch1 Over PF Critical | RW | 2 bytes | Unit:0.01
11105 | Slave01 Inlet Phase3 Branch1 Over PF Critical | RW | 2 bytes | Unit:0.01
11106 | Slave02 Inlet Phase3 Branch1 Over PF Critical | RW | 2 bytes | Unit:0.01
11107 | Slave03 Inlet Phase3 Branch1 Over PF Critical | RW | 2 bytes | Unit:0.01
11108 | Slave04 Inlet Phase3 Branch1 Over PF Critical | RW | 2 bytes | Unit:0.01
11109 | Slave05 Inlet Phase3 Branch1 Over PF Critical | RW | 2 bytes | Unit:0.01
11110 | Slave06 Inlet Phase3 Branch1 Over PF Critical | RW | 2 bytes | Unit:0.01
11111 | Slave07 Inlet Phase3 Branch1 Over PF Critical | RW | 2 bytes | Unit:0.01
11112 | Slave08 Inlet Phase3 Branch1 Over PF Critical | RW | 2 bytes | Unit:0.01
11113 | Slave09 Inlet Phase3 Branch1 Over PF Critical | RW | 2 bytes | Unit:0.01
11114 | Slave10 Inlet Phase3 Branch1 Over PF Critical | RW | 2 bytes | Unit:0.01
11115 | Slave11 Inlet Phase3 Branch1 Over PF Critical | RW | 2 bytes | Unit:0.01
11116 | Slave12 Inlet Phase3 Branch1 Over PF Critical | RW | 2 bytes | Unit:0.01
11117 | Slave13 Inlet Phase3 Branch1 Over PF Critical | RW | 2 bytes | Unit:0.01
11118 | Slave14 Inlet Phase3 Branch1 Over PF Critical | RW | 2 bytes | Unit:0.01
11119 | Slave15 Inlet Phase3 Branch1 Over PF Critical | RW | 2 bytes | Unit:0.01
11120 | Master Inlet Phase1 Branch2 Over PF Warning | RW | 2 bytes | Unit:0.01
11121 | Slave01 Inlet Phase1 Branch2 Over PF Warning | RW | 2 bytes | Unit:0.01
11122 | Slave02 Inlet Phase1 Branch2 Over PF Warning | RW | 2 bytes | Unit:0.01
11123 | Slave03 Inlet Phase1 Branch2 Over PF Warning | RW | 2 bytes | Unit:0.01
11124 | Slave04 Inlet Phase1 Branch2 Over PF Warning | RW | 2 bytes | Unit:0.01
11125 | Slave05 Inlet Phase1 Branch2 Over PF Warning | RW | 2 bytes | Unit:0.01
11126 | Slave06 Inlet Phase1 Branch2 Over PF Warning | RW | 2 bytes | Unit:0.01
11127 | Slave07 Inlet Phase1 Branch2 Over PF Warning | RW | 2 bytes | Unit:0.01
11128 | Slave08 Inlet Phase1 Branch2 Over PF Warning | RW | 2 bytes | Unit:0.01
11129 | Slave09 Inlet Phase1 Branch2 Over PF Warning | RW | 2 bytes | Unit:0.01
11130 | Slave10 Inlet Phase1 Branch2 Over PF Warning | RW | 2 bytes | Unit:0.01
11131 | Slave11 Inlet Phase1 Branch2 Over PF Warning | RW | 2 bytes | Unit:0.01
11132 | Slave12 Inlet Phase1 Branch2 Over PF Warning | RW | 2 bytes | Unit:0.01
11133 | Slave13 Inlet Phase1 Branch2 Over PF Warning | RW | 2 bytes | Unit:0.01
11134 | Slave14 Inlet Phase1 Branch2 Over PF Warning | RW | 2 bytes | Unit:0.01
11135 | Slave15 Inlet Phase1 Branch2 Over PF Warning | RW | 2 bytes | Unit:0.01
11136 | Master Inlet Phase2 Branch2 Over PF Warning | RW | 2 bytes | Unit:0.01
11137 | Slave01 Inlet Phase2 Branch2 Over PF Warning | RW | 2 bytes | Unit:0.01
11138 | Slave02 Inlet Phase2 Branch2 Over PF Warning | RW | 2 bytes | Unit:0.01
11139 | Slave03 Inlet Phase2 Branch2 Over PF Warning | RW | 2 bytes | Unit:0.01
11140 | Slave04 Inlet Phase2 Branch2 Over PF Warning | RW | 2 bytes | Unit:0.01
11141 | Slave05 Inlet Phase2 Branch2 Over PF Warning | RW | 2 bytes | Unit:0.01
11142 | Slave06 Inlet Phase2 Branch2 Over PF Warning | RW | 2 bytes | Unit:0.01
11143 | Slave07 Inlet Phase2 Branch2 Over PF Warning | RW | 2 bytes | Unit:0.01
11144 | Slave08 Inlet Phase2 Branch2 Over PF Warning | RW | 2 bytes | Unit:0.01
11145 | Slave09 Inlet Phase2 Branch2 Over PF Warning | RW | 2 bytes | Unit:0.01
11146 | Slave10 Inlet Phase2 Branch2 Over PF Warning | RW | 2 bytes | Unit:0.01
11147 | Slave11 Inlet Phase2 Branch2 Over PF Warning | RW | 2 bytes | Unit:0.01
11148 | Slave12 Inlet Phase2 Branch2 Over PF Warning | RW | 2 bytes | Unit:0.01
11149 | Slave13 Inlet Phase2 Branch2 Over PF Warning | RW | 2 bytes | Unit:0.01
11150 | Slave14 Inlet Phase2 Branch2 Over PF Warning | RW | 2 bytes | Unit:0.01
11151 | Slave15 Inlet Phase2 Branch2 Over PF Warning | RW | 2 bytes | Unit:0.01
11152 | Master Inlet Phase3 Branch2 Over PF Warning | RW | 2 bytes | Unit:0.01
11153 | Slave01 Inlet Phase3 Branch2 Over PF Warning | RW | 2 bytes | Unit:0.01
11154 | Slave02 Inlet Phase3 Branch2 Over PF Warning | RW | 2 bytes | Unit:0.01
11155 | Slave03 Inlet Phase3 Branch2 Over PF Warning | RW | 2 bytes | Unit:0.01
11156 | Slave04 Inlet Phase3 Branch2 Over PF Warning | RW | 2 bytes | Unit:0.01
11157 | Slave05 Inlet Phase3 Branch2 Over PF Warning | RW | 2 bytes | Unit:0.01
11158 | Slave06 Inlet Phase3 Branch2 Over PF Warning | RW | 2 bytes | Unit:0.01
11159 | Slave07 Inlet Phase3 Branch2 Over PF Warning | RW | 2 bytes | Unit:0.01
11160 | Slave08 Inlet Phase3 Branch2 Over PF Warning | RW | 2 bytes | Unit:0.01
11161 | Slave09 Inlet Phase3 Branch2 Over PF Warning | RW | 2 bytes | Unit:0.01
11162 | Slave10 Inlet Phase3 Branch2 Over PF Warning | RW | 2 bytes | Unit:0.01
11163 | Slave11 Inlet Phase3 Branch2 Over PF Warning | RW | 2 bytes | Unit:0.01
11164 | Slave12 Inlet Phase3 Branch2 Over PF Warning | RW | 2 bytes | Unit:0.01
11165 | Slave13 Inlet Phase3 Branch2 Over PF Warning | RW | 2 bytes | Unit:0.01
11166 | Slave14 Inlet Phase3 Branch2 Over PF Warning | RW | 2 bytes | Unit:0.01
11167 | Slave15 Inlet Phase3 Branch2 Over PF Warning | RW | 2 bytes | Unit:0.01
11168 | Master Inlet Phase1 Branch2 Over PF Critical | RW | 2 bytes | Unit:0.01
11169 | Slave01 Inlet Phase1 Branch2 Over PF Critical | RW | 2 bytes | Unit:0.01
11170 | Slave02 Inlet Phase1 Branch2 Over PF Critical | RW | 2 bytes | Unit:0.01
11171 | Slave03 Inlet Phase1 Branch2 Over PF Critical | RW | 2 bytes | Unit:0.01
11172 | Slave04 Inlet Phase1 Branch2 Over PF Critical | RW | 2 bytes | Unit:0.01
11173 | Slave05 Inlet Phase1 Branch2 Over PF Critical | RW | 2 bytes | Unit:0.01
11174 | Slave06 Inlet Phase1 Branch2 Over PF Critical | RW | 2 bytes | Unit:0.01
11175 | Slave07 Inlet Phase1 Branch2 Over PF Critical | RW | 2 bytes | Unit:0.01
11176 | Slave08 Inlet Phase1 Branch2 Over PF Critical | RW | 2 bytes | Unit:0.01
11177 | Slave09 Inlet Phase1 Branch2 Over PF Critical | RW | 2 bytes | Unit:0.01
11178 | Slave10 Inlet Phase1 Branch2 Over PF Critical | RW | 2 bytes | Unit:0.01
11179 | Slave11 Inlet Phase1 Branch2 Over PF Critical | RW | 2 bytes | Unit:0.01
11180 | Slave12 Inlet Phase1 Branch2 Over PF Critical | RW | 2 bytes | Unit:0.01
11181 | Slave13 Inlet Phase1 Branch2 Over PF Critical | RW | 2 bytes | Unit:0.01
11182 | Slave14 Inlet Phase1 Branch2 Over PF Critical | RW | 2 bytes | Unit:0.01
11183 | Slave15 Inlet Phase1 Branch2 Over PF Critical | RW | 2 bytes | Unit:0.01
11184 | Master Inlet Phase2 Branch2 Over PF Critical | RW | 2 bytes | Unit:0.01
11185 | Slave01 Inlet Phase2 Branch2 Over PF Critical | RW | 2 bytes | Unit:0.01
11186 | Slave02 Inlet Phase2 Branch2 Over PF Critical | RW | 2 bytes | Unit:0.01
11187 | Slave03 Inlet Phase2 Branch2 Over PF Critical | RW | 2 bytes | Unit:0.01
11188 | Slave04 Inlet Phase2 Branch2 Over PF Critical | RW | 2 bytes | Unit:0.01
11189 | Slave05 Inlet Phase2 Branch2 Over PF Critical | RW | 2 bytes | Unit:0.01
11190 | Slave06 Inlet Phase2 Branch2 Over PF Critical | RW | 2 bytes | Unit:0.01
11191 | Slave07 Inlet Phase2 Branch2 Over PF Critical | RW | 2 bytes | Unit:0.01
11192 | Slave08 Inlet Phase2 Branch2 Over PF Critical | RW | 2 bytes | Unit:0.01
11193 | Slave09 Inlet Phase2 Branch2 Over PF Critical | RW | 2 bytes | Unit:0.01
11194 | Slave10 Inlet Phase2 Branch2 Over PF Critical | RW | 2 bytes | Unit:0.01
11195 | Slave11 Inlet Phase2 Branch2 Over PF Critical | RW | 2 bytes | Unit:0.01
11196 | Slave12 Inlet Phase2 Branch2 Over PF Critical | RW | 2 bytes | Unit:0.01
11197 | Slave13 Inlet Phase2 Branch2 Over PF Critical | RW | 2 bytes | Unit:0.01
11198 | Slave14 Inlet Phase2 Branch2 Over PF Critical | RW | 2 bytes | Unit:0.01
11199 | Slave15 Inlet Phase2 Branch2 Over PF Critical | RW | 2 bytes | Unit:0.01
11200 | Master Inlet Phase3 Branch2 Over PF Critical | RW | 2 bytes | Unit:0.01
11201 | Slave01 Inlet Phase3 Branch2 Over PF Critical | RW | 2 bytes | Unit:0.01
11202 | Slave02 Inlet Phase3 Branch2 Over PF Critical | RW | 2 bytes | Unit:0.01
11203 | Slave03 Inlet Phase3 Branch2 Over PF Critical | RW | 2 bytes | Unit:0.01
11204 | Slave04 Inlet Phase3 Branch2 Over PF Critical | RW | 2 bytes | Unit:0.01
11205 | Slave05 Inlet Phase3 Branch2 Over PF Critical | RW | 2 bytes | Unit:0.01
11206 | Slave06 Inlet Phase3 Branch2 Over PF Critical | RW | 2 bytes | Unit:0.01
11207 | Slave07 Inlet Phase3 Branch2 Over PF Critical | RW | 2 bytes | Unit:0.01
11208 | Slave08 Inlet Phase3 Branch2 Over PF Critical | RW | 2 bytes | Unit:0.01
11209 | Slave09 Inlet Phase3 Branch2 Over PF Critical | RW | 2 bytes | Unit:0.01
11210 | Slave10 Inlet Phase3 Branch2 Over PF Critical | RW | 2 bytes | Unit:0.01
11211 | Slave11 Inlet Phase3 Branch2 Over PF Critical | RW | 2 bytes | Unit:0.01
11212 | Slave12 Inlet Phase3 Branch2 Over PF Critical | RW | 2 bytes | Unit:0.01
11213 | Slave13 Inlet Phase3 Branch2 Over PF Critical | RW | 2 bytes | Unit:0.01
11214 | Slave14 Inlet Phase3 Branch2 Over PF Critical | RW | 2 bytes | Unit:0.01
11215 | Slave15 Inlet Phase3 Branch2 Over PF Critical | RW | 2 bytes | Unit:0.01
11216 | Master Inlet Sequential Startup Configuration | RW | 2 bytes | 0:All outlets which were ON before Power OFF should be switching ON with a time delay; 1:All outlets should stay OFF
11217 | Slave01 Inlet Sequential Startup Configuration | RW | 2 bytes | 0:All outlets which were ON before Power OFF should be switching ON with a time delay; 1:All outlets should stay OFF
11218 | Slave02 Inlet Sequential Startup Configuration | RW | 2 bytes | 0:All outlets which were ON before Power OFF should be switching ON with a time delay; 1:All outlets should stay OFF
11219 | Slave03 Inlet Sequential Startup Configuration | RW | 2 bytes | 0:All outlets which were ON before Power OFF should be switching ON with a time delay; 1:All outlets should stay OFF
11220 | Slave04 Inlet Sequential Startup Configuration | RW | 2 bytes | 0:All outlets which were ON before Power OFF should be switching ON with a time delay; 1:All outlets should stay OFF
11221 | Slave05 Inlet Sequential Startup Configuration | RW | 2 bytes | 0:All outlets which were ON before Power OFF should be switching ON with a time delay; 1:All outlets should stay OFF
11222 | Slave06 Inlet Sequential Startup Configuration | RW | 2 bytes | 0:All outlets which were ON before Power OFF should be switching ON with a time delay; 1:All outlets should stay OFF
11223 | Slave07 Inlet Sequential Startup Configuration | RW | 2 bytes | 0:All outlets which were ON before Power OFF should be switching ON with a time delay; 1:All outlets should stay OFF
11224 | Slave08 Inlet Sequential Startup Configuration | RW | 2 bytes | 0:All outlets which were ON before Power OFF should be switching ON with a time delay; 1:All outlets should stay OFF
11225 | Slave09 Inlet Sequential Startup Configuration | RW | 2 bytes | 0:All outlets which were ON before Power OFF should be switching ON with a time delay; 1:All outlets should stay OFF
11226 | Slave10 Inlet Sequential Startup Configuration | RW | 2 bytes | 0:All outlets which were ON before Power OFF should be switching ON with a time delay; 1:All outlets should stay OFF
11227 | Slave11 Inlet Sequential Startup Configuration | RW | 2 bytes | 0:All outlets which were ON before Power OFF should be switching ON with a time delay; 1:All outlets should stay OFF
11228 | Slave12 Inlet Sequential Startup Configuration | RW | 2 bytes | 0:All outlets which were ON before Power OFF should be switching ON with a time delay; 1:All outlets should stay OFF
11229 | Slave13 Inlet Sequential Startup Configuration | RW | 2 bytes | 0:All outlets which were ON before Power OFF should be switching ON with a time delay; 1:All outlets should stay OFF
11230 | Slave14 Inlet Sequential Startup Configuration | RW | 2 bytes | 0:All outlets which were ON before Power OFF should be switching ON with a time delay; 1:All outlets should stay OFF
11231 | Slave15 Inlet Sequential Startup Configuration | RW | 2 bytes | 0:All outlets which were ON before Power OFF should be switching ON with a time delay; 1:All outlets should stay OFF
11232 | Master Outlet Port01 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11233 | Master Outlet Port02 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11234 | Master Outlet Port03 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11235 | Master Outlet Port04 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11236 | Master Outlet Port05 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11237 | Master Outlet Port06 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11238 | Master Outlet Port07 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11239 | Master Outlet Port08 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11240 | Master Outlet Port09 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11241 | Master Outlet Port10 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11242 | Master Outlet Port11 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11243 | Master Outlet Port12 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11244 | Master Outlet Port13 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11245 | Master Outlet Port14 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11246 | Master Outlet Port15 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11247 | Master Outlet Port16 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11248 | Master Outlet Port17 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11249 | Master Outlet Port18 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11250 | Master Outlet Port19 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11251 | Master Outlet Port20 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11252 | Master Outlet Port21 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11253 | Master Outlet Port22 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11254 | Master Outlet Port23 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11255 | Master Outlet Port24 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11256 | Master Outlet Port25 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11257 | Master Outlet Port26 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11258 | Master Outlet Port27 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11259 | Master Outlet Port28 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11260 | Master Outlet Port29 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11261 | Master Outlet Port30 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11262 | Master Outlet Port31 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11263 | Master Outlet Port32 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11264 | Master Outlet Port33 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11265 | Master Outlet Port34 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11266 | Master Outlet Port35 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11267 | Master Outlet Port36 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11268 | Master Outlet Port37 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11269 | Master Outlet Port38 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11270 | Master Outlet Port39 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11271 | Master Outlet Port40 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11272 | Master Outlet Port41 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11273 | Master Outlet Port42 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11274 | Slave01 Outlet Port01 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11275 | Slave01 Outlet Port02 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11276 | Slave01 Outlet Port03 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11277 | Slave01 Outlet Port04 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11278 | Slave01 Outlet Port05 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11279 | Slave01 Outlet Port06 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11280 | Slave01 Outlet Port07 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11281 | Slave01 Outlet Port08 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11282 | Slave01 Outlet Port09 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11283 | Slave01 Outlet Port10 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11284 | Slave01 Outlet Port11 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11285 | Slave01 Outlet Port12 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11286 | Slave01 Outlet Port13 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11287 | Slave01 Outlet Port14 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11288 | Slave01 Outlet Port15 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11289 | Slave01 Outlet Port16 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11290 | Slave01 Outlet Port17 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11291 | Slave01 Outlet Port18 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11292 | Slave01 Outlet Port19 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11293 | Slave01 Outlet Port20 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11294 | Slave01 Outlet Port21 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11295 | Slave01 Outlet Port22 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11296 | Slave01 Outlet Port23 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11297 | Slave01 Outlet Port24 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11298 | Slave01 Outlet Port25 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11299 | Slave01 Outlet Port26 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11300 | Slave01 Outlet Port27 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11301 | Slave01 Outlet Port28 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11302 | Slave01 Outlet Port29 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11303 | Slave01 Outlet Port30 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11304 | Slave01 Outlet Port31 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11305 | Slave01 Outlet Port32 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11306 | Slave01 Outlet Port33 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11307 | Slave01 Outlet Port34 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11308 | Slave01 Outlet Port35 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11309 | Slave01 Outlet Port36 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11310 | Slave01 Outlet Port37 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11311 | Slave01 Outlet Port38 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11312 | Slave01 Outlet Port39 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11313 | Slave01 Outlet Port40 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11314 | Slave01 Outlet Port41 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11315 | Slave01 Outlet Port42 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11316 | Slave02 Outlet Port01 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11317 | Slave02 Outlet Port02 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11318 | Slave02 Outlet Port03 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11319 | Slave02 Outlet Port04 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11320 | Slave02 Outlet Port05 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11321 | Slave02 Outlet Port06 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11322 | Slave02 Outlet Port07 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11323 | Slave02 Outlet Port08 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11324 | Slave02 Outlet Port09 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11325 | Slave02 Outlet Port10 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11326 | Slave02 Outlet Port11 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11327 | Slave02 Outlet Port12 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11328 | Slave02 Outlet Port13 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11329 | Slave02 Outlet Port14 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11330 | Slave02 Outlet Port15 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11331 | Slave02 Outlet Port16 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11332 | Slave02 Outlet Port17 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11333 | Slave02 Outlet Port18 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11334 | Slave02 Outlet Port19 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11335 | Slave02 Outlet Port20 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11336 | Slave02 Outlet Port21 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11337 | Slave02 Outlet Port22 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11338 | Slave02 Outlet Port23 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11339 | Slave02 Outlet Port24 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11340 | Slave02 Outlet Port25 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11341 | Slave02 Outlet Port26 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11342 | Slave02 Outlet Port27 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11343 | Slave02 Outlet Port28 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11344 | Slave02 Outlet Port29 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11345 | Slave02 Outlet Port30 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11346 | Slave02 Outlet Port31 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11347 | Slave02 Outlet Port32 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11348 | Slave02 Outlet Port33 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11349 | Slave02 Outlet Port34 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11350 | Slave02 Outlet Port35 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11351 | Slave02 Outlet Port36 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11352 | Slave02 Outlet Port37 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11353 | Slave02 Outlet Port38 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11354 | Slave02 Outlet Port39 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11355 | Slave02 Outlet Port40 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11356 | Slave02 Outlet Port41 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11357 | Slave02 Outlet Port42 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11358 | Slave03 Outlet Port01 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11359 | Slave03 Outlet Port02 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11360 | Slave03 Outlet Port03 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11361 | Slave03 Outlet Port04 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11362 | Slave03 Outlet Port05 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11363 | Slave03 Outlet Port06 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11364 | Slave03 Outlet Port07 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11365 | Slave03 Outlet Port08 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11366 | Slave03 Outlet Port09 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11367 | Slave03 Outlet Port10 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11368 | Slave03 Outlet Port11 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11369 | Slave03 Outlet Port12 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11370 | Slave03 Outlet Port13 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11371 | Slave03 Outlet Port14 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11372 | Slave03 Outlet Port15 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11373 | Slave03 Outlet Port16 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11374 | Slave03 Outlet Port17 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11375 | Slave03 Outlet Port18 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11376 | Slave03 Outlet Port19 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11377 | Slave03 Outlet Port20 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11378 | Slave03 Outlet Port21 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11379 | Slave03 Outlet Port22 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11380 | Slave03 Outlet Port23 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11381 | Slave03 Outlet Port24 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11382 | Slave03 Outlet Port25 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11383 | Slave03 Outlet Port26 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11384 | Slave03 Outlet Port27 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11385 | Slave03 Outlet Port28 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11386 | Slave03 Outlet Port29 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11387 | Slave03 Outlet Port30 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11388 | Slave03 Outlet Port31 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11389 | Slave03 Outlet Port32 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11390 | Slave03 Outlet Port33 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11391 | Slave03 Outlet Port34 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11392 | Slave03 Outlet Port35 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11393 | Slave03 Outlet Port36 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11394 | Slave03 Outlet Port37 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11395 | Slave03 Outlet Port38 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11396 | Slave03 Outlet Port39 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11397 | Slave03 Outlet Port40 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11398 | Slave03 Outlet Port41 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11399 | Slave03 Outlet Port42 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11400 | Slave04 Outlet Port01 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11401 | Slave04 Outlet Port02 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11402 | Slave04 Outlet Port03 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11403 | Slave04 Outlet Port04 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11404 | Slave04 Outlet Port05 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11405 | Slave04 Outlet Port06 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11406 | Slave04 Outlet Port07 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11407 | Slave04 Outlet Port08 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11408 | Slave04 Outlet Port09 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11409 | Slave04 Outlet Port10 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11410 | Slave04 Outlet Port11 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11411 | Slave04 Outlet Port12 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11412 | Slave04 Outlet Port13 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11413 | Slave04 Outlet Port14 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11414 | Slave04 Outlet Port15 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11415 | Slave04 Outlet Port16 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11416 | Slave04 Outlet Port17 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11417 | Slave04 Outlet Port18 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11418 | Slave04 Outlet Port19 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11419 | Slave04 Outlet Port20 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11420 | Slave04 Outlet Port21 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11421 | Slave04 Outlet Port22 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11422 | Slave04 Outlet Port23 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11423 | Slave04 Outlet Port24 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11424 | Slave04 Outlet Port25 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11425 | Slave04 Outlet Port26 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11426 | Slave04 Outlet Port27 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11427 | Slave04 Outlet Port28 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11428 | Slave04 Outlet Port29 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11429 | Slave04 Outlet Port30 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11430 | Slave04 Outlet Port31 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11431 | Slave04 Outlet Port32 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11432 | Slave04 Outlet Port33 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11433 | Slave04 Outlet Port34 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11434 | Slave04 Outlet Port35 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11435 | Slave04 Outlet Port36 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11436 | Slave04 Outlet Port37 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11437 | Slave04 Outlet Port38 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11438 | Slave04 Outlet Port39 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11439 | Slave04 Outlet Port40 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11440 | Slave04 Outlet Port41 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11441 | Slave04 Outlet Port42 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11442 | Slave05 Outlet Port01 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11443 | Slave05 Outlet Port02 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11444 | Slave05 Outlet Port03 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11445 | Slave05 Outlet Port04 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11446 | Slave05 Outlet Port05 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11447 | Slave05 Outlet Port06 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11448 | Slave05 Outlet Port07 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11449 | Slave05 Outlet Port08 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11450 | Slave05 Outlet Port09 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11451 | Slave05 Outlet Port10 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11452 | Slave05 Outlet Port11 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11453 | Slave05 Outlet Port12 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11454 | Slave05 Outlet Port13 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11455 | Slave05 Outlet Port14 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11456 | Slave05 Outlet Port15 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11457 | Slave05 Outlet Port16 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11458 | Slave05 Outlet Port17 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11459 | Slave05 Outlet Port18 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11460 | Slave05 Outlet Port19 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11461 | Slave05 Outlet Port20 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11462 | Slave05 Outlet Port21 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11463 | Slave05 Outlet Port22 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11464 | Slave05 Outlet Port23 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11465 | Slave05 Outlet Port24 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11466 | Slave05 Outlet Port25 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11467 | Slave05 Outlet Port26 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11468 | Slave05 Outlet Port27 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11469 | Slave05 Outlet Port28 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11470 | Slave05 Outlet Port29 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11471 | Slave05 Outlet Port30 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11472 | Slave05 Outlet Port31 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11473 | Slave05 Outlet Port32 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11474 | Slave05 Outlet Port33 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11475 | Slave05 Outlet Port34 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11476 | Slave05 Outlet Port35 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11477 | Slave05 Outlet Port36 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11478 | Slave05 Outlet Port37 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11479 | Slave05 Outlet Port38 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11480 | Slave05 Outlet Port39 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11481 | Slave05 Outlet Port40 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11482 | Slave05 Outlet Port41 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11483 | Slave05 Outlet Port42 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11484 | Slave06 Outlet Port01 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11485 | Slave06 Outlet Port02 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11486 | Slave06 Outlet Port03 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11487 | Slave06 Outlet Port04 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11488 | Slave06 Outlet Port05 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11489 | Slave06 Outlet Port06 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11490 | Slave06 Outlet Port07 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11491 | Slave06 Outlet Port08 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11492 | Slave06 Outlet Port09 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11493 | Slave06 Outlet Port10 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11494 | Slave06 Outlet Port11 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11495 | Slave06 Outlet Port12 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11496 | Slave06 Outlet Port13 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11497 | Slave06 Outlet Port14 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11498 | Slave06 Outlet Port15 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11499 | Slave06 Outlet Port16 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11500 | Slave06 Outlet Port17 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11501 | Slave06 Outlet Port18 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11502 | Slave06 Outlet Port19 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11503 | Slave06 Outlet Port20 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11504 | Slave06 Outlet Port21 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11505 | Slave06 Outlet Port22 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11506 | Slave06 Outlet Port23 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11507 | Slave06 Outlet Port24 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11508 | Slave06 Outlet Port25 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11509 | Slave06 Outlet Port26 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11510 | Slave06 Outlet Port27 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11511 | Slave06 Outlet Port28 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11512 | Slave06 Outlet Port29 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11513 | Slave06 Outlet Port30 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11514 | Slave06 Outlet Port31 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11515 | Slave06 Outlet Port32 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11516 | Slave06 Outlet Port33 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11517 | Slave06 Outlet Port34 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11518 | Slave06 Outlet Port35 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11519 | Slave06 Outlet Port36 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11520 | Slave06 Outlet Port37 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11521 | Slave06 Outlet Port38 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11522 | Slave06 Outlet Port39 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11523 | Slave06 Outlet Port40 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11524 | Slave06 Outlet Port41 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11525 | Slave06 Outlet Port42 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11526 | Slave07 Outlet Port01 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11527 | Slave07 Outlet Port02 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11528 | Slave07 Outlet Port03 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11529 | Slave07 Outlet Port04 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11530 | Slave07 Outlet Port05 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11531 | Slave07 Outlet Port06 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11532 | Slave07 Outlet Port07 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11533 | Slave07 Outlet Port08 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11534 | Slave07 Outlet Port09 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11535 | Slave07 Outlet Port10 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11536 | Slave07 Outlet Port11 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11537 | Slave07 Outlet Port12 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11538 | Slave07 Outlet Port13 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11539 | Slave07 Outlet Port14 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11540 | Slave07 Outlet Port15 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11541 | Slave07 Outlet Port16 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11542 | Slave07 Outlet Port17 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11543 | Slave07 Outlet Port18 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11544 | Slave07 Outlet Port19 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11545 | Slave07 Outlet Port20 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11546 | Slave07 Outlet Port21 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11547 | Slave07 Outlet Port22 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11548 | Slave07 Outlet Port23 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11549 | Slave07 Outlet Port24 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11550 | Slave07 Outlet Port25 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11551 | Slave07 Outlet Port26 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11552 | Slave07 Outlet Port27 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11553 | Slave07 Outlet Port28 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11554 | Slave07 Outlet Port29 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11555 | Slave07 Outlet Port30 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11556 | Slave07 Outlet Port31 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11557 | Slave07 Outlet Port32 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11558 | Slave07 Outlet Port33 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11559 | Slave07 Outlet Port34 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11560 | Slave07 Outlet Port35 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11561 | Slave07 Outlet Port36 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11562 | Slave07 Outlet Port37 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11563 | Slave07 Outlet Port38 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11564 | Slave07 Outlet Port39 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11565 | Slave07 Outlet Port40 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11566 | Slave07 Outlet Port41 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11567 | Slave07 Outlet Port42 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11568 | Slave08 Outlet Port01 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11569 | Slave08 Outlet Port02 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11570 | Slave08 Outlet Port03 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11571 | Slave08 Outlet Port04 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11572 | Slave08 Outlet Port05 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11573 | Slave08 Outlet Port06 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11574 | Slave08 Outlet Port07 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11575 | Slave08 Outlet Port08 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11576 | Slave08 Outlet Port09 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11577 | Slave08 Outlet Port10 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11578 | Slave08 Outlet Port11 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11579 | Slave08 Outlet Port12 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11580 | Slave08 Outlet Port13 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11581 | Slave08 Outlet Port14 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11582 | Slave08 Outlet Port15 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11583 | Slave08 Outlet Port16 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11584 | Slave08 Outlet Port17 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11585 | Slave08 Outlet Port18 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11586 | Slave08 Outlet Port19 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11587 | Slave08 Outlet Port20 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11588 | Slave08 Outlet Port21 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11589 | Slave08 Outlet Port22 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11590 | Slave08 Outlet Port23 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11591 | Slave08 Outlet Port24 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11592 | Slave08 Outlet Port25 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11593 | Slave08 Outlet Port26 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11594 | Slave08 Outlet Port27 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11595 | Slave08 Outlet Port28 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11596 | Slave08 Outlet Port29 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11597 | Slave08 Outlet Port30 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11598 | Slave08 Outlet Port31 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11599 | Slave08 Outlet Port32 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11600 | Slave08 Outlet Port33 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11601 | Slave08 Outlet Port34 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11602 | Slave08 Outlet Port35 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11603 | Slave08 Outlet Port36 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11604 | Slave08 Outlet Port37 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11605 | Slave08 Outlet Port38 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11606 | Slave08 Outlet Port39 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11607 | Slave08 Outlet Port40 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11608 | Slave08 Outlet Port41 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11609 | Slave08 Outlet Port42 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11610 | Slave09 Outlet Port01 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11611 | Slave09 Outlet Port02 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11612 | Slave09 Outlet Port03 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11613 | Slave09 Outlet Port04 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11614 | Slave09 Outlet Port05 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11615 | Slave09 Outlet Port06 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11616 | Slave09 Outlet Port07 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11617 | Slave09 Outlet Port08 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11618 | Slave09 Outlet Port09 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11619 | Slave09 Outlet Port10 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11620 | Slave09 Outlet Port11 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11621 | Slave09 Outlet Port12 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11622 | Slave09 Outlet Port13 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11623 | Slave09 Outlet Port14 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11624 | Slave09 Outlet Port15 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11625 | Slave09 Outlet Port16 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11626 | Slave09 Outlet Port17 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11627 | Slave09 Outlet Port18 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11628 | Slave09 Outlet Port19 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11629 | Slave09 Outlet Port20 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11630 | Slave09 Outlet Port21 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11631 | Slave09 Outlet Port22 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11632 | Slave09 Outlet Port23 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11633 | Slave09 Outlet Port24 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11634 | Slave09 Outlet Port25 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11635 | Slave09 Outlet Port26 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11636 | Slave09 Outlet Port27 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11637 | Slave09 Outlet Port28 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11638 | Slave09 Outlet Port29 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11639 | Slave09 Outlet Port30 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11640 | Slave09 Outlet Port31 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11641 | Slave09 Outlet Port32 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11642 | Slave09 Outlet Port33 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11643 | Slave09 Outlet Port34 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11644 | Slave09 Outlet Port35 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11645 | Slave09 Outlet Port36 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11646 | Slave09 Outlet Port37 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11647 | Slave09 Outlet Port38 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11648 | Slave09 Outlet Port39 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11649 | Slave09 Outlet Port40 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11650 | Slave09 Outlet Port41 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11651 | Slave09 Outlet Port42 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11652 | Slave10 Outlet Port01 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11653 | Slave10 Outlet Port02 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11654 | Slave10 Outlet Port03 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11655 | Slave10 Outlet Port04 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11656 | Slave10 Outlet Port05 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11657 | Slave10 Outlet Port06 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11658 | Slave10 Outlet Port07 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11659 | Slave10 Outlet Port08 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11660 | Slave10 Outlet Port09 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11661 | Slave10 Outlet Port10 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11662 | Slave10 Outlet Port11 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11663 | Slave10 Outlet Port12 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11664 | Slave10 Outlet Port13 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11665 | Slave10 Outlet Port14 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11666 | Slave10 Outlet Port15 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11667 | Slave10 Outlet Port16 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11668 | Slave10 Outlet Port17 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11669 | Slave10 Outlet Port18 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11670 | Slave10 Outlet Port19 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11671 | Slave10 Outlet Port20 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11672 | Slave10 Outlet Port21 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11673 | Slave10 Outlet Port22 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11674 | Slave10 Outlet Port23 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11675 | Slave10 Outlet Port24 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11676 | Slave10 Outlet Port25 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11677 | Slave10 Outlet Port26 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11678 | Slave10 Outlet Port27 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11679 | Slave10 Outlet Port28 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11680 | Slave10 Outlet Port29 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11681 | Slave10 Outlet Port30 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11682 | Slave10 Outlet Port31 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11683 | Slave10 Outlet Port32 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11684 | Slave10 Outlet Port33 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11685 | Slave10 Outlet Port34 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11686 | Slave10 Outlet Port35 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11687 | Slave10 Outlet Port36 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11688 | Slave10 Outlet Port37 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11689 | Slave10 Outlet Port38 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11690 | Slave10 Outlet Port39 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11691 | Slave10 Outlet Port40 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11692 | Slave10 Outlet Port41 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11693 | Slave10 Outlet Port42 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11694 | Slave11 Outlet Port01 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11695 | Slave11 Outlet Port02 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11696 | Slave11 Outlet Port03 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11697 | Slave11 Outlet Port04 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11698 | Slave11 Outlet Port05 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11699 | Slave11 Outlet Port06 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11700 | Slave11 Outlet Port07 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11701 | Slave11 Outlet Port08 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11702 | Slave11 Outlet Port09 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11703 | Slave11 Outlet Port10 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11704 | Slave11 Outlet Port11 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11705 | Slave11 Outlet Port12 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11706 | Slave11 Outlet Port13 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11707 | Slave11 Outlet Port14 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11708 | Slave11 Outlet Port15 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11709 | Slave11 Outlet Port16 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11710 | Slave11 Outlet Port17 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11711 | Slave11 Outlet Port18 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11712 | Slave11 Outlet Port19 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11713 | Slave11 Outlet Port20 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11714 | Slave11 Outlet Port21 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11715 | Slave11 Outlet Port22 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11716 | Slave11 Outlet Port23 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11717 | Slave11 Outlet Port24 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11718 | Slave11 Outlet Port25 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11719 | Slave11 Outlet Port26 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11720 | Slave11 Outlet Port27 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11721 | Slave11 Outlet Port28 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11722 | Slave11 Outlet Port29 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11723 | Slave11 Outlet Port30 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11724 | Slave11 Outlet Port31 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11725 | Slave11 Outlet Port32 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11726 | Slave11 Outlet Port33 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11727 | Slave11 Outlet Port34 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11728 | Slave11 Outlet Port35 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11729 | Slave11 Outlet Port36 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11730 | Slave11 Outlet Port37 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11731 | Slave11 Outlet Port38 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11732 | Slave11 Outlet Port39 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11733 | Slave11 Outlet Port40 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11734 | Slave11 Outlet Port41 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11735 | Slave11 Outlet Port42 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11736 | Slave12 Outlet Port01 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11737 | Slave12 Outlet Port02 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11738 | Slave12 Outlet Port03 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11739 | Slave12 Outlet Port04 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11740 | Slave12 Outlet Port05 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11741 | Slave12 Outlet Port06 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11742 | Slave12 Outlet Port07 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11743 | Slave12 Outlet Port08 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11744 | Slave12 Outlet Port09 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11745 | Slave12 Outlet Port10 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11746 | Slave12 Outlet Port11 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11747 | Slave12 Outlet Port12 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11748 | Slave12 Outlet Port13 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11749 | Slave12 Outlet Port14 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11750 | Slave12 Outlet Port15 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11751 | Slave12 Outlet Port16 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11752 | Slave12 Outlet Port17 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11753 | Slave12 Outlet Port18 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11754 | Slave12 Outlet Port19 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11755 | Slave12 Outlet Port20 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11756 | Slave12 Outlet Port21 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11757 | Slave12 Outlet Port22 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11758 | Slave12 Outlet Port23 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11759 | Slave12 Outlet Port24 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11760 | Slave12 Outlet Port25 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11761 | Slave12 Outlet Port26 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11762 | Slave12 Outlet Port27 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11763 | Slave12 Outlet Port28 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11764 | Slave12 Outlet Port29 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11765 | Slave12 Outlet Port30 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11766 | Slave12 Outlet Port31 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11767 | Slave12 Outlet Port32 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11768 | Slave12 Outlet Port33 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11769 | Slave12 Outlet Port34 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11770 | Slave12 Outlet Port35 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11771 | Slave12 Outlet Port36 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11772 | Slave12 Outlet Port37 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11773 | Slave12 Outlet Port38 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11774 | Slave12 Outlet Port39 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11775 | Slave12 Outlet Port40 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11776 | Slave12 Outlet Port41 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11777 | Slave12 Outlet Port42 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11778 | Slave13 Outlet Port01 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11779 | Slave13 Outlet Port02 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11780 | Slave13 Outlet Port03 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11781 | Slave13 Outlet Port04 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11782 | Slave13 Outlet Port05 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11783 | Slave13 Outlet Port06 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11784 | Slave13 Outlet Port07 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11785 | Slave13 Outlet Port08 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11786 | Slave13 Outlet Port09 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11787 | Slave13 Outlet Port10 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11788 | Slave13 Outlet Port11 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11789 | Slave13 Outlet Port12 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11790 | Slave13 Outlet Port13 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11791 | Slave13 Outlet Port14 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11792 | Slave13 Outlet Port15 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11793 | Slave13 Outlet Port16 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11794 | Slave13 Outlet Port17 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11795 | Slave13 Outlet Port18 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11796 | Slave13 Outlet Port19 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11797 | Slave13 Outlet Port20 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11798 | Slave13 Outlet Port21 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11799 | Slave13 Outlet Port22 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11800 | Slave13 Outlet Port23 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11801 | Slave13 Outlet Port24 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11802 | Slave13 Outlet Port25 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11803 | Slave13 Outlet Port26 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11804 | Slave13 Outlet Port27 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11805 | Slave13 Outlet Port28 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11806 | Slave13 Outlet Port29 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11807 | Slave13 Outlet Port30 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11808 | Slave13 Outlet Port31 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11809 | Slave13 Outlet Port32 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11810 | Slave13 Outlet Port33 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11811 | Slave13 Outlet Port34 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11812 | Slave13 Outlet Port35 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11813 | Slave13 Outlet Port36 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11814 | Slave13 Outlet Port37 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11815 | Slave13 Outlet Port38 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11816 | Slave13 Outlet Port39 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11817 | Slave13 Outlet Port40 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11818 | Slave13 Outlet Port41 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11819 | Slave13 Outlet Port42 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11820 | Slave14 Outlet Port01 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11821 | Slave14 Outlet Port02 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11822 | Slave14 Outlet Port03 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11823 | Slave14 Outlet Port04 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11824 | Slave14 Outlet Port05 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11825 | Slave14 Outlet Port06 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11826 | Slave14 Outlet Port07 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11827 | Slave14 Outlet Port08 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11828 | Slave14 Outlet Port09 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11829 | Slave14 Outlet Port10 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11830 | Slave14 Outlet Port11 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11831 | Slave14 Outlet Port12 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11832 | Slave14 Outlet Port13 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11833 | Slave14 Outlet Port14 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11834 | Slave14 Outlet Port15 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11835 | Slave14 Outlet Port16 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11836 | Slave14 Outlet Port17 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11837 | Slave14 Outlet Port18 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11838 | Slave14 Outlet Port19 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11839 | Slave14 Outlet Port20 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11840 | Slave14 Outlet Port21 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11841 | Slave14 Outlet Port22 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11842 | Slave14 Outlet Port23 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11843 | Slave14 Outlet Port24 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11844 | Slave14 Outlet Port25 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11845 | Slave14 Outlet Port26 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11846 | Slave14 Outlet Port27 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11847 | Slave14 Outlet Port28 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11848 | Slave14 Outlet Port29 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11849 | Slave14 Outlet Port30 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11850 | Slave14 Outlet Port31 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11851 | Slave14 Outlet Port32 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11852 | Slave14 Outlet Port33 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11853 | Slave14 Outlet Port34 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11854 | Slave14 Outlet Port35 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11855 | Slave14 Outlet Port36 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11856 | Slave14 Outlet Port37 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11857 | Slave14 Outlet Port38 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11858 | Slave14 Outlet Port39 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11859 | Slave14 Outlet Port40 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11860 | Slave14 Outlet Port41 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11861 | Slave14 Outlet Port42 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11862 | Slave15 Outlet Port01 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11863 | Slave15 Outlet Port02 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11864 | Slave15 Outlet Port03 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11865 | Slave15 Outlet Port04 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11866 | Slave15 Outlet Port05 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11867 | Slave15 Outlet Port06 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11868 | Slave15 Outlet Port07 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11869 | Slave15 Outlet Port08 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11870 | Slave15 Outlet Port09 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11871 | Slave15 Outlet Port10 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11872 | Slave15 Outlet Port11 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11873 | Slave15 Outlet Port12 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11874 | Slave15 Outlet Port13 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11875 | Slave15 Outlet Port14 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11876 | Slave15 Outlet Port15 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11877 | Slave15 Outlet Port16 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11878 | Slave15 Outlet Port17 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11879 | Slave15 Outlet Port18 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11880 | Slave15 Outlet Port19 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11881 | Slave15 Outlet Port20 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11882 | Slave15 Outlet Port21 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11883 | Slave15 Outlet Port22 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11884 | Slave15 Outlet Port23 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11885 | Slave15 Outlet Port24 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11886 | Slave15 Outlet Port25 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11887 | Slave15 Outlet Port26 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11888 | Slave15 Outlet Port27 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11889 | Slave15 Outlet Port28 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11890 | Slave15 Outlet Port29 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11891 | Slave15 Outlet Port30 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11892 | Slave15 Outlet Port31 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11893 | Slave15 Outlet Port32 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11894 | Slave15 Outlet Port33 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11895 | Slave15 Outlet Port34 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11896 | Slave15 Outlet Port35 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11897 | Slave15 Outlet Port36 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11898 | Slave15 Outlet Port37 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11899 | Slave15 Outlet Port38 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11900 | Slave15 Outlet Port39 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11901 | Slave15 Outlet Port40 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11902 | Slave15 Outlet Port41 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11903 | Slave15 Outlet Port42 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11904 | Master Outlet Port01 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
11905 | Master Outlet Port02 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
11906 | Master Outlet Port03 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
11907 | Master Outlet Port04 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
11908 | Master Outlet Port05 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
11909 | Master Outlet Port06 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
11910 | Master Outlet Port07 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
11911 | Master Outlet Port08 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
11912 | Master Outlet Port09 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
11913 | Master Outlet Port10 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
11914 | Master Outlet Port11 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
11915 | Master Outlet Port12 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
11916 | Master Outlet Port13 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
11917 | Master Outlet Port14 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
11918 | Master Outlet Port15 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
11919 | Master Outlet Port16 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
11920 | Master Outlet Port17 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
11921 | Master Outlet Port18 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
11922 | Master Outlet Port19 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
11923 | Master Outlet Port20 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
11924 | Master Outlet Port21 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
11925 | Master Outlet Port22 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
11926 | Master Outlet Port23 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
11927 | Master Outlet Port24 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
11928 | Master Outlet Port25 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
11929 | Master Outlet Port26 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
11930 | Master Outlet Port27 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
11931 | Master Outlet Port28 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
11932 | Master Outlet Port29 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
11933 | Master Outlet Port30 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
11934 | Master Outlet Port31 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
11935 | Master Outlet Port32 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
11936 | Master Outlet Port33 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
11937 | Master Outlet Port34 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
11938 | Master Outlet Port35 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
11939 | Master Outlet Port36 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
11940 | Master Outlet Port37 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
11941 | Master Outlet Port38 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
11942 | Master Outlet Port39 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
11943 | Master Outlet Port40 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
11944 | Master Outlet Port41 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
11945 | Master Outlet Port42 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
11946 | Slave01 Outlet Port01 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
11947 | Slave01 Outlet Port02 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
11948 | Slave01 Outlet Port03 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
11949 | Slave01 Outlet Port04 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
11950 | Slave01 Outlet Port05 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
11951 | Slave01 Outlet Port06 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
11952 | Slave01 Outlet Port07 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
11953 | Slave01 Outlet Port08 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
11954 | Slave01 Outlet Port09 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
11955 | Slave01 Outlet Port10 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
11956 | Slave01 Outlet Port11 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
11957 | Slave01 Outlet Port12 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
11958 | Slave01 Outlet Port13 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
11959 | Slave01 Outlet Port14 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
11960 | Slave01 Outlet Port15 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
11961 | Slave01 Outlet Port16 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
11962 | Slave01 Outlet Port17 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
11963 | Slave01 Outlet Port18 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
11964 | Slave01 Outlet Port19 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
11965 | Slave01 Outlet Port20 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
11966 | Slave01 Outlet Port21 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
11967 | Slave01 Outlet Port22 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
11968 | Slave01 Outlet Port23 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
11969 | Slave01 Outlet Port24 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
11970 | Slave01 Outlet Port25 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
11971 | Slave01 Outlet Port26 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
11972 | Slave01 Outlet Port27 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
11973 | Slave01 Outlet Port28 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
11974 | Slave01 Outlet Port29 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
11975 | Slave01 Outlet Port30 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
11976 | Slave01 Outlet Port31 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
11977 | Slave01 Outlet Port32 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
11978 | Slave01 Outlet Port33 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
11979 | Slave01 Outlet Port34 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
11980 | Slave01 Outlet Port35 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
11981 | Slave01 Outlet Port36 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
11982 | Slave01 Outlet Port37 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
11983 | Slave01 Outlet Port38 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
11984 | Slave01 Outlet Port39 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
11985 | Slave01 Outlet Port40 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
11986 | Slave01 Outlet Port41 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
11987 | Slave01 Outlet Port42 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
11988 | Slave02 Outlet Port01 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
11989 | Slave02 Outlet Port02 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
11990 | Slave02 Outlet Port03 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
11991 | Slave02 Outlet Port04 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
11992 | Slave02 Outlet Port05 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
11993 | Slave02 Outlet Port06 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
11994 | Slave02 Outlet Port07 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
11995 | Slave02 Outlet Port08 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
11996 | Slave02 Outlet Port09 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
11997 | Slave02 Outlet Port10 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
11998 | Slave02 Outlet Port11 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
11999 | Slave02 Outlet Port12 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12000 | Slave02 Outlet Port13 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12001 | Slave02 Outlet Port14 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12002 | Slave02 Outlet Port15 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12003 | Slave02 Outlet Port16 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12004 | Slave02 Outlet Port17 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12005 | Slave02 Outlet Port18 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12006 | Slave02 Outlet Port19 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12007 | Slave02 Outlet Port20 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12008 | Slave02 Outlet Port21 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12009 | Slave02 Outlet Port22 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12010 | Slave02 Outlet Port23 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12011 | Slave02 Outlet Port24 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12012 | Slave02 Outlet Port25 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12013 | Slave02 Outlet Port26 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12014 | Slave02 Outlet Port27 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12015 | Slave02 Outlet Port28 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12016 | Slave02 Outlet Port29 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12017 | Slave02 Outlet Port30 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12018 | Slave02 Outlet Port31 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12019 | Slave02 Outlet Port32 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12020 | Slave02 Outlet Port33 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12021 | Slave02 Outlet Port34 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12022 | Slave02 Outlet Port35 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12023 | Slave02 Outlet Port36 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12024 | Slave02 Outlet Port37 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12025 | Slave02 Outlet Port38 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12026 | Slave02 Outlet Port39 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12027 | Slave02 Outlet Port40 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12028 | Slave02 Outlet Port41 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12029 | Slave02 Outlet Port42 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12030 | Slave03 Outlet Port01 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12031 | Slave03 Outlet Port02 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12032 | Slave03 Outlet Port03 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12033 | Slave03 Outlet Port04 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12034 | Slave03 Outlet Port05 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12035 | Slave03 Outlet Port06 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12036 | Slave03 Outlet Port07 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12037 | Slave03 Outlet Port08 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12038 | Slave03 Outlet Port09 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12039 | Slave03 Outlet Port10 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12040 | Slave03 Outlet Port11 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12041 | Slave03 Outlet Port12 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12042 | Slave03 Outlet Port13 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12043 | Slave03 Outlet Port14 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12044 | Slave03 Outlet Port15 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12045 | Slave03 Outlet Port16 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12046 | Slave03 Outlet Port17 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12047 | Slave03 Outlet Port18 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12048 | Slave03 Outlet Port19 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12049 | Slave03 Outlet Port20 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12050 | Slave03 Outlet Port21 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12051 | Slave03 Outlet Port22 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12052 | Slave03 Outlet Port23 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12053 | Slave03 Outlet Port24 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12054 | Slave03 Outlet Port25 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12055 | Slave03 Outlet Port26 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12056 | Slave03 Outlet Port27 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12057 | Slave03 Outlet Port28 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12058 | Slave03 Outlet Port29 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12059 | Slave03 Outlet Port30 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12060 | Slave03 Outlet Port31 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12061 | Slave03 Outlet Port32 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12062 | Slave03 Outlet Port33 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12063 | Slave03 Outlet Port34 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12064 | Slave03 Outlet Port35 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12065 | Slave03 Outlet Port36 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12066 | Slave03 Outlet Port37 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12067 | Slave03 Outlet Port38 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12068 | Slave03 Outlet Port39 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12069 | Slave03 Outlet Port40 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12070 | Slave03 Outlet Port41 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12071 | Slave03 Outlet Port42 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12072 | Slave04 Outlet Port01 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12073 | Slave04 Outlet Port02 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12074 | Slave04 Outlet Port03 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12075 | Slave04 Outlet Port04 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12076 | Slave04 Outlet Port05 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12077 | Slave04 Outlet Port06 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12078 | Slave04 Outlet Port07 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12079 | Slave04 Outlet Port08 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12080 | Slave04 Outlet Port09 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12081 | Slave04 Outlet Port10 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12082 | Slave04 Outlet Port11 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12083 | Slave04 Outlet Port12 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12084 | Slave04 Outlet Port13 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12085 | Slave04 Outlet Port14 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12086 | Slave04 Outlet Port15 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12087 | Slave04 Outlet Port16 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12088 | Slave04 Outlet Port17 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12089 | Slave04 Outlet Port18 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12090 | Slave04 Outlet Port19 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12091 | Slave04 Outlet Port20 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12092 | Slave04 Outlet Port21 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12093 | Slave04 Outlet Port22 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12094 | Slave04 Outlet Port23 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12095 | Slave04 Outlet Port24 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12096 | Slave04 Outlet Port25 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12097 | Slave04 Outlet Port26 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12098 | Slave04 Outlet Port27 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12099 | Slave04 Outlet Port28 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12100 | Slave04 Outlet Port29 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12101 | Slave04 Outlet Port30 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12102 | Slave04 Outlet Port31 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12103 | Slave04 Outlet Port32 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12104 | Slave04 Outlet Port33 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12105 | Slave04 Outlet Port34 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12106 | Slave04 Outlet Port35 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12107 | Slave04 Outlet Port36 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12108 | Slave04 Outlet Port37 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12109 | Slave04 Outlet Port38 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12110 | Slave04 Outlet Port39 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12111 | Slave04 Outlet Port40 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12112 | Slave04 Outlet Port41 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12113 | Slave04 Outlet Port42 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12114 | Slave05 Outlet Port01 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12115 | Slave05 Outlet Port02 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12116 | Slave05 Outlet Port03 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12117 | Slave05 Outlet Port04 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12118 | Slave05 Outlet Port05 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12119 | Slave05 Outlet Port06 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12120 | Slave05 Outlet Port07 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12121 | Slave05 Outlet Port08 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12122 | Slave05 Outlet Port09 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12123 | Slave05 Outlet Port10 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12124 | Slave05 Outlet Port11 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12125 | Slave05 Outlet Port12 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12126 | Slave05 Outlet Port13 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12127 | Slave05 Outlet Port14 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12128 | Slave05 Outlet Port15 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12129 | Slave05 Outlet Port16 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12130 | Slave05 Outlet Port17 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12131 | Slave05 Outlet Port18 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12132 | Slave05 Outlet Port19 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12133 | Slave05 Outlet Port20 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12134 | Slave05 Outlet Port21 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12135 | Slave05 Outlet Port22 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12136 | Slave05 Outlet Port23 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12137 | Slave05 Outlet Port24 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12138 | Slave05 Outlet Port25 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12139 | Slave05 Outlet Port26 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12140 | Slave05 Outlet Port27 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12141 | Slave05 Outlet Port28 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12142 | Slave05 Outlet Port29 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12143 | Slave05 Outlet Port30 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12144 | Slave05 Outlet Port31 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12145 | Slave05 Outlet Port32 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12146 | Slave05 Outlet Port33 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12147 | Slave05 Outlet Port34 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12148 | Slave05 Outlet Port35 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12149 | Slave05 Outlet Port36 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12150 | Slave05 Outlet Port37 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12151 | Slave05 Outlet Port38 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12152 | Slave05 Outlet Port39 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12153 | Slave05 Outlet Port40 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12154 | Slave05 Outlet Port41 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12155 | Slave05 Outlet Port42 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12156 | Slave06 Outlet Port01 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12157 | Slave06 Outlet Port02 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12158 | Slave06 Outlet Port03 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12159 | Slave06 Outlet Port04 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12160 | Slave06 Outlet Port05 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12161 | Slave06 Outlet Port06 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12162 | Slave06 Outlet Port07 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12163 | Slave06 Outlet Port08 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12164 | Slave06 Outlet Port09 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12165 | Slave06 Outlet Port10 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12166 | Slave06 Outlet Port11 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12167 | Slave06 Outlet Port12 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12168 | Slave06 Outlet Port13 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12169 | Slave06 Outlet Port14 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12170 | Slave06 Outlet Port15 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12171 | Slave06 Outlet Port16 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12172 | Slave06 Outlet Port17 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12173 | Slave06 Outlet Port18 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12174 | Slave06 Outlet Port19 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12175 | Slave06 Outlet Port20 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12176 | Slave06 Outlet Port21 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12177 | Slave06 Outlet Port22 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12178 | Slave06 Outlet Port23 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12179 | Slave06 Outlet Port24 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12180 | Slave06 Outlet Port25 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12181 | Slave06 Outlet Port26 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12182 | Slave06 Outlet Port27 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12183 | Slave06 Outlet Port28 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12184 | Slave06 Outlet Port29 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12185 | Slave06 Outlet Port30 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12186 | Slave06 Outlet Port31 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12187 | Slave06 Outlet Port32 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12188 | Slave06 Outlet Port33 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12189 | Slave06 Outlet Port34 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12190 | Slave06 Outlet Port35 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12191 | Slave06 Outlet Port36 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12192 | Slave06 Outlet Port37 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12193 | Slave06 Outlet Port38 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12194 | Slave06 Outlet Port39 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12195 | Slave06 Outlet Port40 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12196 | Slave06 Outlet Port41 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12197 | Slave06 Outlet Port42 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12198 | Slave07 Outlet Port01 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12199 | Slave07 Outlet Port02 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12200 | Slave07 Outlet Port03 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12201 | Slave07 Outlet Port04 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12202 | Slave07 Outlet Port05 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12203 | Slave07 Outlet Port06 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12204 | Slave07 Outlet Port07 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12205 | Slave07 Outlet Port08 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12206 | Slave07 Outlet Port09 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12207 | Slave07 Outlet Port10 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12208 | Slave07 Outlet Port11 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12209 | Slave07 Outlet Port12 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12210 | Slave07 Outlet Port13 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12211 | Slave07 Outlet Port14 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12212 | Slave07 Outlet Port15 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12213 | Slave07 Outlet Port16 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12214 | Slave07 Outlet Port17 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12215 | Slave07 Outlet Port18 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12216 | Slave07 Outlet Port19 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12217 | Slave07 Outlet Port20 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12218 | Slave07 Outlet Port21 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12219 | Slave07 Outlet Port22 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12220 | Slave07 Outlet Port23 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12221 | Slave07 Outlet Port24 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12222 | Slave07 Outlet Port25 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12223 | Slave07 Outlet Port26 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12224 | Slave07 Outlet Port27 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12225 | Slave07 Outlet Port28 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12226 | Slave07 Outlet Port29 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12227 | Slave07 Outlet Port30 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12228 | Slave07 Outlet Port31 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12229 | Slave07 Outlet Port32 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12230 | Slave07 Outlet Port33 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12231 | Slave07 Outlet Port34 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12232 | Slave07 Outlet Port35 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12233 | Slave07 Outlet Port36 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12234 | Slave07 Outlet Port37 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12235 | Slave07 Outlet Port38 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12236 | Slave07 Outlet Port39 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12237 | Slave07 Outlet Port40 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12238 | Slave07 Outlet Port41 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12239 | Slave07 Outlet Port42 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12240 | Slave08 Outlet Port01 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12241 | Slave08 Outlet Port02 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12242 | Slave08 Outlet Port03 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12243 | Slave08 Outlet Port04 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12244 | Slave08 Outlet Port05 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12245 | Slave08 Outlet Port06 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12246 | Slave08 Outlet Port07 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12247 | Slave08 Outlet Port08 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12248 | Slave08 Outlet Port09 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12249 | Slave08 Outlet Port10 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12250 | Slave08 Outlet Port11 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12251 | Slave08 Outlet Port12 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12252 | Slave08 Outlet Port13 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12253 | Slave08 Outlet Port14 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12254 | Slave08 Outlet Port15 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12255 | Slave08 Outlet Port16 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12256 | Slave08 Outlet Port17 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12257 | Slave08 Outlet Port18 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12258 | Slave08 Outlet Port19 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12259 | Slave08 Outlet Port20 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12260 | Slave08 Outlet Port21 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12261 | Slave08 Outlet Port22 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12262 | Slave08 Outlet Port23 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12263 | Slave08 Outlet Port24 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12264 | Slave08 Outlet Port25 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12265 | Slave08 Outlet Port26 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12266 | Slave08 Outlet Port27 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12267 | Slave08 Outlet Port28 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12268 | Slave08 Outlet Port29 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12269 | Slave08 Outlet Port30 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12270 | Slave08 Outlet Port31 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12271 | Slave08 Outlet Port32 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12272 | Slave08 Outlet Port33 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12273 | Slave08 Outlet Port34 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12274 | Slave08 Outlet Port35 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12275 | Slave08 Outlet Port36 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12276 | Slave08 Outlet Port37 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12277 | Slave08 Outlet Port38 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12278 | Slave08 Outlet Port39 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12279 | Slave08 Outlet Port40 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12280 | Slave08 Outlet Port41 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12281 | Slave08 Outlet Port42 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12282 | Slave09 Outlet Port01 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12283 | Slave09 Outlet Port02 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12284 | Slave09 Outlet Port03 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12285 | Slave09 Outlet Port04 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12286 | Slave09 Outlet Port05 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12287 | Slave09 Outlet Port06 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12288 | Slave09 Outlet Port07 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12289 | Slave09 Outlet Port08 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12290 | Slave09 Outlet Port09 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12291 | Slave09 Outlet Port10 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12292 | Slave09 Outlet Port11 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12293 | Slave09 Outlet Port12 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12294 | Slave09 Outlet Port13 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12295 | Slave09 Outlet Port14 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12296 | Slave09 Outlet Port15 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12297 | Slave09 Outlet Port16 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12298 | Slave09 Outlet Port17 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12299 | Slave09 Outlet Port18 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12300 | Slave09 Outlet Port19 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12301 | Slave09 Outlet Port20 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12302 | Slave09 Outlet Port21 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12303 | Slave09 Outlet Port22 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12304 | Slave09 Outlet Port23 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12305 | Slave09 Outlet Port24 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12306 | Slave09 Outlet Port25 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12307 | Slave09 Outlet Port26 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12308 | Slave09 Outlet Port27 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12309 | Slave09 Outlet Port28 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12310 | Slave09 Outlet Port29 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12311 | Slave09 Outlet Port30 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12312 | Slave09 Outlet Port31 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12313 | Slave09 Outlet Port32 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12314 | Slave09 Outlet Port33 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12315 | Slave09 Outlet Port34 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12316 | Slave09 Outlet Port35 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12317 | Slave09 Outlet Port36 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12318 | Slave09 Outlet Port37 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12319 | Slave09 Outlet Port38 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12320 | Slave09 Outlet Port39 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12321 | Slave09 Outlet Port40 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12322 | Slave09 Outlet Port41 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12323 | Slave09 Outlet Port42 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12324 | Slave10 Outlet Port01 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12325 | Slave10 Outlet Port02 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12326 | Slave10 Outlet Port03 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12327 | Slave10 Outlet Port04 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12328 | Slave10 Outlet Port05 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12329 | Slave10 Outlet Port06 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12330 | Slave10 Outlet Port07 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12331 | Slave10 Outlet Port08 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12332 | Slave10 Outlet Port09 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12333 | Slave10 Outlet Port10 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12334 | Slave10 Outlet Port11 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12335 | Slave10 Outlet Port12 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12336 | Slave10 Outlet Port13 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12337 | Slave10 Outlet Port14 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12338 | Slave10 Outlet Port15 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12339 | Slave10 Outlet Port16 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12340 | Slave10 Outlet Port17 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12341 | Slave10 Outlet Port18 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12342 | Slave10 Outlet Port19 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12343 | Slave10 Outlet Port20 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12344 | Slave10 Outlet Port21 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12345 | Slave10 Outlet Port22 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12346 | Slave10 Outlet Port23 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12347 | Slave10 Outlet Port24 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12348 | Slave10 Outlet Port25 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12349 | Slave10 Outlet Port26 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12350 | Slave10 Outlet Port27 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12351 | Slave10 Outlet Port28 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12352 | Slave10 Outlet Port29 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12353 | Slave10 Outlet Port30 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12354 | Slave10 Outlet Port31 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12355 | Slave10 Outlet Port32 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12356 | Slave10 Outlet Port33 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12357 | Slave10 Outlet Port34 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12358 | Slave10 Outlet Port35 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12359 | Slave10 Outlet Port36 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12360 | Slave10 Outlet Port37 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12361 | Slave10 Outlet Port38 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12362 | Slave10 Outlet Port39 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12363 | Slave10 Outlet Port40 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12364 | Slave10 Outlet Port41 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12365 | Slave10 Outlet Port42 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12366 | Slave11 Outlet Port01 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12367 | Slave11 Outlet Port02 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12368 | Slave11 Outlet Port03 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12369 | Slave11 Outlet Port04 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12370 | Slave11 Outlet Port05 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12371 | Slave11 Outlet Port06 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12372 | Slave11 Outlet Port07 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12373 | Slave11 Outlet Port08 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12374 | Slave11 Outlet Port09 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12375 | Slave11 Outlet Port10 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12376 | Slave11 Outlet Port11 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12377 | Slave11 Outlet Port12 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12378 | Slave11 Outlet Port13 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12379 | Slave11 Outlet Port14 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12380 | Slave11 Outlet Port15 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12381 | Slave11 Outlet Port16 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12382 | Slave11 Outlet Port17 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12383 | Slave11 Outlet Port18 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12384 | Slave11 Outlet Port19 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12385 | Slave11 Outlet Port20 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12386 | Slave11 Outlet Port21 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12387 | Slave11 Outlet Port22 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12388 | Slave11 Outlet Port23 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12389 | Slave11 Outlet Port24 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12390 | Slave11 Outlet Port25 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12391 | Slave11 Outlet Port26 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12392 | Slave11 Outlet Port27 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12393 | Slave11 Outlet Port28 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12394 | Slave11 Outlet Port29 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12395 | Slave11 Outlet Port30 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12396 | Slave11 Outlet Port31 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12397 | Slave11 Outlet Port32 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12398 | Slave11 Outlet Port33 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12399 | Slave11 Outlet Port34 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12400 | Slave11 Outlet Port35 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12401 | Slave11 Outlet Port36 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12402 | Slave11 Outlet Port37 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12403 | Slave11 Outlet Port38 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12404 | Slave11 Outlet Port39 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12405 | Slave11 Outlet Port40 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12406 | Slave11 Outlet Port41 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12407 | Slave11 Outlet Port42 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12408 | Slave12 Outlet Port01 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12409 | Slave12 Outlet Port02 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12410 | Slave12 Outlet Port03 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12411 | Slave12 Outlet Port04 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12412 | Slave12 Outlet Port05 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12413 | Slave12 Outlet Port06 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12414 | Slave12 Outlet Port07 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12415 | Slave12 Outlet Port08 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12416 | Slave12 Outlet Port09 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12417 | Slave12 Outlet Port10 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12418 | Slave12 Outlet Port11 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12419 | Slave12 Outlet Port12 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12420 | Slave12 Outlet Port13 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12421 | Slave12 Outlet Port14 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12422 | Slave12 Outlet Port15 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12423 | Slave12 Outlet Port16 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12424 | Slave12 Outlet Port17 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12425 | Slave12 Outlet Port18 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12426 | Slave12 Outlet Port19 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12427 | Slave12 Outlet Port20 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12428 | Slave12 Outlet Port21 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12429 | Slave12 Outlet Port22 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12430 | Slave12 Outlet Port23 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12431 | Slave12 Outlet Port24 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12432 | Slave12 Outlet Port25 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12433 | Slave12 Outlet Port26 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12434 | Slave12 Outlet Port27 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12435 | Slave12 Outlet Port28 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12436 | Slave12 Outlet Port29 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12437 | Slave12 Outlet Port30 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12438 | Slave12 Outlet Port31 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12439 | Slave12 Outlet Port32 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12440 | Slave12 Outlet Port33 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12441 | Slave12 Outlet Port34 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12442 | Slave12 Outlet Port35 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12443 | Slave12 Outlet Port36 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12444 | Slave12 Outlet Port37 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12445 | Slave12 Outlet Port38 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12446 | Slave12 Outlet Port39 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12447 | Slave12 Outlet Port40 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12448 | Slave12 Outlet Port41 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12449 | Slave12 Outlet Port42 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12450 | Slave13 Outlet Port01 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12451 | Slave13 Outlet Port02 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12452 | Slave13 Outlet Port03 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12453 | Slave13 Outlet Port04 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12454 | Slave13 Outlet Port05 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12455 | Slave13 Outlet Port06 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12456 | Slave13 Outlet Port07 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12457 | Slave13 Outlet Port08 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12458 | Slave13 Outlet Port09 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12459 | Slave13 Outlet Port10 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12460 | Slave13 Outlet Port11 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12461 | Slave13 Outlet Port12 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12462 | Slave13 Outlet Port13 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12463 | Slave13 Outlet Port14 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12464 | Slave13 Outlet Port15 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12465 | Slave13 Outlet Port16 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12466 | Slave13 Outlet Port17 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12467 | Slave13 Outlet Port18 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12468 | Slave13 Outlet Port19 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12469 | Slave13 Outlet Port20 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12470 | Slave13 Outlet Port21 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12471 | Slave13 Outlet Port22 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12472 | Slave13 Outlet Port23 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12473 | Slave13 Outlet Port24 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12474 | Slave13 Outlet Port25 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12475 | Slave13 Outlet Port26 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12476 | Slave13 Outlet Port27 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12477 | Slave13 Outlet Port28 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12478 | Slave13 Outlet Port29 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12479 | Slave13 Outlet Port30 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12480 | Slave13 Outlet Port31 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12481 | Slave13 Outlet Port32 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12482 | Slave13 Outlet Port33 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12483 | Slave13 Outlet Port34 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12484 | Slave13 Outlet Port35 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12485 | Slave13 Outlet Port36 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12486 | Slave13 Outlet Port37 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12487 | Slave13 Outlet Port38 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12488 | Slave13 Outlet Port39 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12489 | Slave13 Outlet Port40 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12490 | Slave13 Outlet Port41 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12491 | Slave13 Outlet Port42 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12492 | Slave14 Outlet Port01 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12493 | Slave14 Outlet Port02 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12494 | Slave14 Outlet Port03 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12495 | Slave14 Outlet Port04 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12496 | Slave14 Outlet Port05 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12497 | Slave14 Outlet Port06 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12498 | Slave14 Outlet Port07 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12499 | Slave14 Outlet Port08 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12500 | Slave14 Outlet Port09 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12501 | Slave14 Outlet Port10 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12502 | Slave14 Outlet Port11 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12503 | Slave14 Outlet Port12 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12504 | Slave14 Outlet Port13 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12505 | Slave14 Outlet Port14 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12506 | Slave14 Outlet Port15 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12507 | Slave14 Outlet Port16 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12508 | Slave14 Outlet Port17 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12509 | Slave14 Outlet Port18 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12510 | Slave14 Outlet Port19 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12511 | Slave14 Outlet Port20 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12512 | Slave14 Outlet Port21 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12513 | Slave14 Outlet Port22 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12514 | Slave14 Outlet Port23 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12515 | Slave14 Outlet Port24 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12516 | Slave14 Outlet Port25 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12517 | Slave14 Outlet Port26 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12518 | Slave14 Outlet Port27 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12519 | Slave14 Outlet Port28 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12520 | Slave14 Outlet Port29 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12521 | Slave14 Outlet Port30 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12522 | Slave14 Outlet Port31 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12523 | Slave14 Outlet Port32 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12524 | Slave14 Outlet Port33 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12525 | Slave14 Outlet Port34 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12526 | Slave14 Outlet Port35 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12527 | Slave14 Outlet Port36 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12528 | Slave14 Outlet Port37 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12529 | Slave14 Outlet Port38 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12530 | Slave14 Outlet Port39 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12531 | Slave14 Outlet Port40 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12532 | Slave14 Outlet Port41 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12533 | Slave14 Outlet Port42 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12534 | Slave15 Outlet Port01 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12535 | Slave15 Outlet Port02 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12536 | Slave15 Outlet Port03 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12537 | Slave15 Outlet Port04 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12538 | Slave15 Outlet Port05 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12539 | Slave15 Outlet Port06 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12540 | Slave15 Outlet Port07 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12541 | Slave15 Outlet Port08 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12542 | Slave15 Outlet Port09 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12543 | Slave15 Outlet Port10 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12544 | Slave15 Outlet Port11 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12545 | Slave15 Outlet Port12 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12546 | Slave15 Outlet Port13 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12547 | Slave15 Outlet Port14 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12548 | Slave15 Outlet Port15 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12549 | Slave15 Outlet Port16 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12550 | Slave15 Outlet Port17 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12551 | Slave15 Outlet Port18 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12552 | Slave15 Outlet Port19 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12553 | Slave15 Outlet Port20 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12554 | Slave15 Outlet Port21 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12555 | Slave15 Outlet Port22 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12556 | Slave15 Outlet Port23 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12557 | Slave15 Outlet Port24 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12558 | Slave15 Outlet Port25 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12559 | Slave15 Outlet Port26 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12560 | Slave15 Outlet Port27 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12561 | Slave15 Outlet Port28 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12562 | Slave15 Outlet Port29 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12563 | Slave15 Outlet Port30 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12564 | Slave15 Outlet Port31 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12565 | Slave15 Outlet Port32 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12566 | Slave15 Outlet Port33 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12567 | Slave15 Outlet Port34 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12568 | Slave15 Outlet Port35 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12569 | Slave15 Outlet Port36 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12570 | Slave15 Outlet Port37 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12571 | Slave15 Outlet Port38 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12572 | Slave15 Outlet Port39 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12573 | Slave15 Outlet Port40 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12574 | Slave15 Outlet Port41 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12575 | Slave15 Outlet Port42 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12576 | Master Outlet Port01 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12577 | Master Outlet Port02 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12578 | Master Outlet Port03 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12579 | Master Outlet Port04 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12580 | Master Outlet Port05 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12581 | Master Outlet Port06 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12582 | Master Outlet Port07 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12583 | Master Outlet Port08 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12584 | Master Outlet Port09 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12585 | Master Outlet Port10 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12586 | Master Outlet Port11 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12587 | Master Outlet Port12 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12588 | Master Outlet Port13 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12589 | Master Outlet Port14 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12590 | Master Outlet Port15 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12591 | Master Outlet Port16 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12592 | Master Outlet Port17 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12593 | Master Outlet Port18 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12594 | Master Outlet Port19 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12595 | Master Outlet Port20 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12596 | Master Outlet Port21 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12597 | Master Outlet Port22 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12598 | Master Outlet Port23 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12599 | Master Outlet Port24 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12600 | Master Outlet Port25 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12601 | Master Outlet Port26 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12602 | Master Outlet Port27 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12603 | Master Outlet Port28 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12604 | Master Outlet Port29 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12605 | Master Outlet Port30 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12606 | Master Outlet Port31 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12607 | Master Outlet Port32 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12608 | Master Outlet Port33 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12609 | Master Outlet Port34 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12610 | Master Outlet Port35 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12611 | Master Outlet Port36 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12612 | Master Outlet Port37 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12613 | Master Outlet Port38 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12614 | Master Outlet Port39 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12615 | Master Outlet Port40 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12616 | Master Outlet Port41 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12617 | Master Outlet Port42 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12618 | Slave01 Outlet Port01 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12619 | Slave01 Outlet Port02 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12620 | Slave01 Outlet Port03 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12621 | Slave01 Outlet Port04 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12622 | Slave01 Outlet Port05 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12623 | Slave01 Outlet Port06 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12624 | Slave01 Outlet Port07 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12625 | Slave01 Outlet Port08 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12626 | Slave01 Outlet Port09 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12627 | Slave01 Outlet Port10 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12628 | Slave01 Outlet Port11 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12629 | Slave01 Outlet Port12 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12630 | Slave01 Outlet Port13 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12631 | Slave01 Outlet Port14 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12632 | Slave01 Outlet Port15 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12633 | Slave01 Outlet Port16 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12634 | Slave01 Outlet Port17 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12635 | Slave01 Outlet Port18 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12636 | Slave01 Outlet Port19 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12637 | Slave01 Outlet Port20 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12638 | Slave01 Outlet Port21 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12639 | Slave01 Outlet Port22 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12640 | Slave01 Outlet Port23 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12641 | Slave01 Outlet Port24 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12642 | Slave01 Outlet Port25 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12643 | Slave01 Outlet Port26 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12644 | Slave01 Outlet Port27 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12645 | Slave01 Outlet Port28 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12646 | Slave01 Outlet Port29 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12647 | Slave01 Outlet Port30 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12648 | Slave01 Outlet Port31 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12649 | Slave01 Outlet Port32 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12650 | Slave01 Outlet Port33 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12651 | Slave01 Outlet Port34 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12652 | Slave01 Outlet Port35 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12653 | Slave01 Outlet Port36 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12654 | Slave01 Outlet Port37 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12655 | Slave01 Outlet Port38 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12656 | Slave01 Outlet Port39 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12657 | Slave01 Outlet Port40 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12658 | Slave01 Outlet Port41 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12659 | Slave01 Outlet Port42 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12660 | Slave02 Outlet Port01 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12661 | Slave02 Outlet Port02 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12662 | Slave02 Outlet Port03 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12663 | Slave02 Outlet Port04 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12664 | Slave02 Outlet Port05 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12665 | Slave02 Outlet Port06 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12666 | Slave02 Outlet Port07 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12667 | Slave02 Outlet Port08 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12668 | Slave02 Outlet Port09 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12669 | Slave02 Outlet Port10 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12670 | Slave02 Outlet Port11 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12671 | Slave02 Outlet Port12 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12672 | Slave02 Outlet Port13 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12673 | Slave02 Outlet Port14 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12674 | Slave02 Outlet Port15 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12675 | Slave02 Outlet Port16 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12676 | Slave02 Outlet Port17 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12677 | Slave02 Outlet Port18 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12678 | Slave02 Outlet Port19 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12679 | Slave02 Outlet Port20 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12680 | Slave02 Outlet Port21 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12681 | Slave02 Outlet Port22 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12682 | Slave02 Outlet Port23 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12683 | Slave02 Outlet Port24 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12684 | Slave02 Outlet Port25 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12685 | Slave02 Outlet Port26 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12686 | Slave02 Outlet Port27 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12687 | Slave02 Outlet Port28 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12688 | Slave02 Outlet Port29 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12689 | Slave02 Outlet Port30 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12690 | Slave02 Outlet Port31 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12691 | Slave02 Outlet Port32 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12692 | Slave02 Outlet Port33 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12693 | Slave02 Outlet Port34 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12694 | Slave02 Outlet Port35 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12695 | Slave02 Outlet Port36 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12696 | Slave02 Outlet Port37 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12697 | Slave02 Outlet Port38 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12698 | Slave02 Outlet Port39 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12699 | Slave02 Outlet Port40 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12700 | Slave02 Outlet Port41 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12701 | Slave02 Outlet Port42 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12702 | Slave03 Outlet Port01 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12703 | Slave03 Outlet Port02 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12704 | Slave03 Outlet Port03 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12705 | Slave03 Outlet Port04 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12706 | Slave03 Outlet Port05 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12707 | Slave03 Outlet Port06 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12708 | Slave03 Outlet Port07 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12709 | Slave03 Outlet Port08 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12710 | Slave03 Outlet Port09 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12711 | Slave03 Outlet Port10 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12712 | Slave03 Outlet Port11 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12713 | Slave03 Outlet Port12 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12714 | Slave03 Outlet Port13 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12715 | Slave03 Outlet Port14 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12716 | Slave03 Outlet Port15 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12717 | Slave03 Outlet Port16 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12718 | Slave03 Outlet Port17 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12719 | Slave03 Outlet Port18 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12720 | Slave03 Outlet Port19 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12721 | Slave03 Outlet Port20 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12722 | Slave03 Outlet Port21 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12723 | Slave03 Outlet Port22 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12724 | Slave03 Outlet Port23 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12725 | Slave03 Outlet Port24 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12726 | Slave03 Outlet Port25 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12727 | Slave03 Outlet Port26 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12728 | Slave03 Outlet Port27 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12729 | Slave03 Outlet Port28 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12730 | Slave03 Outlet Port29 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12731 | Slave03 Outlet Port30 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12732 | Slave03 Outlet Port31 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12733 | Slave03 Outlet Port32 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12734 | Slave03 Outlet Port33 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12735 | Slave03 Outlet Port34 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12736 | Slave03 Outlet Port35 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12737 | Slave03 Outlet Port36 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12738 | Slave03 Outlet Port37 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12739 | Slave03 Outlet Port38 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12740 | Slave03 Outlet Port39 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12741 | Slave03 Outlet Port40 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12742 | Slave03 Outlet Port41 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12743 | Slave03 Outlet Port42 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12744 | Slave04 Outlet Port01 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12745 | Slave04 Outlet Port02 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12746 | Slave04 Outlet Port03 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12747 | Slave04 Outlet Port04 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12748 | Slave04 Outlet Port05 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12749 | Slave04 Outlet Port06 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12750 | Slave04 Outlet Port07 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12751 | Slave04 Outlet Port08 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12752 | Slave04 Outlet Port09 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12753 | Slave04 Outlet Port10 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12754 | Slave04 Outlet Port11 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12755 | Slave04 Outlet Port12 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12756 | Slave04 Outlet Port13 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12757 | Slave04 Outlet Port14 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12758 | Slave04 Outlet Port15 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12759 | Slave04 Outlet Port16 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12760 | Slave04 Outlet Port17 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12761 | Slave04 Outlet Port18 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12762 | Slave04 Outlet Port19 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12763 | Slave04 Outlet Port20 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12764 | Slave04 Outlet Port21 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12765 | Slave04 Outlet Port22 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12766 | Slave04 Outlet Port23 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12767 | Slave04 Outlet Port24 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12768 | Slave04 Outlet Port25 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12769 | Slave04 Outlet Port26 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12770 | Slave04 Outlet Port27 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12771 | Slave04 Outlet Port28 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12772 | Slave04 Outlet Port29 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12773 | Slave04 Outlet Port30 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12774 | Slave04 Outlet Port31 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12775 | Slave04 Outlet Port32 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12776 | Slave04 Outlet Port33 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12777 | Slave04 Outlet Port34 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12778 | Slave04 Outlet Port35 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12779 | Slave04 Outlet Port36 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12780 | Slave04 Outlet Port37 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12781 | Slave04 Outlet Port38 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12782 | Slave04 Outlet Port39 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12783 | Slave04 Outlet Port40 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12784 | Slave04 Outlet Port41 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12785 | Slave04 Outlet Port42 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12786 | Slave05 Outlet Port01 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12787 | Slave05 Outlet Port02 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12788 | Slave05 Outlet Port03 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12789 | Slave05 Outlet Port04 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12790 | Slave05 Outlet Port05 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12791 | Slave05 Outlet Port06 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12792 | Slave05 Outlet Port07 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12793 | Slave05 Outlet Port08 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12794 | Slave05 Outlet Port09 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12795 | Slave05 Outlet Port10 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12796 | Slave05 Outlet Port11 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12797 | Slave05 Outlet Port12 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12798 | Slave05 Outlet Port13 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12799 | Slave05 Outlet Port14 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12800 | Slave05 Outlet Port15 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12801 | Slave05 Outlet Port16 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12802 | Slave05 Outlet Port17 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12803 | Slave05 Outlet Port18 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12804 | Slave05 Outlet Port19 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12805 | Slave05 Outlet Port20 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12806 | Slave05 Outlet Port21 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12807 | Slave05 Outlet Port22 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12808 | Slave05 Outlet Port23 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12809 | Slave05 Outlet Port24 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12810 | Slave05 Outlet Port25 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12811 | Slave05 Outlet Port26 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12812 | Slave05 Outlet Port27 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12813 | Slave05 Outlet Port28 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12814 | Slave05 Outlet Port29 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12815 | Slave05 Outlet Port30 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12816 | Slave05 Outlet Port31 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12817 | Slave05 Outlet Port32 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12818 | Slave05 Outlet Port33 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12819 | Slave05 Outlet Port34 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12820 | Slave05 Outlet Port35 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12821 | Slave05 Outlet Port36 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12822 | Slave05 Outlet Port37 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12823 | Slave05 Outlet Port38 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12824 | Slave05 Outlet Port39 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12825 | Slave05 Outlet Port40 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12826 | Slave05 Outlet Port41 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12827 | Slave05 Outlet Port42 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12828 | Slave06 Outlet Port01 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12829 | Slave06 Outlet Port02 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12830 | Slave06 Outlet Port03 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12831 | Slave06 Outlet Port04 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12832 | Slave06 Outlet Port05 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12833 | Slave06 Outlet Port06 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12834 | Slave06 Outlet Port07 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12835 | Slave06 Outlet Port08 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12836 | Slave06 Outlet Port09 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12837 | Slave06 Outlet Port10 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12838 | Slave06 Outlet Port11 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12839 | Slave06 Outlet Port12 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12840 | Slave06 Outlet Port13 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12841 | Slave06 Outlet Port14 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12842 | Slave06 Outlet Port15 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12843 | Slave06 Outlet Port16 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12844 | Slave06 Outlet Port17 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12845 | Slave06 Outlet Port18 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12846 | Slave06 Outlet Port19 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12847 | Slave06 Outlet Port20 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12848 | Slave06 Outlet Port21 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12849 | Slave06 Outlet Port22 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12850 | Slave06 Outlet Port23 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12851 | Slave06 Outlet Port24 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12852 | Slave06 Outlet Port25 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12853 | Slave06 Outlet Port26 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12854 | Slave06 Outlet Port27 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12855 | Slave06 Outlet Port28 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12856 | Slave06 Outlet Port29 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12857 | Slave06 Outlet Port30 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12858 | Slave06 Outlet Port31 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12859 | Slave06 Outlet Port32 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12860 | Slave06 Outlet Port33 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12861 | Slave06 Outlet Port34 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12862 | Slave06 Outlet Port35 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12863 | Slave06 Outlet Port36 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12864 | Slave06 Outlet Port37 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12865 | Slave06 Outlet Port38 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12866 | Slave06 Outlet Port39 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12867 | Slave06 Outlet Port40 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12868 | Slave06 Outlet Port41 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12869 | Slave06 Outlet Port42 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12870 | Slave07 Outlet Port01 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12871 | Slave07 Outlet Port02 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12872 | Slave07 Outlet Port03 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12873 | Slave07 Outlet Port04 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12874 | Slave07 Outlet Port05 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12875 | Slave07 Outlet Port06 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12876 | Slave07 Outlet Port07 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12877 | Slave07 Outlet Port08 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12878 | Slave07 Outlet Port09 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12879 | Slave07 Outlet Port10 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12880 | Slave07 Outlet Port11 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12881 | Slave07 Outlet Port12 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12882 | Slave07 Outlet Port13 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12883 | Slave07 Outlet Port14 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12884 | Slave07 Outlet Port15 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12885 | Slave07 Outlet Port16 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12886 | Slave07 Outlet Port17 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12887 | Slave07 Outlet Port18 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12888 | Slave07 Outlet Port19 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12889 | Slave07 Outlet Port20 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12890 | Slave07 Outlet Port21 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12891 | Slave07 Outlet Port22 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12892 | Slave07 Outlet Port23 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12893 | Slave07 Outlet Port24 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12894 | Slave07 Outlet Port25 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12895 | Slave07 Outlet Port26 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12896 | Slave07 Outlet Port27 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12897 | Slave07 Outlet Port28 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12898 | Slave07 Outlet Port29 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12899 | Slave07 Outlet Port30 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12900 | Slave07 Outlet Port31 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12901 | Slave07 Outlet Port32 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12902 | Slave07 Outlet Port33 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12903 | Slave07 Outlet Port34 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12904 | Slave07 Outlet Port35 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12905 | Slave07 Outlet Port36 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12906 | Slave07 Outlet Port37 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12907 | Slave07 Outlet Port38 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12908 | Slave07 Outlet Port39 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12909 | Slave07 Outlet Port40 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12910 | Slave07 Outlet Port41 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12911 | Slave07 Outlet Port42 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12912 | Slave08 Outlet Port01 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12913 | Slave08 Outlet Port02 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12914 | Slave08 Outlet Port03 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12915 | Slave08 Outlet Port04 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12916 | Slave08 Outlet Port05 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12917 | Slave08 Outlet Port06 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12918 | Slave08 Outlet Port07 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12919 | Slave08 Outlet Port08 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12920 | Slave08 Outlet Port09 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12921 | Slave08 Outlet Port10 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12922 | Slave08 Outlet Port11 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12923 | Slave08 Outlet Port12 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12924 | Slave08 Outlet Port13 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12925 | Slave08 Outlet Port14 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12926 | Slave08 Outlet Port15 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12927 | Slave08 Outlet Port16 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12928 | Slave08 Outlet Port17 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12929 | Slave08 Outlet Port18 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12930 | Slave08 Outlet Port19 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12931 | Slave08 Outlet Port20 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12932 | Slave08 Outlet Port21 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12933 | Slave08 Outlet Port22 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12934 | Slave08 Outlet Port23 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12935 | Slave08 Outlet Port24 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12936 | Slave08 Outlet Port25 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12937 | Slave08 Outlet Port26 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12938 | Slave08 Outlet Port27 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12939 | Slave08 Outlet Port28 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12940 | Slave08 Outlet Port29 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12941 | Slave08 Outlet Port30 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12942 | Slave08 Outlet Port31 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12943 | Slave08 Outlet Port32 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12944 | Slave08 Outlet Port33 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12945 | Slave08 Outlet Port34 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12946 | Slave08 Outlet Port35 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12947 | Slave08 Outlet Port36 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12948 | Slave08 Outlet Port37 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12949 | Slave08 Outlet Port38 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12950 | Slave08 Outlet Port39 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12951 | Slave08 Outlet Port40 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12952 | Slave08 Outlet Port41 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12953 | Slave08 Outlet Port42 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12954 | Slave09 Outlet Port01 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12955 | Slave09 Outlet Port02 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12956 | Slave09 Outlet Port03 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12957 | Slave09 Outlet Port04 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12958 | Slave09 Outlet Port05 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12959 | Slave09 Outlet Port06 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12960 | Slave09 Outlet Port07 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12961 | Slave09 Outlet Port08 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12962 | Slave09 Outlet Port09 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12963 | Slave09 Outlet Port10 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12964 | Slave09 Outlet Port11 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12965 | Slave09 Outlet Port12 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12966 | Slave09 Outlet Port13 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12967 | Slave09 Outlet Port14 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12968 | Slave09 Outlet Port15 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12969 | Slave09 Outlet Port16 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12970 | Slave09 Outlet Port17 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12971 | Slave09 Outlet Port18 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12972 | Slave09 Outlet Port19 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12973 | Slave09 Outlet Port20 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12974 | Slave09 Outlet Port21 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12975 | Slave09 Outlet Port22 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12976 | Slave09 Outlet Port23 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12977 | Slave09 Outlet Port24 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12978 | Slave09 Outlet Port25 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12979 | Slave09 Outlet Port26 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12980 | Slave09 Outlet Port27 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12981 | Slave09 Outlet Port28 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12982 | Slave09 Outlet Port29 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12983 | Slave09 Outlet Port30 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12984 | Slave09 Outlet Port31 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12985 | Slave09 Outlet Port32 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12986 | Slave09 Outlet Port33 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12987 | Slave09 Outlet Port34 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12988 | Slave09 Outlet Port35 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12989 | Slave09 Outlet Port36 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12990 | Slave09 Outlet Port37 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12991 | Slave09 Outlet Port38 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12992 | Slave09 Outlet Port39 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12993 | Slave09 Outlet Port40 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12994 | Slave09 Outlet Port41 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12995 | Slave09 Outlet Port42 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12996 | Slave10 Outlet Port01 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12997 | Slave10 Outlet Port02 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12998 | Slave10 Outlet Port03 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
12999 | Slave10 Outlet Port04 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13000 | Slave10 Outlet Port05 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13001 | Slave10 Outlet Port06 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13002 | Slave10 Outlet Port07 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13003 | Slave10 Outlet Port08 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13004 | Slave10 Outlet Port09 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13005 | Slave10 Outlet Port10 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13006 | Slave10 Outlet Port11 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13007 | Slave10 Outlet Port12 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13008 | Slave10 Outlet Port13 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13009 | Slave10 Outlet Port14 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13010 | Slave10 Outlet Port15 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13011 | Slave10 Outlet Port16 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13012 | Slave10 Outlet Port17 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13013 | Slave10 Outlet Port18 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13014 | Slave10 Outlet Port19 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13015 | Slave10 Outlet Port20 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13016 | Slave10 Outlet Port21 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13017 | Slave10 Outlet Port22 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13018 | Slave10 Outlet Port23 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13019 | Slave10 Outlet Port24 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13020 | Slave10 Outlet Port25 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13021 | Slave10 Outlet Port26 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13022 | Slave10 Outlet Port27 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13023 | Slave10 Outlet Port28 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13024 | Slave10 Outlet Port29 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13025 | Slave10 Outlet Port30 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13026 | Slave10 Outlet Port31 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13027 | Slave10 Outlet Port32 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13028 | Slave10 Outlet Port33 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13029 | Slave10 Outlet Port34 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13030 | Slave10 Outlet Port35 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13031 | Slave10 Outlet Port36 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13032 | Slave10 Outlet Port37 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13033 | Slave10 Outlet Port38 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13034 | Slave10 Outlet Port39 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13035 | Slave10 Outlet Port40 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13036 | Slave10 Outlet Port41 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13037 | Slave10 Outlet Port42 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13038 | Slave11 Outlet Port01 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13039 | Slave11 Outlet Port02 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13040 | Slave11 Outlet Port03 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13041 | Slave11 Outlet Port04 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13042 | Slave11 Outlet Port05 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13043 | Slave11 Outlet Port06 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13044 | Slave11 Outlet Port07 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13045 | Slave11 Outlet Port08 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13046 | Slave11 Outlet Port09 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13047 | Slave11 Outlet Port10 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13048 | Slave11 Outlet Port11 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13049 | Slave11 Outlet Port12 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13050 | Slave11 Outlet Port13 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13051 | Slave11 Outlet Port14 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13052 | Slave11 Outlet Port15 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13053 | Slave11 Outlet Port16 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13054 | Slave11 Outlet Port17 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13055 | Slave11 Outlet Port18 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13056 | Slave11 Outlet Port19 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13057 | Slave11 Outlet Port20 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13058 | Slave11 Outlet Port21 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13059 | Slave11 Outlet Port22 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13060 | Slave11 Outlet Port23 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13061 | Slave11 Outlet Port24 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13062 | Slave11 Outlet Port25 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13063 | Slave11 Outlet Port26 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13064 | Slave11 Outlet Port27 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13065 | Slave11 Outlet Port28 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13066 | Slave11 Outlet Port29 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13067 | Slave11 Outlet Port30 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13068 | Slave11 Outlet Port31 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13069 | Slave11 Outlet Port32 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13070 | Slave11 Outlet Port33 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13071 | Slave11 Outlet Port34 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13072 | Slave11 Outlet Port35 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13073 | Slave11 Outlet Port36 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13074 | Slave11 Outlet Port37 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13075 | Slave11 Outlet Port38 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13076 | Slave11 Outlet Port39 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13077 | Slave11 Outlet Port40 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13078 | Slave11 Outlet Port41 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13079 | Slave11 Outlet Port42 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13080 | Slave12 Outlet Port01 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13081 | Slave12 Outlet Port02 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13082 | Slave12 Outlet Port03 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13083 | Slave12 Outlet Port04 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13084 | Slave12 Outlet Port05 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13085 | Slave12 Outlet Port06 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13086 | Slave12 Outlet Port07 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13087 | Slave12 Outlet Port08 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13088 | Slave12 Outlet Port09 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13089 | Slave12 Outlet Port10 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13090 | Slave12 Outlet Port11 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13091 | Slave12 Outlet Port12 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13092 | Slave12 Outlet Port13 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13093 | Slave12 Outlet Port14 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13094 | Slave12 Outlet Port15 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13095 | Slave12 Outlet Port16 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13096 | Slave12 Outlet Port17 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13097 | Slave12 Outlet Port18 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13098 | Slave12 Outlet Port19 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13099 | Slave12 Outlet Port20 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13100 | Slave12 Outlet Port21 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13101 | Slave12 Outlet Port22 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13102 | Slave12 Outlet Port23 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13103 | Slave12 Outlet Port24 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13104 | Slave12 Outlet Port25 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13105 | Slave12 Outlet Port26 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13106 | Slave12 Outlet Port27 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13107 | Slave12 Outlet Port28 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13108 | Slave12 Outlet Port29 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13109 | Slave12 Outlet Port30 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13110 | Slave12 Outlet Port31 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13111 | Slave12 Outlet Port32 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13112 | Slave12 Outlet Port33 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13113 | Slave12 Outlet Port34 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13114 | Slave12 Outlet Port35 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13115 | Slave12 Outlet Port36 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13116 | Slave12 Outlet Port37 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13117 | Slave12 Outlet Port38 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13118 | Slave12 Outlet Port39 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13119 | Slave12 Outlet Port40 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13120 | Slave12 Outlet Port41 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13121 | Slave12 Outlet Port42 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13122 | Slave13 Outlet Port01 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13123 | Slave13 Outlet Port02 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13124 | Slave13 Outlet Port03 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13125 | Slave13 Outlet Port04 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13126 | Slave13 Outlet Port05 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13127 | Slave13 Outlet Port06 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13128 | Slave13 Outlet Port07 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13129 | Slave13 Outlet Port08 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13130 | Slave13 Outlet Port09 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13131 | Slave13 Outlet Port10 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13132 | Slave13 Outlet Port11 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13133 | Slave13 Outlet Port12 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13134 | Slave13 Outlet Port13 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13135 | Slave13 Outlet Port14 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13136 | Slave13 Outlet Port15 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13137 | Slave13 Outlet Port16 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13138 | Slave13 Outlet Port17 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13139 | Slave13 Outlet Port18 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13140 | Slave13 Outlet Port19 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13141 | Slave13 Outlet Port20 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13142 | Slave13 Outlet Port21 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13143 | Slave13 Outlet Port22 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13144 | Slave13 Outlet Port23 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13145 | Slave13 Outlet Port24 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13146 | Slave13 Outlet Port25 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13147 | Slave13 Outlet Port26 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13148 | Slave13 Outlet Port27 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13149 | Slave13 Outlet Port28 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13150 | Slave13 Outlet Port29 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13151 | Slave13 Outlet Port30 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13152 | Slave13 Outlet Port31 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13153 | Slave13 Outlet Port32 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13154 | Slave13 Outlet Port33 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13155 | Slave13 Outlet Port34 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13156 | Slave13 Outlet Port35 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13157 | Slave13 Outlet Port36 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13158 | Slave13 Outlet Port37 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13159 | Slave13 Outlet Port38 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13160 | Slave13 Outlet Port39 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13161 | Slave13 Outlet Port40 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13162 | Slave13 Outlet Port41 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13163 | Slave13 Outlet Port42 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13164 | Slave14 Outlet Port01 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13165 | Slave14 Outlet Port02 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13166 | Slave14 Outlet Port03 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13167 | Slave14 Outlet Port04 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13168 | Slave14 Outlet Port05 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13169 | Slave14 Outlet Port06 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13170 | Slave14 Outlet Port07 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13171 | Slave14 Outlet Port08 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13172 | Slave14 Outlet Port09 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13173 | Slave14 Outlet Port10 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13174 | Slave14 Outlet Port11 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13175 | Slave14 Outlet Port12 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13176 | Slave14 Outlet Port13 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13177 | Slave14 Outlet Port14 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13178 | Slave14 Outlet Port15 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13179 | Slave14 Outlet Port16 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13180 | Slave14 Outlet Port17 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13181 | Slave14 Outlet Port18 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13182 | Slave14 Outlet Port19 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13183 | Slave14 Outlet Port20 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13184 | Slave14 Outlet Port21 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13185 | Slave14 Outlet Port22 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13186 | Slave14 Outlet Port23 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13187 | Slave14 Outlet Port24 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13188 | Slave14 Outlet Port25 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13189 | Slave14 Outlet Port26 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13190 | Slave14 Outlet Port27 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13191 | Slave14 Outlet Port28 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13192 | Slave14 Outlet Port29 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13193 | Slave14 Outlet Port30 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13194 | Slave14 Outlet Port31 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13195 | Slave14 Outlet Port32 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13196 | Slave14 Outlet Port33 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13197 | Slave14 Outlet Port34 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13198 | Slave14 Outlet Port35 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13199 | Slave14 Outlet Port36 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13200 | Slave14 Outlet Port37 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13201 | Slave14 Outlet Port38 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13202 | Slave14 Outlet Port39 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13203 | Slave14 Outlet Port40 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13204 | Slave14 Outlet Port41 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13205 | Slave14 Outlet Port42 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13206 | Slave15 Outlet Port01 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13207 | Slave15 Outlet Port02 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13208 | Slave15 Outlet Port03 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13209 | Slave15 Outlet Port04 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13210 | Slave15 Outlet Port05 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13211 | Slave15 Outlet Port06 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13212 | Slave15 Outlet Port07 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13213 | Slave15 Outlet Port08 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13214 | Slave15 Outlet Port09 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13215 | Slave15 Outlet Port10 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13216 | Slave15 Outlet Port11 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13217 | Slave15 Outlet Port12 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13218 | Slave15 Outlet Port13 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13219 | Slave15 Outlet Port14 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13220 | Slave15 Outlet Port15 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13221 | Slave15 Outlet Port16 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13222 | Slave15 Outlet Port17 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13223 | Slave15 Outlet Port18 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13224 | Slave15 Outlet Port19 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13225 | Slave15 Outlet Port20 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13226 | Slave15 Outlet Port21 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13227 | Slave15 Outlet Port22 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13228 | Slave15 Outlet Port23 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13229 | Slave15 Outlet Port24 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13230 | Slave15 Outlet Port25 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13231 | Slave15 Outlet Port26 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13232 | Slave15 Outlet Port27 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13233 | Slave15 Outlet Port28 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13234 | Slave15 Outlet Port29 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13235 | Slave15 Outlet Port30 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13236 | Slave15 Outlet Port31 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13237 | Slave15 Outlet Port32 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13238 | Slave15 Outlet Port33 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13239 | Slave15 Outlet Port34 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13240 | Slave15 Outlet Port35 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13241 | Slave15 Outlet Port36 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13242 | Slave15 Outlet Port37 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13243 | Slave15 Outlet Port38 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13244 | Slave15 Outlet Port39 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13245 | Slave15 Outlet Port40 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13246 | Slave15 Outlet Port41 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13247 | Slave15 Outlet Port42 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13248 | Master Outlet Port01 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13249 | Master Outlet Port02 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13250 | Master Outlet Port03 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13251 | Master Outlet Port04 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13252 | Master Outlet Port05 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13253 | Master Outlet Port06 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13254 | Master Outlet Port07 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13255 | Master Outlet Port08 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13256 | Master Outlet Port09 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13257 | Master Outlet Port10 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13258 | Master Outlet Port11 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13259 | Master Outlet Port12 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13260 | Master Outlet Port13 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13261 | Master Outlet Port14 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13262 | Master Outlet Port15 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13263 | Master Outlet Port16 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13264 | Master Outlet Port17 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13265 | Master Outlet Port18 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13266 | Master Outlet Port19 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13267 | Master Outlet Port20 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13268 | Master Outlet Port21 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13269 | Master Outlet Port22 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13270 | Master Outlet Port23 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13271 | Master Outlet Port24 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13272 | Master Outlet Port25 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13273 | Master Outlet Port26 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13274 | Master Outlet Port27 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13275 | Master Outlet Port28 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13276 | Master Outlet Port29 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13277 | Master Outlet Port30 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13278 | Master Outlet Port31 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13279 | Master Outlet Port32 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13280 | Master Outlet Port33 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13281 | Master Outlet Port34 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13282 | Master Outlet Port35 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13283 | Master Outlet Port36 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13284 | Master Outlet Port37 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13285 | Master Outlet Port38 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13286 | Master Outlet Port39 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13287 | Master Outlet Port40 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13288 | Master Outlet Port41 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13289 | Master Outlet Port42 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13290 | Slave01 Outlet Port01 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13291 | Slave01 Outlet Port02 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13292 | Slave01 Outlet Port03 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13293 | Slave01 Outlet Port04 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13294 | Slave01 Outlet Port05 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13295 | Slave01 Outlet Port06 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13296 | Slave01 Outlet Port07 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13297 | Slave01 Outlet Port08 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13298 | Slave01 Outlet Port09 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13299 | Slave01 Outlet Port10 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13300 | Slave01 Outlet Port11 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13301 | Slave01 Outlet Port12 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13302 | Slave01 Outlet Port13 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13303 | Slave01 Outlet Port14 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13304 | Slave01 Outlet Port15 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13305 | Slave01 Outlet Port16 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13306 | Slave01 Outlet Port17 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13307 | Slave01 Outlet Port18 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13308 | Slave01 Outlet Port19 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13309 | Slave01 Outlet Port20 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13310 | Slave01 Outlet Port21 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13311 | Slave01 Outlet Port22 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13312 | Slave01 Outlet Port23 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13313 | Slave01 Outlet Port24 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13314 | Slave01 Outlet Port25 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13315 | Slave01 Outlet Port26 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13316 | Slave01 Outlet Port27 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13317 | Slave01 Outlet Port28 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13318 | Slave01 Outlet Port29 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13319 | Slave01 Outlet Port30 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13320 | Slave01 Outlet Port31 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13321 | Slave01 Outlet Port32 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13322 | Slave01 Outlet Port33 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13323 | Slave01 Outlet Port34 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13324 | Slave01 Outlet Port35 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13325 | Slave01 Outlet Port36 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13326 | Slave01 Outlet Port37 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13327 | Slave01 Outlet Port38 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13328 | Slave01 Outlet Port39 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13329 | Slave01 Outlet Port40 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13330 | Slave01 Outlet Port41 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13331 | Slave01 Outlet Port42 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13332 | Slave02 Outlet Port01 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13333 | Slave02 Outlet Port02 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13334 | Slave02 Outlet Port03 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13335 | Slave02 Outlet Port04 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13336 | Slave02 Outlet Port05 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13337 | Slave02 Outlet Port06 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13338 | Slave02 Outlet Port07 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13339 | Slave02 Outlet Port08 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13340 | Slave02 Outlet Port09 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13341 | Slave02 Outlet Port10 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13342 | Slave02 Outlet Port11 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13343 | Slave02 Outlet Port12 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13344 | Slave02 Outlet Port13 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13345 | Slave02 Outlet Port14 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13346 | Slave02 Outlet Port15 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13347 | Slave02 Outlet Port16 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13348 | Slave02 Outlet Port17 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13349 | Slave02 Outlet Port18 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13350 | Slave02 Outlet Port19 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13351 | Slave02 Outlet Port20 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13352 | Slave02 Outlet Port21 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13353 | Slave02 Outlet Port22 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13354 | Slave02 Outlet Port23 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13355 | Slave02 Outlet Port24 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13356 | Slave02 Outlet Port25 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13357 | Slave02 Outlet Port26 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13358 | Slave02 Outlet Port27 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13359 | Slave02 Outlet Port28 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13360 | Slave02 Outlet Port29 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13361 | Slave02 Outlet Port30 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13362 | Slave02 Outlet Port31 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13363 | Slave02 Outlet Port32 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13364 | Slave02 Outlet Port33 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13365 | Slave02 Outlet Port34 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13366 | Slave02 Outlet Port35 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13367 | Slave02 Outlet Port36 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13368 | Slave02 Outlet Port37 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13369 | Slave02 Outlet Port38 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13370 | Slave02 Outlet Port39 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13371 | Slave02 Outlet Port40 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13372 | Slave02 Outlet Port41 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13373 | Slave02 Outlet Port42 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13374 | Slave03 Outlet Port01 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13375 | Slave03 Outlet Port02 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13376 | Slave03 Outlet Port03 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13377 | Slave03 Outlet Port04 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13378 | Slave03 Outlet Port05 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13379 | Slave03 Outlet Port06 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13380 | Slave03 Outlet Port07 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13381 | Slave03 Outlet Port08 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13382 | Slave03 Outlet Port09 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13383 | Slave03 Outlet Port10 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13384 | Slave03 Outlet Port11 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13385 | Slave03 Outlet Port12 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13386 | Slave03 Outlet Port13 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13387 | Slave03 Outlet Port14 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13388 | Slave03 Outlet Port15 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13389 | Slave03 Outlet Port16 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13390 | Slave03 Outlet Port17 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13391 | Slave03 Outlet Port18 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13392 | Slave03 Outlet Port19 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13393 | Slave03 Outlet Port20 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13394 | Slave03 Outlet Port21 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13395 | Slave03 Outlet Port22 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13396 | Slave03 Outlet Port23 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13397 | Slave03 Outlet Port24 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13398 | Slave03 Outlet Port25 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13399 | Slave03 Outlet Port26 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13400 | Slave03 Outlet Port27 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13401 | Slave03 Outlet Port28 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13402 | Slave03 Outlet Port29 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13403 | Slave03 Outlet Port30 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13404 | Slave03 Outlet Port31 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13405 | Slave03 Outlet Port32 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13406 | Slave03 Outlet Port33 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13407 | Slave03 Outlet Port34 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13408 | Slave03 Outlet Port35 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13409 | Slave03 Outlet Port36 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13410 | Slave03 Outlet Port37 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13411 | Slave03 Outlet Port38 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13412 | Slave03 Outlet Port39 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13413 | Slave03 Outlet Port40 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13414 | Slave03 Outlet Port41 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13415 | Slave03 Outlet Port42 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13416 | Slave04 Outlet Port01 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13417 | Slave04 Outlet Port02 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13418 | Slave04 Outlet Port03 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13419 | Slave04 Outlet Port04 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13420 | Slave04 Outlet Port05 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13421 | Slave04 Outlet Port06 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13422 | Slave04 Outlet Port07 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13423 | Slave04 Outlet Port08 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13424 | Slave04 Outlet Port09 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13425 | Slave04 Outlet Port10 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13426 | Slave04 Outlet Port11 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13427 | Slave04 Outlet Port12 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13428 | Slave04 Outlet Port13 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13429 | Slave04 Outlet Port14 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13430 | Slave04 Outlet Port15 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13431 | Slave04 Outlet Port16 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13432 | Slave04 Outlet Port17 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13433 | Slave04 Outlet Port18 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13434 | Slave04 Outlet Port19 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13435 | Slave04 Outlet Port20 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13436 | Slave04 Outlet Port21 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13437 | Slave04 Outlet Port22 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13438 | Slave04 Outlet Port23 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13439 | Slave04 Outlet Port24 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13440 | Slave04 Outlet Port25 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13441 | Slave04 Outlet Port26 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13442 | Slave04 Outlet Port27 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13443 | Slave04 Outlet Port28 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13444 | Slave04 Outlet Port29 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13445 | Slave04 Outlet Port30 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13446 | Slave04 Outlet Port31 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13447 | Slave04 Outlet Port32 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13448 | Slave04 Outlet Port33 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13449 | Slave04 Outlet Port34 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13450 | Slave04 Outlet Port35 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13451 | Slave04 Outlet Port36 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13452 | Slave04 Outlet Port37 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13453 | Slave04 Outlet Port38 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13454 | Slave04 Outlet Port39 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13455 | Slave04 Outlet Port40 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13456 | Slave04 Outlet Port41 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13457 | Slave04 Outlet Port42 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13458 | Slave05 Outlet Port01 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13459 | Slave05 Outlet Port02 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13460 | Slave05 Outlet Port03 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13461 | Slave05 Outlet Port04 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13462 | Slave05 Outlet Port05 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13463 | Slave05 Outlet Port06 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13464 | Slave05 Outlet Port07 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13465 | Slave05 Outlet Port08 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13466 | Slave05 Outlet Port09 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13467 | Slave05 Outlet Port10 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13468 | Slave05 Outlet Port11 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13469 | Slave05 Outlet Port12 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13470 | Slave05 Outlet Port13 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13471 | Slave05 Outlet Port14 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13472 | Slave05 Outlet Port15 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13473 | Slave05 Outlet Port16 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13474 | Slave05 Outlet Port17 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13475 | Slave05 Outlet Port18 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13476 | Slave05 Outlet Port19 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13477 | Slave05 Outlet Port20 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13478 | Slave05 Outlet Port21 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13479 | Slave05 Outlet Port22 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13480 | Slave05 Outlet Port23 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13481 | Slave05 Outlet Port24 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13482 | Slave05 Outlet Port25 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13483 | Slave05 Outlet Port26 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13484 | Slave05 Outlet Port27 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13485 | Slave05 Outlet Port28 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13486 | Slave05 Outlet Port29 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13487 | Slave05 Outlet Port30 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13488 | Slave05 Outlet Port31 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13489 | Slave05 Outlet Port32 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13490 | Slave05 Outlet Port33 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13491 | Slave05 Outlet Port34 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13492 | Slave05 Outlet Port35 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13493 | Slave05 Outlet Port36 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13494 | Slave05 Outlet Port37 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13495 | Slave05 Outlet Port38 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13496 | Slave05 Outlet Port39 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13497 | Slave05 Outlet Port40 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13498 | Slave05 Outlet Port41 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13499 | Slave05 Outlet Port42 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13500 | Slave06 Outlet Port01 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13501 | Slave06 Outlet Port02 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13502 | Slave06 Outlet Port03 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13503 | Slave06 Outlet Port04 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13504 | Slave06 Outlet Port05 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13505 | Slave06 Outlet Port06 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13506 | Slave06 Outlet Port07 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13507 | Slave06 Outlet Port08 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13508 | Slave06 Outlet Port09 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13509 | Slave06 Outlet Port10 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13510 | Slave06 Outlet Port11 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13511 | Slave06 Outlet Port12 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13512 | Slave06 Outlet Port13 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13513 | Slave06 Outlet Port14 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13514 | Slave06 Outlet Port15 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13515 | Slave06 Outlet Port16 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13516 | Slave06 Outlet Port17 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13517 | Slave06 Outlet Port18 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13518 | Slave06 Outlet Port19 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13519 | Slave06 Outlet Port20 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13520 | Slave06 Outlet Port21 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13521 | Slave06 Outlet Port22 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13522 | Slave06 Outlet Port23 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13523 | Slave06 Outlet Port24 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13524 | Slave06 Outlet Port25 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13525 | Slave06 Outlet Port26 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13526 | Slave06 Outlet Port27 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13527 | Slave06 Outlet Port28 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13528 | Slave06 Outlet Port29 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13529 | Slave06 Outlet Port30 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13530 | Slave06 Outlet Port31 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13531 | Slave06 Outlet Port32 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13532 | Slave06 Outlet Port33 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13533 | Slave06 Outlet Port34 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13534 | Slave06 Outlet Port35 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13535 | Slave06 Outlet Port36 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13536 | Slave06 Outlet Port37 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13537 | Slave06 Outlet Port38 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13538 | Slave06 Outlet Port39 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13539 | Slave06 Outlet Port40 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13540 | Slave06 Outlet Port41 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13541 | Slave06 Outlet Port42 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13542 | Slave07 Outlet Port01 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13543 | Slave07 Outlet Port02 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13544 | Slave07 Outlet Port03 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13545 | Slave07 Outlet Port04 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13546 | Slave07 Outlet Port05 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13547 | Slave07 Outlet Port06 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13548 | Slave07 Outlet Port07 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13549 | Slave07 Outlet Port08 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13550 | Slave07 Outlet Port09 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13551 | Slave07 Outlet Port10 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13552 | Slave07 Outlet Port11 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13553 | Slave07 Outlet Port12 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13554 | Slave07 Outlet Port13 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13555 | Slave07 Outlet Port14 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13556 | Slave07 Outlet Port15 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13557 | Slave07 Outlet Port16 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13558 | Slave07 Outlet Port17 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13559 | Slave07 Outlet Port18 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13560 | Slave07 Outlet Port19 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13561 | Slave07 Outlet Port20 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13562 | Slave07 Outlet Port21 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13563 | Slave07 Outlet Port22 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13564 | Slave07 Outlet Port23 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13565 | Slave07 Outlet Port24 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13566 | Slave07 Outlet Port25 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13567 | Slave07 Outlet Port26 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13568 | Slave07 Outlet Port27 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13569 | Slave07 Outlet Port28 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13570 | Slave07 Outlet Port29 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13571 | Slave07 Outlet Port30 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13572 | Slave07 Outlet Port31 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13573 | Slave07 Outlet Port32 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13574 | Slave07 Outlet Port33 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13575 | Slave07 Outlet Port34 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13576 | Slave07 Outlet Port35 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13577 | Slave07 Outlet Port36 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13578 | Slave07 Outlet Port37 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13579 | Slave07 Outlet Port38 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13580 | Slave07 Outlet Port39 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13581 | Slave07 Outlet Port40 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13582 | Slave07 Outlet Port41 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13583 | Slave07 Outlet Port42 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13584 | Slave08 Outlet Port01 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13585 | Slave08 Outlet Port02 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13586 | Slave08 Outlet Port03 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13587 | Slave08 Outlet Port04 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13588 | Slave08 Outlet Port05 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13589 | Slave08 Outlet Port06 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13590 | Slave08 Outlet Port07 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13591 | Slave08 Outlet Port08 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13592 | Slave08 Outlet Port09 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13593 | Slave08 Outlet Port10 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13594 | Slave08 Outlet Port11 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13595 | Slave08 Outlet Port12 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13596 | Slave08 Outlet Port13 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13597 | Slave08 Outlet Port14 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13598 | Slave08 Outlet Port15 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13599 | Slave08 Outlet Port16 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13600 | Slave08 Outlet Port17 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13601 | Slave08 Outlet Port18 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13602 | Slave08 Outlet Port19 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13603 | Slave08 Outlet Port20 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13604 | Slave08 Outlet Port21 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13605 | Slave08 Outlet Port22 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13606 | Slave08 Outlet Port23 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13607 | Slave08 Outlet Port24 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13608 | Slave08 Outlet Port25 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13609 | Slave08 Outlet Port26 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13610 | Slave08 Outlet Port27 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13611 | Slave08 Outlet Port28 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13612 | Slave08 Outlet Port29 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13613 | Slave08 Outlet Port30 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13614 | Slave08 Outlet Port31 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13615 | Slave08 Outlet Port32 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13616 | Slave08 Outlet Port33 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13617 | Slave08 Outlet Port34 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13618 | Slave08 Outlet Port35 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13619 | Slave08 Outlet Port36 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13620 | Slave08 Outlet Port37 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13621 | Slave08 Outlet Port38 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13622 | Slave08 Outlet Port39 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13623 | Slave08 Outlet Port40 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13624 | Slave08 Outlet Port41 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13625 | Slave08 Outlet Port42 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13626 | Slave09 Outlet Port01 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13627 | Slave09 Outlet Port02 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13628 | Slave09 Outlet Port03 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13629 | Slave09 Outlet Port04 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13630 | Slave09 Outlet Port05 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13631 | Slave09 Outlet Port06 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13632 | Slave09 Outlet Port07 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13633 | Slave09 Outlet Port08 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13634 | Slave09 Outlet Port09 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13635 | Slave09 Outlet Port10 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13636 | Slave09 Outlet Port11 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13637 | Slave09 Outlet Port12 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13638 | Slave09 Outlet Port13 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13639 | Slave09 Outlet Port14 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13640 | Slave09 Outlet Port15 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13641 | Slave09 Outlet Port16 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13642 | Slave09 Outlet Port17 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13643 | Slave09 Outlet Port18 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13644 | Slave09 Outlet Port19 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13645 | Slave09 Outlet Port20 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13646 | Slave09 Outlet Port21 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13647 | Slave09 Outlet Port22 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13648 | Slave09 Outlet Port23 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13649 | Slave09 Outlet Port24 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13650 | Slave09 Outlet Port25 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13651 | Slave09 Outlet Port26 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13652 | Slave09 Outlet Port27 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13653 | Slave09 Outlet Port28 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13654 | Slave09 Outlet Port29 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13655 | Slave09 Outlet Port30 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13656 | Slave09 Outlet Port31 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13657 | Slave09 Outlet Port32 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13658 | Slave09 Outlet Port33 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13659 | Slave09 Outlet Port34 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13660 | Slave09 Outlet Port35 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13661 | Slave09 Outlet Port36 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13662 | Slave09 Outlet Port37 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13663 | Slave09 Outlet Port38 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13664 | Slave09 Outlet Port39 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13665 | Slave09 Outlet Port40 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13666 | Slave09 Outlet Port41 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13667 | Slave09 Outlet Port42 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13668 | Slave10 Outlet Port01 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13669 | Slave10 Outlet Port02 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13670 | Slave10 Outlet Port03 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13671 | Slave10 Outlet Port04 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13672 | Slave10 Outlet Port05 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13673 | Slave10 Outlet Port06 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13674 | Slave10 Outlet Port07 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13675 | Slave10 Outlet Port08 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13676 | Slave10 Outlet Port09 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13677 | Slave10 Outlet Port10 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13678 | Slave10 Outlet Port11 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13679 | Slave10 Outlet Port12 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13680 | Slave10 Outlet Port13 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13681 | Slave10 Outlet Port14 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13682 | Slave10 Outlet Port15 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13683 | Slave10 Outlet Port16 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13684 | Slave10 Outlet Port17 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13685 | Slave10 Outlet Port18 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13686 | Slave10 Outlet Port19 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13687 | Slave10 Outlet Port20 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13688 | Slave10 Outlet Port21 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13689 | Slave10 Outlet Port22 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13690 | Slave10 Outlet Port23 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13691 | Slave10 Outlet Port24 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13692 | Slave10 Outlet Port25 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13693 | Slave10 Outlet Port26 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13694 | Slave10 Outlet Port27 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13695 | Slave10 Outlet Port28 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13696 | Slave10 Outlet Port29 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13697 | Slave10 Outlet Port30 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13698 | Slave10 Outlet Port31 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13699 | Slave10 Outlet Port32 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13700 | Slave10 Outlet Port33 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13701 | Slave10 Outlet Port34 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13702 | Slave10 Outlet Port35 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13703 | Slave10 Outlet Port36 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13704 | Slave10 Outlet Port37 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13705 | Slave10 Outlet Port38 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13706 | Slave10 Outlet Port39 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13707 | Slave10 Outlet Port40 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13708 | Slave10 Outlet Port41 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13709 | Slave10 Outlet Port42 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13710 | Slave11 Outlet Port01 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13711 | Slave11 Outlet Port02 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13712 | Slave11 Outlet Port03 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13713 | Slave11 Outlet Port04 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13714 | Slave11 Outlet Port05 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13715 | Slave11 Outlet Port06 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13716 | Slave11 Outlet Port07 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13717 | Slave11 Outlet Port08 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13718 | Slave11 Outlet Port09 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13719 | Slave11 Outlet Port10 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13720 | Slave11 Outlet Port11 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13721 | Slave11 Outlet Port12 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13722 | Slave11 Outlet Port13 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13723 | Slave11 Outlet Port14 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13724 | Slave11 Outlet Port15 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13725 | Slave11 Outlet Port16 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13726 | Slave11 Outlet Port17 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13727 | Slave11 Outlet Port18 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13728 | Slave11 Outlet Port19 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13729 | Slave11 Outlet Port20 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13730 | Slave11 Outlet Port21 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13731 | Slave11 Outlet Port22 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13732 | Slave11 Outlet Port23 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13733 | Slave11 Outlet Port24 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13734 | Slave11 Outlet Port25 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13735 | Slave11 Outlet Port26 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13736 | Slave11 Outlet Port27 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13737 | Slave11 Outlet Port28 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13738 | Slave11 Outlet Port29 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13739 | Slave11 Outlet Port30 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13740 | Slave11 Outlet Port31 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13741 | Slave11 Outlet Port32 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13742 | Slave11 Outlet Port33 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13743 | Slave11 Outlet Port34 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13744 | Slave11 Outlet Port35 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13745 | Slave11 Outlet Port36 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13746 | Slave11 Outlet Port37 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13747 | Slave11 Outlet Port38 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13748 | Slave11 Outlet Port39 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13749 | Slave11 Outlet Port40 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13750 | Slave11 Outlet Port41 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13751 | Slave11 Outlet Port42 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13752 | Slave12 Outlet Port01 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13753 | Slave12 Outlet Port02 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13754 | Slave12 Outlet Port03 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13755 | Slave12 Outlet Port04 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13756 | Slave12 Outlet Port05 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13757 | Slave12 Outlet Port06 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13758 | Slave12 Outlet Port07 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13759 | Slave12 Outlet Port08 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13760 | Slave12 Outlet Port09 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13761 | Slave12 Outlet Port10 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13762 | Slave12 Outlet Port11 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13763 | Slave12 Outlet Port12 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13764 | Slave12 Outlet Port13 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13765 | Slave12 Outlet Port14 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13766 | Slave12 Outlet Port15 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13767 | Slave12 Outlet Port16 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13768 | Slave12 Outlet Port17 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13769 | Slave12 Outlet Port18 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13770 | Slave12 Outlet Port19 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13771 | Slave12 Outlet Port20 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13772 | Slave12 Outlet Port21 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13773 | Slave12 Outlet Port22 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13774 | Slave12 Outlet Port23 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13775 | Slave12 Outlet Port24 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13776 | Slave12 Outlet Port25 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13777 | Slave12 Outlet Port26 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13778 | Slave12 Outlet Port27 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13779 | Slave12 Outlet Port28 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13780 | Slave12 Outlet Port29 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13781 | Slave12 Outlet Port30 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13782 | Slave12 Outlet Port31 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13783 | Slave12 Outlet Port32 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13784 | Slave12 Outlet Port33 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13785 | Slave12 Outlet Port34 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13786 | Slave12 Outlet Port35 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13787 | Slave12 Outlet Port36 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13788 | Slave12 Outlet Port37 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13789 | Slave12 Outlet Port38 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13790 | Slave12 Outlet Port39 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13791 | Slave12 Outlet Port40 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13792 | Slave12 Outlet Port41 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13793 | Slave12 Outlet Port42 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13794 | Slave13 Outlet Port01 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13795 | Slave13 Outlet Port02 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13796 | Slave13 Outlet Port03 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13797 | Slave13 Outlet Port04 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13798 | Slave13 Outlet Port05 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13799 | Slave13 Outlet Port06 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13800 | Slave13 Outlet Port07 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13801 | Slave13 Outlet Port08 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13802 | Slave13 Outlet Port09 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13803 | Slave13 Outlet Port10 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13804 | Slave13 Outlet Port11 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13805 | Slave13 Outlet Port12 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13806 | Slave13 Outlet Port13 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13807 | Slave13 Outlet Port14 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13808 | Slave13 Outlet Port15 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13809 | Slave13 Outlet Port16 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13810 | Slave13 Outlet Port17 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13811 | Slave13 Outlet Port18 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13812 | Slave13 Outlet Port19 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13813 | Slave13 Outlet Port20 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13814 | Slave13 Outlet Port21 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13815 | Slave13 Outlet Port22 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13816 | Slave13 Outlet Port23 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13817 | Slave13 Outlet Port24 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13818 | Slave13 Outlet Port25 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13819 | Slave13 Outlet Port26 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13820 | Slave13 Outlet Port27 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13821 | Slave13 Outlet Port28 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13822 | Slave13 Outlet Port29 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13823 | Slave13 Outlet Port30 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13824 | Slave13 Outlet Port31 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13825 | Slave13 Outlet Port32 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13826 | Slave13 Outlet Port33 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13827 | Slave13 Outlet Port34 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13828 | Slave13 Outlet Port35 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13829 | Slave13 Outlet Port36 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13830 | Slave13 Outlet Port37 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13831 | Slave13 Outlet Port38 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13832 | Slave13 Outlet Port39 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13833 | Slave13 Outlet Port40 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13834 | Slave13 Outlet Port41 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13835 | Slave13 Outlet Port42 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13836 | Slave14 Outlet Port01 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13837 | Slave14 Outlet Port02 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13838 | Slave14 Outlet Port03 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13839 | Slave14 Outlet Port04 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13840 | Slave14 Outlet Port05 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13841 | Slave14 Outlet Port06 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13842 | Slave14 Outlet Port07 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13843 | Slave14 Outlet Port08 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13844 | Slave14 Outlet Port09 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13845 | Slave14 Outlet Port10 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13846 | Slave14 Outlet Port11 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13847 | Slave14 Outlet Port12 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13848 | Slave14 Outlet Port13 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13849 | Slave14 Outlet Port14 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13850 | Slave14 Outlet Port15 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13851 | Slave14 Outlet Port16 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13852 | Slave14 Outlet Port17 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13853 | Slave14 Outlet Port18 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13854 | Slave14 Outlet Port19 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13855 | Slave14 Outlet Port20 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13856 | Slave14 Outlet Port21 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13857 | Slave14 Outlet Port22 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13858 | Slave14 Outlet Port23 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13859 | Slave14 Outlet Port24 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13860 | Slave14 Outlet Port25 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13861 | Slave14 Outlet Port26 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13862 | Slave14 Outlet Port27 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13863 | Slave14 Outlet Port28 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13864 | Slave14 Outlet Port29 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13865 | Slave14 Outlet Port30 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13866 | Slave14 Outlet Port31 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13867 | Slave14 Outlet Port32 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13868 | Slave14 Outlet Port33 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13869 | Slave14 Outlet Port34 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13870 | Slave14 Outlet Port35 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13871 | Slave14 Outlet Port36 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13872 | Slave14 Outlet Port37 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13873 | Slave14 Outlet Port38 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13874 | Slave14 Outlet Port39 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13875 | Slave14 Outlet Port40 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13876 | Slave14 Outlet Port41 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13877 | Slave14 Outlet Port42 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13878 | Slave15 Outlet Port01 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13879 | Slave15 Outlet Port02 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13880 | Slave15 Outlet Port03 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13881 | Slave15 Outlet Port04 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13882 | Slave15 Outlet Port05 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13883 | Slave15 Outlet Port06 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13884 | Slave15 Outlet Port07 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13885 | Slave15 Outlet Port08 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13886 | Slave15 Outlet Port09 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13887 | Slave15 Outlet Port10 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13888 | Slave15 Outlet Port11 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13889 | Slave15 Outlet Port12 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13890 | Slave15 Outlet Port13 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13891 | Slave15 Outlet Port14 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13892 | Slave15 Outlet Port15 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13893 | Slave15 Outlet Port16 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13894 | Slave15 Outlet Port17 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13895 | Slave15 Outlet Port18 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13896 | Slave15 Outlet Port19 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13897 | Slave15 Outlet Port20 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13898 | Slave15 Outlet Port21 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13899 | Slave15 Outlet Port22 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13900 | Slave15 Outlet Port23 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13901 | Slave15 Outlet Port24 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13902 | Slave15 Outlet Port25 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13903 | Slave15 Outlet Port26 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13904 | Slave15 Outlet Port27 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13905 | Slave15 Outlet Port28 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13906 | Slave15 Outlet Port29 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13907 | Slave15 Outlet Port30 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13908 | Slave15 Outlet Port31 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13909 | Slave15 Outlet Port32 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13910 | Slave15 Outlet Port33 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13911 | Slave15 Outlet Port34 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13912 | Slave15 Outlet Port35 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13913 | Slave15 Outlet Port36 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13914 | Slave15 Outlet Port37 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13915 | Slave15 Outlet Port38 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13916 | Slave15 Outlet Port39 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13917 | Slave15 Outlet Port40 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13918 | Slave15 Outlet Port41 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13919 | Slave15 Outlet Port42 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
13920 | Master Outlet Port01 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
13921 | Master Outlet Port02 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
13922 | Master Outlet Port03 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
13923 | Master Outlet Port04 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
13924 | Master Outlet Port05 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
13925 | Master Outlet Port06 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
13926 | Master Outlet Port07 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
13927 | Master Outlet Port08 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
13928 | Master Outlet Port09 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
13929 | Master Outlet Port10 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
13930 | Master Outlet Port11 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
13931 | Master Outlet Port12 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
13932 | Master Outlet Port13 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
13933 | Master Outlet Port14 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
13934 | Master Outlet Port15 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
13935 | Master Outlet Port16 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
13936 | Master Outlet Port17 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
13937 | Master Outlet Port18 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
13938 | Master Outlet Port19 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
13939 | Master Outlet Port20 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
13940 | Master Outlet Port21 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
13941 | Master Outlet Port22 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
13942 | Master Outlet Port23 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
13943 | Master Outlet Port24 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
13944 | Master Outlet Port25 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
13945 | Master Outlet Port26 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
13946 | Master Outlet Port27 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
13947 | Master Outlet Port28 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
13948 | Master Outlet Port29 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
13949 | Master Outlet Port30 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
13950 | Master Outlet Port31 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
13951 | Master Outlet Port32 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
13952 | Master Outlet Port33 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
13953 | Master Outlet Port34 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
13954 | Master Outlet Port35 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
13955 | Master Outlet Port36 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
13956 | Master Outlet Port37 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
13957 | Master Outlet Port38 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
13958 | Master Outlet Port39 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
13959 | Master Outlet Port40 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
13960 | Master Outlet Port41 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
13961 | Master Outlet Port42 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
13962 | Slave01 Outlet Port01 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
13963 | Slave01 Outlet Port02 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
13964 | Slave01 Outlet Port03 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
13965 | Slave01 Outlet Port04 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
13966 | Slave01 Outlet Port05 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
13967 | Slave01 Outlet Port06 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
13968 | Slave01 Outlet Port07 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
13969 | Slave01 Outlet Port08 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
13970 | Slave01 Outlet Port09 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
13971 | Slave01 Outlet Port10 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
13972 | Slave01 Outlet Port11 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
13973 | Slave01 Outlet Port12 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
13974 | Slave01 Outlet Port13 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
13975 | Slave01 Outlet Port14 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
13976 | Slave01 Outlet Port15 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
13977 | Slave01 Outlet Port16 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
13978 | Slave01 Outlet Port17 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
13979 | Slave01 Outlet Port18 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
13980 | Slave01 Outlet Port19 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
13981 | Slave01 Outlet Port20 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
13982 | Slave01 Outlet Port21 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
13983 | Slave01 Outlet Port22 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
13984 | Slave01 Outlet Port23 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
13985 | Slave01 Outlet Port24 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
13986 | Slave01 Outlet Port25 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
13987 | Slave01 Outlet Port26 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
13988 | Slave01 Outlet Port27 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
13989 | Slave01 Outlet Port28 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
13990 | Slave01 Outlet Port29 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
13991 | Slave01 Outlet Port30 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
13992 | Slave01 Outlet Port31 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
13993 | Slave01 Outlet Port32 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
13994 | Slave01 Outlet Port33 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
13995 | Slave01 Outlet Port34 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
13996 | Slave01 Outlet Port35 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
13997 | Slave01 Outlet Port36 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
13998 | Slave01 Outlet Port37 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
13999 | Slave01 Outlet Port38 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14000 | Slave01 Outlet Port39 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14001 | Slave01 Outlet Port40 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14002 | Slave01 Outlet Port41 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14003 | Slave01 Outlet Port42 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14004 | Slave02 Outlet Port01 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14005 | Slave02 Outlet Port02 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14006 | Slave02 Outlet Port03 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14007 | Slave02 Outlet Port04 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14008 | Slave02 Outlet Port05 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14009 | Slave02 Outlet Port06 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14010 | Slave02 Outlet Port07 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14011 | Slave02 Outlet Port08 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14012 | Slave02 Outlet Port09 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14013 | Slave02 Outlet Port10 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14014 | Slave02 Outlet Port11 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14015 | Slave02 Outlet Port12 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14016 | Slave02 Outlet Port13 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14017 | Slave02 Outlet Port14 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14018 | Slave02 Outlet Port15 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14019 | Slave02 Outlet Port16 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14020 | Slave02 Outlet Port17 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14021 | Slave02 Outlet Port18 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14022 | Slave02 Outlet Port19 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14023 | Slave02 Outlet Port20 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14024 | Slave02 Outlet Port21 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14025 | Slave02 Outlet Port22 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14026 | Slave02 Outlet Port23 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14027 | Slave02 Outlet Port24 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14028 | Slave02 Outlet Port25 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14029 | Slave02 Outlet Port26 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14030 | Slave02 Outlet Port27 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14031 | Slave02 Outlet Port28 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14032 | Slave02 Outlet Port29 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14033 | Slave02 Outlet Port30 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14034 | Slave02 Outlet Port31 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14035 | Slave02 Outlet Port32 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14036 | Slave02 Outlet Port33 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14037 | Slave02 Outlet Port34 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14038 | Slave02 Outlet Port35 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14039 | Slave02 Outlet Port36 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14040 | Slave02 Outlet Port37 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14041 | Slave02 Outlet Port38 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14042 | Slave02 Outlet Port39 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14043 | Slave02 Outlet Port40 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14044 | Slave02 Outlet Port41 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14045 | Slave02 Outlet Port42 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14046 | Slave03 Outlet Port01 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14047 | Slave03 Outlet Port02 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14048 | Slave03 Outlet Port03 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14049 | Slave03 Outlet Port04 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14050 | Slave03 Outlet Port05 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14051 | Slave03 Outlet Port06 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14052 | Slave03 Outlet Port07 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14053 | Slave03 Outlet Port08 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14054 | Slave03 Outlet Port09 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14055 | Slave03 Outlet Port10 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14056 | Slave03 Outlet Port11 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14057 | Slave03 Outlet Port12 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14058 | Slave03 Outlet Port13 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14059 | Slave03 Outlet Port14 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14060 | Slave03 Outlet Port15 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14061 | Slave03 Outlet Port16 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14062 | Slave03 Outlet Port17 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14063 | Slave03 Outlet Port18 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14064 | Slave03 Outlet Port19 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14065 | Slave03 Outlet Port20 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14066 | Slave03 Outlet Port21 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14067 | Slave03 Outlet Port22 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14068 | Slave03 Outlet Port23 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14069 | Slave03 Outlet Port24 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14070 | Slave03 Outlet Port25 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14071 | Slave03 Outlet Port26 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14072 | Slave03 Outlet Port27 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14073 | Slave03 Outlet Port28 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14074 | Slave03 Outlet Port29 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14075 | Slave03 Outlet Port30 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14076 | Slave03 Outlet Port31 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14077 | Slave03 Outlet Port32 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14078 | Slave03 Outlet Port33 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14079 | Slave03 Outlet Port34 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14080 | Slave03 Outlet Port35 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14081 | Slave03 Outlet Port36 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14082 | Slave03 Outlet Port37 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14083 | Slave03 Outlet Port38 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14084 | Slave03 Outlet Port39 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14085 | Slave03 Outlet Port40 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14086 | Slave03 Outlet Port41 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14087 | Slave03 Outlet Port42 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14088 | Slave04 Outlet Port01 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14089 | Slave04 Outlet Port02 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14090 | Slave04 Outlet Port03 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14091 | Slave04 Outlet Port04 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14092 | Slave04 Outlet Port05 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14093 | Slave04 Outlet Port06 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14094 | Slave04 Outlet Port07 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14095 | Slave04 Outlet Port08 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14096 | Slave04 Outlet Port09 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14097 | Slave04 Outlet Port10 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14098 | Slave04 Outlet Port11 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14099 | Slave04 Outlet Port12 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14100 | Slave04 Outlet Port13 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14101 | Slave04 Outlet Port14 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14102 | Slave04 Outlet Port15 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14103 | Slave04 Outlet Port16 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14104 | Slave04 Outlet Port17 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14105 | Slave04 Outlet Port18 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14106 | Slave04 Outlet Port19 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14107 | Slave04 Outlet Port20 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14108 | Slave04 Outlet Port21 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14109 | Slave04 Outlet Port22 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14110 | Slave04 Outlet Port23 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14111 | Slave04 Outlet Port24 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14112 | Slave04 Outlet Port25 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14113 | Slave04 Outlet Port26 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14114 | Slave04 Outlet Port27 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14115 | Slave04 Outlet Port28 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14116 | Slave04 Outlet Port29 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14117 | Slave04 Outlet Port30 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14118 | Slave04 Outlet Port31 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14119 | Slave04 Outlet Port32 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14120 | Slave04 Outlet Port33 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14121 | Slave04 Outlet Port34 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14122 | Slave04 Outlet Port35 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14123 | Slave04 Outlet Port36 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14124 | Slave04 Outlet Port37 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14125 | Slave04 Outlet Port38 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14126 | Slave04 Outlet Port39 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14127 | Slave04 Outlet Port40 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14128 | Slave04 Outlet Port41 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14129 | Slave04 Outlet Port42 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14130 | Slave05 Outlet Port01 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14131 | Slave05 Outlet Port02 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14132 | Slave05 Outlet Port03 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14133 | Slave05 Outlet Port04 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14134 | Slave05 Outlet Port05 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14135 | Slave05 Outlet Port06 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14136 | Slave05 Outlet Port07 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14137 | Slave05 Outlet Port08 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14138 | Slave05 Outlet Port09 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14139 | Slave05 Outlet Port10 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14140 | Slave05 Outlet Port11 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14141 | Slave05 Outlet Port12 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14142 | Slave05 Outlet Port13 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14143 | Slave05 Outlet Port14 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14144 | Slave05 Outlet Port15 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14145 | Slave05 Outlet Port16 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14146 | Slave05 Outlet Port17 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14147 | Slave05 Outlet Port18 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14148 | Slave05 Outlet Port19 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14149 | Slave05 Outlet Port20 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14150 | Slave05 Outlet Port21 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14151 | Slave05 Outlet Port22 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14152 | Slave05 Outlet Port23 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14153 | Slave05 Outlet Port24 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14154 | Slave05 Outlet Port25 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14155 | Slave05 Outlet Port26 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14156 | Slave05 Outlet Port27 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14157 | Slave05 Outlet Port28 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14158 | Slave05 Outlet Port29 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14159 | Slave05 Outlet Port30 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14160 | Slave05 Outlet Port31 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14161 | Slave05 Outlet Port32 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14162 | Slave05 Outlet Port33 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14163 | Slave05 Outlet Port34 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14164 | Slave05 Outlet Port35 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14165 | Slave05 Outlet Port36 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14166 | Slave05 Outlet Port37 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14167 | Slave05 Outlet Port38 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14168 | Slave05 Outlet Port39 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14169 | Slave05 Outlet Port40 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14170 | Slave05 Outlet Port41 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14171 | Slave05 Outlet Port42 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14172 | Slave06 Outlet Port01 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14173 | Slave06 Outlet Port02 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14174 | Slave06 Outlet Port03 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14175 | Slave06 Outlet Port04 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14176 | Slave06 Outlet Port05 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14177 | Slave06 Outlet Port06 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14178 | Slave06 Outlet Port07 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14179 | Slave06 Outlet Port08 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14180 | Slave06 Outlet Port09 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14181 | Slave06 Outlet Port10 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14182 | Slave06 Outlet Port11 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14183 | Slave06 Outlet Port12 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14184 | Slave06 Outlet Port13 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14185 | Slave06 Outlet Port14 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14186 | Slave06 Outlet Port15 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14187 | Slave06 Outlet Port16 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14188 | Slave06 Outlet Port17 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14189 | Slave06 Outlet Port18 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14190 | Slave06 Outlet Port19 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14191 | Slave06 Outlet Port20 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14192 | Slave06 Outlet Port21 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14193 | Slave06 Outlet Port22 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14194 | Slave06 Outlet Port23 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14195 | Slave06 Outlet Port24 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14196 | Slave06 Outlet Port25 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14197 | Slave06 Outlet Port26 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14198 | Slave06 Outlet Port27 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14199 | Slave06 Outlet Port28 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14200 | Slave06 Outlet Port29 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14201 | Slave06 Outlet Port30 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14202 | Slave06 Outlet Port31 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14203 | Slave06 Outlet Port32 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14204 | Slave06 Outlet Port33 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14205 | Slave06 Outlet Port34 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14206 | Slave06 Outlet Port35 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14207 | Slave06 Outlet Port36 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14208 | Slave06 Outlet Port37 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14209 | Slave06 Outlet Port38 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14210 | Slave06 Outlet Port39 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14211 | Slave06 Outlet Port40 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14212 | Slave06 Outlet Port41 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14213 | Slave06 Outlet Port42 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14214 | Slave07 Outlet Port01 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14215 | Slave07 Outlet Port02 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14216 | Slave07 Outlet Port03 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14217 | Slave07 Outlet Port04 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14218 | Slave07 Outlet Port05 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14219 | Slave07 Outlet Port06 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14220 | Slave07 Outlet Port07 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14221 | Slave07 Outlet Port08 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14222 | Slave07 Outlet Port09 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14223 | Slave07 Outlet Port10 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14224 | Slave07 Outlet Port11 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14225 | Slave07 Outlet Port12 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14226 | Slave07 Outlet Port13 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14227 | Slave07 Outlet Port14 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14228 | Slave07 Outlet Port15 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14229 | Slave07 Outlet Port16 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14230 | Slave07 Outlet Port17 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14231 | Slave07 Outlet Port18 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14232 | Slave07 Outlet Port19 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14233 | Slave07 Outlet Port20 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14234 | Slave07 Outlet Port21 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14235 | Slave07 Outlet Port22 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14236 | Slave07 Outlet Port23 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14237 | Slave07 Outlet Port24 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14238 | Slave07 Outlet Port25 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14239 | Slave07 Outlet Port26 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14240 | Slave07 Outlet Port27 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14241 | Slave07 Outlet Port28 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14242 | Slave07 Outlet Port29 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14243 | Slave07 Outlet Port30 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14244 | Slave07 Outlet Port31 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14245 | Slave07 Outlet Port32 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14246 | Slave07 Outlet Port33 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14247 | Slave07 Outlet Port34 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14248 | Slave07 Outlet Port35 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14249 | Slave07 Outlet Port36 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14250 | Slave07 Outlet Port37 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14251 | Slave07 Outlet Port38 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14252 | Slave07 Outlet Port39 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14253 | Slave07 Outlet Port40 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14254 | Slave07 Outlet Port41 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14255 | Slave07 Outlet Port42 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14256 | Slave08 Outlet Port01 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14257 | Slave08 Outlet Port02 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14258 | Slave08 Outlet Port03 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14259 | Slave08 Outlet Port04 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14260 | Slave08 Outlet Port05 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14261 | Slave08 Outlet Port06 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14262 | Slave08 Outlet Port07 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14263 | Slave08 Outlet Port08 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14264 | Slave08 Outlet Port09 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14265 | Slave08 Outlet Port10 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14266 | Slave08 Outlet Port11 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14267 | Slave08 Outlet Port12 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14268 | Slave08 Outlet Port13 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14269 | Slave08 Outlet Port14 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14270 | Slave08 Outlet Port15 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14271 | Slave08 Outlet Port16 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14272 | Slave08 Outlet Port17 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14273 | Slave08 Outlet Port18 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14274 | Slave08 Outlet Port19 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14275 | Slave08 Outlet Port20 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14276 | Slave08 Outlet Port21 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14277 | Slave08 Outlet Port22 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14278 | Slave08 Outlet Port23 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14279 | Slave08 Outlet Port24 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14280 | Slave08 Outlet Port25 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14281 | Slave08 Outlet Port26 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14282 | Slave08 Outlet Port27 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14283 | Slave08 Outlet Port28 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14284 | Slave08 Outlet Port29 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14285 | Slave08 Outlet Port30 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14286 | Slave08 Outlet Port31 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14287 | Slave08 Outlet Port32 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14288 | Slave08 Outlet Port33 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14289 | Slave08 Outlet Port34 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14290 | Slave08 Outlet Port35 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14291 | Slave08 Outlet Port36 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14292 | Slave08 Outlet Port37 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14293 | Slave08 Outlet Port38 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14294 | Slave08 Outlet Port39 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14295 | Slave08 Outlet Port40 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14296 | Slave08 Outlet Port41 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14297 | Slave08 Outlet Port42 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14298 | Slave09 Outlet Port01 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14299 | Slave09 Outlet Port02 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14300 | Slave09 Outlet Port03 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14301 | Slave09 Outlet Port04 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14302 | Slave09 Outlet Port05 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14303 | Slave09 Outlet Port06 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14304 | Slave09 Outlet Port07 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14305 | Slave09 Outlet Port08 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14306 | Slave09 Outlet Port09 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14307 | Slave09 Outlet Port10 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14308 | Slave09 Outlet Port11 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14309 | Slave09 Outlet Port12 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14310 | Slave09 Outlet Port13 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14311 | Slave09 Outlet Port14 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14312 | Slave09 Outlet Port15 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14313 | Slave09 Outlet Port16 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14314 | Slave09 Outlet Port17 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14315 | Slave09 Outlet Port18 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14316 | Slave09 Outlet Port19 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14317 | Slave09 Outlet Port20 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14318 | Slave09 Outlet Port21 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14319 | Slave09 Outlet Port22 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14320 | Slave09 Outlet Port23 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14321 | Slave09 Outlet Port24 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14322 | Slave09 Outlet Port25 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14323 | Slave09 Outlet Port26 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14324 | Slave09 Outlet Port27 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14325 | Slave09 Outlet Port28 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14326 | Slave09 Outlet Port29 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14327 | Slave09 Outlet Port30 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14328 | Slave09 Outlet Port31 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14329 | Slave09 Outlet Port32 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14330 | Slave09 Outlet Port33 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14331 | Slave09 Outlet Port34 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14332 | Slave09 Outlet Port35 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14333 | Slave09 Outlet Port36 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14334 | Slave09 Outlet Port37 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14335 | Slave09 Outlet Port38 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14336 | Slave09 Outlet Port39 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14337 | Slave09 Outlet Port40 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14338 | Slave09 Outlet Port41 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14339 | Slave09 Outlet Port42 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14340 | Slave10 Outlet Port01 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14341 | Slave10 Outlet Port02 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14342 | Slave10 Outlet Port03 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14343 | Slave10 Outlet Port04 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14344 | Slave10 Outlet Port05 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14345 | Slave10 Outlet Port06 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14346 | Slave10 Outlet Port07 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14347 | Slave10 Outlet Port08 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14348 | Slave10 Outlet Port09 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14349 | Slave10 Outlet Port10 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14350 | Slave10 Outlet Port11 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14351 | Slave10 Outlet Port12 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14352 | Slave10 Outlet Port13 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14353 | Slave10 Outlet Port14 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14354 | Slave10 Outlet Port15 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14355 | Slave10 Outlet Port16 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14356 | Slave10 Outlet Port17 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14357 | Slave10 Outlet Port18 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14358 | Slave10 Outlet Port19 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14359 | Slave10 Outlet Port20 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14360 | Slave10 Outlet Port21 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14361 | Slave10 Outlet Port22 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14362 | Slave10 Outlet Port23 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14363 | Slave10 Outlet Port24 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14364 | Slave10 Outlet Port25 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14365 | Slave10 Outlet Port26 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14366 | Slave10 Outlet Port27 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14367 | Slave10 Outlet Port28 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14368 | Slave10 Outlet Port29 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14369 | Slave10 Outlet Port30 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14370 | Slave10 Outlet Port31 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14371 | Slave10 Outlet Port32 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14372 | Slave10 Outlet Port33 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14373 | Slave10 Outlet Port34 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14374 | Slave10 Outlet Port35 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14375 | Slave10 Outlet Port36 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14376 | Slave10 Outlet Port37 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14377 | Slave10 Outlet Port38 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14378 | Slave10 Outlet Port39 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14379 | Slave10 Outlet Port40 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14380 | Slave10 Outlet Port41 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14381 | Slave10 Outlet Port42 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14382 | Slave11 Outlet Port01 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14383 | Slave11 Outlet Port02 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14384 | Slave11 Outlet Port03 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14385 | Slave11 Outlet Port04 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14386 | Slave11 Outlet Port05 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14387 | Slave11 Outlet Port06 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14388 | Slave11 Outlet Port07 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14389 | Slave11 Outlet Port08 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14390 | Slave11 Outlet Port09 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14391 | Slave11 Outlet Port10 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14392 | Slave11 Outlet Port11 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14393 | Slave11 Outlet Port12 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14394 | Slave11 Outlet Port13 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14395 | Slave11 Outlet Port14 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14396 | Slave11 Outlet Port15 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14397 | Slave11 Outlet Port16 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14398 | Slave11 Outlet Port17 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14399 | Slave11 Outlet Port18 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14400 | Slave11 Outlet Port19 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14401 | Slave11 Outlet Port20 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14402 | Slave11 Outlet Port21 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14403 | Slave11 Outlet Port22 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14404 | Slave11 Outlet Port23 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14405 | Slave11 Outlet Port24 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14406 | Slave11 Outlet Port25 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14407 | Slave11 Outlet Port26 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14408 | Slave11 Outlet Port27 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14409 | Slave11 Outlet Port28 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14410 | Slave11 Outlet Port29 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14411 | Slave11 Outlet Port30 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14412 | Slave11 Outlet Port31 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14413 | Slave11 Outlet Port32 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14414 | Slave11 Outlet Port33 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14415 | Slave11 Outlet Port34 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14416 | Slave11 Outlet Port35 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14417 | Slave11 Outlet Port36 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14418 | Slave11 Outlet Port37 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14419 | Slave11 Outlet Port38 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14420 | Slave11 Outlet Port39 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14421 | Slave11 Outlet Port40 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14422 | Slave11 Outlet Port41 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14423 | Slave11 Outlet Port42 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14424 | Slave12 Outlet Port01 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14425 | Slave12 Outlet Port02 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14426 | Slave12 Outlet Port03 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14427 | Slave12 Outlet Port04 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14428 | Slave12 Outlet Port05 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14429 | Slave12 Outlet Port06 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14430 | Slave12 Outlet Port07 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14431 | Slave12 Outlet Port08 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14432 | Slave12 Outlet Port09 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14433 | Slave12 Outlet Port10 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14434 | Slave12 Outlet Port11 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14435 | Slave12 Outlet Port12 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14436 | Slave12 Outlet Port13 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14437 | Slave12 Outlet Port14 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14438 | Slave12 Outlet Port15 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14439 | Slave12 Outlet Port16 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14440 | Slave12 Outlet Port17 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14441 | Slave12 Outlet Port18 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14442 | Slave12 Outlet Port19 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14443 | Slave12 Outlet Port20 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14444 | Slave12 Outlet Port21 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14445 | Slave12 Outlet Port22 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14446 | Slave12 Outlet Port23 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14447 | Slave12 Outlet Port24 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14448 | Slave12 Outlet Port25 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14449 | Slave12 Outlet Port26 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14450 | Slave12 Outlet Port27 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14451 | Slave12 Outlet Port28 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14452 | Slave12 Outlet Port29 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14453 | Slave12 Outlet Port30 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14454 | Slave12 Outlet Port31 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14455 | Slave12 Outlet Port32 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14456 | Slave12 Outlet Port33 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14457 | Slave12 Outlet Port34 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14458 | Slave12 Outlet Port35 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14459 | Slave12 Outlet Port36 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14460 | Slave12 Outlet Port37 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14461 | Slave12 Outlet Port38 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14462 | Slave12 Outlet Port39 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14463 | Slave12 Outlet Port40 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14464 | Slave12 Outlet Port41 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14465 | Slave12 Outlet Port42 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14466 | Slave13 Outlet Port01 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14467 | Slave13 Outlet Port02 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14468 | Slave13 Outlet Port03 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14469 | Slave13 Outlet Port04 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14470 | Slave13 Outlet Port05 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14471 | Slave13 Outlet Port06 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14472 | Slave13 Outlet Port07 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14473 | Slave13 Outlet Port08 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14474 | Slave13 Outlet Port09 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14475 | Slave13 Outlet Port10 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14476 | Slave13 Outlet Port11 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14477 | Slave13 Outlet Port12 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14478 | Slave13 Outlet Port13 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14479 | Slave13 Outlet Port14 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14480 | Slave13 Outlet Port15 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14481 | Slave13 Outlet Port16 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14482 | Slave13 Outlet Port17 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14483 | Slave13 Outlet Port18 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14484 | Slave13 Outlet Port19 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14485 | Slave13 Outlet Port20 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14486 | Slave13 Outlet Port21 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14487 | Slave13 Outlet Port22 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14488 | Slave13 Outlet Port23 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14489 | Slave13 Outlet Port24 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14490 | Slave13 Outlet Port25 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14491 | Slave13 Outlet Port26 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14492 | Slave13 Outlet Port27 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14493 | Slave13 Outlet Port28 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14494 | Slave13 Outlet Port29 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14495 | Slave13 Outlet Port30 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14496 | Slave13 Outlet Port31 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14497 | Slave13 Outlet Port32 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14498 | Slave13 Outlet Port33 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14499 | Slave13 Outlet Port34 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14500 | Slave13 Outlet Port35 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14501 | Slave13 Outlet Port36 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14502 | Slave13 Outlet Port37 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14503 | Slave13 Outlet Port38 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14504 | Slave13 Outlet Port39 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14505 | Slave13 Outlet Port40 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14506 | Slave13 Outlet Port41 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14507 | Slave13 Outlet Port42 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14508 | Slave14 Outlet Port01 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14509 | Slave14 Outlet Port02 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14510 | Slave14 Outlet Port03 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14511 | Slave14 Outlet Port04 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14512 | Slave14 Outlet Port05 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14513 | Slave14 Outlet Port06 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14514 | Slave14 Outlet Port07 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14515 | Slave14 Outlet Port08 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14516 | Slave14 Outlet Port09 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14517 | Slave14 Outlet Port10 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14518 | Slave14 Outlet Port11 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14519 | Slave14 Outlet Port12 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14520 | Slave14 Outlet Port13 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14521 | Slave14 Outlet Port14 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14522 | Slave14 Outlet Port15 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14523 | Slave14 Outlet Port16 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14524 | Slave14 Outlet Port17 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14525 | Slave14 Outlet Port18 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14526 | Slave14 Outlet Port19 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14527 | Slave14 Outlet Port20 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14528 | Slave14 Outlet Port21 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14529 | Slave14 Outlet Port22 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14530 | Slave14 Outlet Port23 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14531 | Slave14 Outlet Port24 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14532 | Slave14 Outlet Port25 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14533 | Slave14 Outlet Port26 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14534 | Slave14 Outlet Port27 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14535 | Slave14 Outlet Port28 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14536 | Slave14 Outlet Port29 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14537 | Slave14 Outlet Port30 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14538 | Slave14 Outlet Port31 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14539 | Slave14 Outlet Port32 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14540 | Slave14 Outlet Port33 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14541 | Slave14 Outlet Port34 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14542 | Slave14 Outlet Port35 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14543 | Slave14 Outlet Port36 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14544 | Slave14 Outlet Port37 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14545 | Slave14 Outlet Port38 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14546 | Slave14 Outlet Port39 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14547 | Slave14 Outlet Port40 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14548 | Slave14 Outlet Port41 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14549 | Slave14 Outlet Port42 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14550 | Slave15 Outlet Port01 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14551 | Slave15 Outlet Port02 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14552 | Slave15 Outlet Port03 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14553 | Slave15 Outlet Port04 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14554 | Slave15 Outlet Port05 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14555 | Slave15 Outlet Port06 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14556 | Slave15 Outlet Port07 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14557 | Slave15 Outlet Port08 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14558 | Slave15 Outlet Port09 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14559 | Slave15 Outlet Port10 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14560 | Slave15 Outlet Port11 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14561 | Slave15 Outlet Port12 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14562 | Slave15 Outlet Port13 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14563 | Slave15 Outlet Port14 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14564 | Slave15 Outlet Port15 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14565 | Slave15 Outlet Port16 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14566 | Slave15 Outlet Port17 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14567 | Slave15 Outlet Port18 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14568 | Slave15 Outlet Port19 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14569 | Slave15 Outlet Port20 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14570 | Slave15 Outlet Port21 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14571 | Slave15 Outlet Port22 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14572 | Slave15 Outlet Port23 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14573 | Slave15 Outlet Port24 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14574 | Slave15 Outlet Port25 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14575 | Slave15 Outlet Port26 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14576 | Slave15 Outlet Port27 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14577 | Slave15 Outlet Port28 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14578 | Slave15 Outlet Port29 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14579 | Slave15 Outlet Port30 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14580 | Slave15 Outlet Port31 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14581 | Slave15 Outlet Port32 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14582 | Slave15 Outlet Port33 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14583 | Slave15 Outlet Port34 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14584 | Slave15 Outlet Port35 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14585 | Slave15 Outlet Port36 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14586 | Slave15 Outlet Port37 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14587 | Slave15 Outlet Port38 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14588 | Slave15 Outlet Port39 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14589 | Slave15 Outlet Port40 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14590 | Slave15 Outlet Port41 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14591 | Slave15 Outlet Port42 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
14592 | Master Outlet Port01 Over Current Critical | RW | 2 bytes | Unit:0.01A
14593 | Master Outlet Port02 Over Current Critical | RW | 2 bytes | Unit:0.01A
14594 | Master Outlet Port03 Over Current Critical | RW | 2 bytes | Unit:0.01A
14595 | Master Outlet Port04 Over Current Critical | RW | 2 bytes | Unit:0.01A
14596 | Master Outlet Port05 Over Current Critical | RW | 2 bytes | Unit:0.01A
14597 | Master Outlet Port06 Over Current Critical | RW | 2 bytes | Unit:0.01A
14598 | Master Outlet Port07 Over Current Critical | RW | 2 bytes | Unit:0.01A
14599 | Master Outlet Port08 Over Current Critical | RW | 2 bytes | Unit:0.01A
14600 | Master Outlet Port09 Over Current Critical | RW | 2 bytes | Unit:0.01A
14601 | Master Outlet Port10 Over Current Critical | RW | 2 bytes | Unit:0.01A
14602 | Master Outlet Port11 Over Current Critical | RW | 2 bytes | Unit:0.01A
14603 | Master Outlet Port12 Over Current Critical | RW | 2 bytes | Unit:0.01A
14604 | Master Outlet Port13 Over Current Critical | RW | 2 bytes | Unit:0.01A
14605 | Master Outlet Port14 Over Current Critical | RW | 2 bytes | Unit:0.01A
14606 | Master Outlet Port15 Over Current Critical | RW | 2 bytes | Unit:0.01A
14607 | Master Outlet Port16 Over Current Critical | RW | 2 bytes | Unit:0.01A
14608 | Master Outlet Port17 Over Current Critical | RW | 2 bytes | Unit:0.01A
14609 | Master Outlet Port18 Over Current Critical | RW | 2 bytes | Unit:0.01A
14610 | Master Outlet Port19 Over Current Critical | RW | 2 bytes | Unit:0.01A
14611 | Master Outlet Port20 Over Current Critical | RW | 2 bytes | Unit:0.01A
14612 | Master Outlet Port21 Over Current Critical | RW | 2 bytes | Unit:0.01A
14613 | Master Outlet Port22 Over Current Critical | RW | 2 bytes | Unit:0.01A
14614 | Master Outlet Port23 Over Current Critical | RW | 2 bytes | Unit:0.01A
14615 | Master Outlet Port24 Over Current Critical | RW | 2 bytes | Unit:0.01A
14616 | Master Outlet Port25 Over Current Critical | RW | 2 bytes | Unit:0.01A
14617 | Master Outlet Port26 Over Current Critical | RW | 2 bytes | Unit:0.01A
14618 | Master Outlet Port27 Over Current Critical | RW | 2 bytes | Unit:0.01A
14619 | Master Outlet Port28 Over Current Critical | RW | 2 bytes | Unit:0.01A
14620 | Master Outlet Port29 Over Current Critical | RW | 2 bytes | Unit:0.01A
14621 | Master Outlet Port30 Over Current Critical | RW | 2 bytes | Unit:0.01A
14622 | Master Outlet Port31 Over Current Critical | RW | 2 bytes | Unit:0.01A
14623 | Master Outlet Port32 Over Current Critical | RW | 2 bytes | Unit:0.01A
14624 | Master Outlet Port33 Over Current Critical | RW | 2 bytes | Unit:0.01A
14625 | Master Outlet Port34 Over Current Critical | RW | 2 bytes | Unit:0.01A
14626 | Master Outlet Port35 Over Current Critical | RW | 2 bytes | Unit:0.01A
14627 | Master Outlet Port36 Over Current Critical | RW | 2 bytes | Unit:0.01A
14628 | Master Outlet Port37 Over Current Critical | RW | 2 bytes | Unit:0.01A
14629 | Master Outlet Port38 Over Current Critical | RW | 2 bytes | Unit:0.01A
14630 | Master Outlet Port39 Over Current Critical | RW | 2 bytes | Unit:0.01A
14631 | Master Outlet Port40 Over Current Critical | RW | 2 bytes | Unit:0.01A
14632 | Master Outlet Port41 Over Current Critical | RW | 2 bytes | Unit:0.01A
14633 | Master Outlet Port42 Over Current Critical | RW | 2 bytes | Unit:0.01A
14634 | Slave01 Outlet Port01 Over Current Critical | RW | 2 bytes | Unit:0.01A
14635 | Slave01 Outlet Port02 Over Current Critical | RW | 2 bytes | Unit:0.01A
14636 | Slave01 Outlet Port03 Over Current Critical | RW | 2 bytes | Unit:0.01A
14637 | Slave01 Outlet Port04 Over Current Critical | RW | 2 bytes | Unit:0.01A
14638 | Slave01 Outlet Port05 Over Current Critical | RW | 2 bytes | Unit:0.01A
14639 | Slave01 Outlet Port06 Over Current Critical | RW | 2 bytes | Unit:0.01A
14640 | Slave01 Outlet Port07 Over Current Critical | RW | 2 bytes | Unit:0.01A
14641 | Slave01 Outlet Port08 Over Current Critical | RW | 2 bytes | Unit:0.01A
14642 | Slave01 Outlet Port09 Over Current Critical | RW | 2 bytes | Unit:0.01A
14643 | Slave01 Outlet Port10 Over Current Critical | RW | 2 bytes | Unit:0.01A
14644 | Slave01 Outlet Port11 Over Current Critical | RW | 2 bytes | Unit:0.01A
14645 | Slave01 Outlet Port12 Over Current Critical | RW | 2 bytes | Unit:0.01A
14646 | Slave01 Outlet Port13 Over Current Critical | RW | 2 bytes | Unit:0.01A
14647 | Slave01 Outlet Port14 Over Current Critical | RW | 2 bytes | Unit:0.01A
14648 | Slave01 Outlet Port15 Over Current Critical | RW | 2 bytes | Unit:0.01A
14649 | Slave01 Outlet Port16 Over Current Critical | RW | 2 bytes | Unit:0.01A
14650 | Slave01 Outlet Port17 Over Current Critical | RW | 2 bytes | Unit:0.01A
14651 | Slave01 Outlet Port18 Over Current Critical | RW | 2 bytes | Unit:0.01A
14652 | Slave01 Outlet Port19 Over Current Critical | RW | 2 bytes | Unit:0.01A
14653 | Slave01 Outlet Port20 Over Current Critical | RW | 2 bytes | Unit:0.01A
14654 | Slave01 Outlet Port21 Over Current Critical | RW | 2 bytes | Unit:0.01A
14655 | Slave01 Outlet Port22 Over Current Critical | RW | 2 bytes | Unit:0.01A
14656 | Slave01 Outlet Port23 Over Current Critical | RW | 2 bytes | Unit:0.01A
14657 | Slave01 Outlet Port24 Over Current Critical | RW | 2 bytes | Unit:0.01A
14658 | Slave01 Outlet Port25 Over Current Critical | RW | 2 bytes | Unit:0.01A
14659 | Slave01 Outlet Port26 Over Current Critical | RW | 2 bytes | Unit:0.01A
14660 | Slave01 Outlet Port27 Over Current Critical | RW | 2 bytes | Unit:0.01A
14661 | Slave01 Outlet Port28 Over Current Critical | RW | 2 bytes | Unit:0.01A
14662 | Slave01 Outlet Port29 Over Current Critical | RW | 2 bytes | Unit:0.01A
14663 | Slave01 Outlet Port30 Over Current Critical | RW | 2 bytes | Unit:0.01A
14664 | Slave01 Outlet Port31 Over Current Critical | RW | 2 bytes | Unit:0.01A
14665 | Slave01 Outlet Port32 Over Current Critical | RW | 2 bytes | Unit:0.01A
14666 | Slave01 Outlet Port33 Over Current Critical | RW | 2 bytes | Unit:0.01A
14667 | Slave01 Outlet Port34 Over Current Critical | RW | 2 bytes | Unit:0.01A
14668 | Slave01 Outlet Port35 Over Current Critical | RW | 2 bytes | Unit:0.01A
14669 | Slave01 Outlet Port36 Over Current Critical | RW | 2 bytes | Unit:0.01A
14670 | Slave01 Outlet Port37 Over Current Critical | RW | 2 bytes | Unit:0.01A
14671 | Slave01 Outlet Port38 Over Current Critical | RW | 2 bytes | Unit:0.01A
14672 | Slave01 Outlet Port39 Over Current Critical | RW | 2 bytes | Unit:0.01A
14673 | Slave01 Outlet Port40 Over Current Critical | RW | 2 bytes | Unit:0.01A
14674 | Slave01 Outlet Port41 Over Current Critical | RW | 2 bytes | Unit:0.01A
14675 | Slave01 Outlet Port42 Over Current Critical | RW | 2 bytes | Unit:0.01A
14676 | Slave02 Outlet Port01 Over Current Critical | RW | 2 bytes | Unit:0.01A
14677 | Slave02 Outlet Port02 Over Current Critical | RW | 2 bytes | Unit:0.01A
14678 | Slave02 Outlet Port03 Over Current Critical | RW | 2 bytes | Unit:0.01A
14679 | Slave02 Outlet Port04 Over Current Critical | RW | 2 bytes | Unit:0.01A
14680 | Slave02 Outlet Port05 Over Current Critical | RW | 2 bytes | Unit:0.01A
14681 | Slave02 Outlet Port06 Over Current Critical | RW | 2 bytes | Unit:0.01A
14682 | Slave02 Outlet Port07 Over Current Critical | RW | 2 bytes | Unit:0.01A
14683 | Slave02 Outlet Port08 Over Current Critical | RW | 2 bytes | Unit:0.01A
14684 | Slave02 Outlet Port09 Over Current Critical | RW | 2 bytes | Unit:0.01A
14685 | Slave02 Outlet Port10 Over Current Critical | RW | 2 bytes | Unit:0.01A
14686 | Slave02 Outlet Port11 Over Current Critical | RW | 2 bytes | Unit:0.01A
14687 | Slave02 Outlet Port12 Over Current Critical | RW | 2 bytes | Unit:0.01A
14688 | Slave02 Outlet Port13 Over Current Critical | RW | 2 bytes | Unit:0.01A
14689 | Slave02 Outlet Port14 Over Current Critical | RW | 2 bytes | Unit:0.01A
14690 | Slave02 Outlet Port15 Over Current Critical | RW | 2 bytes | Unit:0.01A
14691 | Slave02 Outlet Port16 Over Current Critical | RW | 2 bytes | Unit:0.01A
14692 | Slave02 Outlet Port17 Over Current Critical | RW | 2 bytes | Unit:0.01A
14693 | Slave02 Outlet Port18 Over Current Critical | RW | 2 bytes | Unit:0.01A
14694 | Slave02 Outlet Port19 Over Current Critical | RW | 2 bytes | Unit:0.01A
14695 | Slave02 Outlet Port20 Over Current Critical | RW | 2 bytes | Unit:0.01A
14696 | Slave02 Outlet Port21 Over Current Critical | RW | 2 bytes | Unit:0.01A
14697 | Slave02 Outlet Port22 Over Current Critical | RW | 2 bytes | Unit:0.01A
14698 | Slave02 Outlet Port23 Over Current Critical | RW | 2 bytes | Unit:0.01A
14699 | Slave02 Outlet Port24 Over Current Critical | RW | 2 bytes | Unit:0.01A
14700 | Slave02 Outlet Port25 Over Current Critical | RW | 2 bytes | Unit:0.01A
14701 | Slave02 Outlet Port26 Over Current Critical | RW | 2 bytes | Unit:0.01A
14702 | Slave02 Outlet Port27 Over Current Critical | RW | 2 bytes | Unit:0.01A
14703 | Slave02 Outlet Port28 Over Current Critical | RW | 2 bytes | Unit:0.01A
14704 | Slave02 Outlet Port29 Over Current Critical | RW | 2 bytes | Unit:0.01A
14705 | Slave02 Outlet Port30 Over Current Critical | RW | 2 bytes | Unit:0.01A
14706 | Slave02 Outlet Port31 Over Current Critical | RW | 2 bytes | Unit:0.01A
14707 | Slave02 Outlet Port32 Over Current Critical | RW | 2 bytes | Unit:0.01A
14708 | Slave02 Outlet Port33 Over Current Critical | RW | 2 bytes | Unit:0.01A
14709 | Slave02 Outlet Port34 Over Current Critical | RW | 2 bytes | Unit:0.01A
14710 | Slave02 Outlet Port35 Over Current Critical | RW | 2 bytes | Unit:0.01A
14711 | Slave02 Outlet Port36 Over Current Critical | RW | 2 bytes | Unit:0.01A
14712 | Slave02 Outlet Port37 Over Current Critical | RW | 2 bytes | Unit:0.01A
14713 | Slave02 Outlet Port38 Over Current Critical | RW | 2 bytes | Unit:0.01A
14714 | Slave02 Outlet Port39 Over Current Critical | RW | 2 bytes | Unit:0.01A
14715 | Slave02 Outlet Port40 Over Current Critical | RW | 2 bytes | Unit:0.01A
14716 | Slave02 Outlet Port41 Over Current Critical | RW | 2 bytes | Unit:0.01A
14717 | Slave02 Outlet Port42 Over Current Critical | RW | 2 bytes | Unit:0.01A
14718 | Slave03 Outlet Port01 Over Current Critical | RW | 2 bytes | Unit:0.01A
14719 | Slave03 Outlet Port02 Over Current Critical | RW | 2 bytes | Unit:0.01A
14720 | Slave03 Outlet Port03 Over Current Critical | RW | 2 bytes | Unit:0.01A
14721 | Slave03 Outlet Port04 Over Current Critical | RW | 2 bytes | Unit:0.01A
14722 | Slave03 Outlet Port05 Over Current Critical | RW | 2 bytes | Unit:0.01A
14723 | Slave03 Outlet Port06 Over Current Critical | RW | 2 bytes | Unit:0.01A
14724 | Slave03 Outlet Port07 Over Current Critical | RW | 2 bytes | Unit:0.01A
14725 | Slave03 Outlet Port08 Over Current Critical | RW | 2 bytes | Unit:0.01A
14726 | Slave03 Outlet Port09 Over Current Critical | RW | 2 bytes | Unit:0.01A
14727 | Slave03 Outlet Port10 Over Current Critical | RW | 2 bytes | Unit:0.01A
14728 | Slave03 Outlet Port11 Over Current Critical | RW | 2 bytes | Unit:0.01A
14729 | Slave03 Outlet Port12 Over Current Critical | RW | 2 bytes | Unit:0.01A
14730 | Slave03 Outlet Port13 Over Current Critical | RW | 2 bytes | Unit:0.01A
14731 | Slave03 Outlet Port14 Over Current Critical | RW | 2 bytes | Unit:0.01A
14732 | Slave03 Outlet Port15 Over Current Critical | RW | 2 bytes | Unit:0.01A
14733 | Slave03 Outlet Port16 Over Current Critical | RW | 2 bytes | Unit:0.01A
14734 | Slave03 Outlet Port17 Over Current Critical | RW | 2 bytes | Unit:0.01A
14735 | Slave03 Outlet Port18 Over Current Critical | RW | 2 bytes | Unit:0.01A
14736 | Slave03 Outlet Port19 Over Current Critical | RW | 2 bytes | Unit:0.01A
14737 | Slave03 Outlet Port20 Over Current Critical | RW | 2 bytes | Unit:0.01A
14738 | Slave03 Outlet Port21 Over Current Critical | RW | 2 bytes | Unit:0.01A
14739 | Slave03 Outlet Port22 Over Current Critical | RW | 2 bytes | Unit:0.01A
14740 | Slave03 Outlet Port23 Over Current Critical | RW | 2 bytes | Unit:0.01A
14741 | Slave03 Outlet Port24 Over Current Critical | RW | 2 bytes | Unit:0.01A
14742 | Slave03 Outlet Port25 Over Current Critical | RW | 2 bytes | Unit:0.01A
14743 | Slave03 Outlet Port26 Over Current Critical | RW | 2 bytes | Unit:0.01A
14744 | Slave03 Outlet Port27 Over Current Critical | RW | 2 bytes | Unit:0.01A
14745 | Slave03 Outlet Port28 Over Current Critical | RW | 2 bytes | Unit:0.01A
14746 | Slave03 Outlet Port29 Over Current Critical | RW | 2 bytes | Unit:0.01A
14747 | Slave03 Outlet Port30 Over Current Critical | RW | 2 bytes | Unit:0.01A
14748 | Slave03 Outlet Port31 Over Current Critical | RW | 2 bytes | Unit:0.01A
14749 | Slave03 Outlet Port32 Over Current Critical | RW | 2 bytes | Unit:0.01A
14750 | Slave03 Outlet Port33 Over Current Critical | RW | 2 bytes | Unit:0.01A
14751 | Slave03 Outlet Port34 Over Current Critical | RW | 2 bytes | Unit:0.01A
14752 | Slave03 Outlet Port35 Over Current Critical | RW | 2 bytes | Unit:0.01A
14753 | Slave03 Outlet Port36 Over Current Critical | RW | 2 bytes | Unit:0.01A
14754 | Slave03 Outlet Port37 Over Current Critical | RW | 2 bytes | Unit:0.01A
14755 | Slave03 Outlet Port38 Over Current Critical | RW | 2 bytes | Unit:0.01A
14756 | Slave03 Outlet Port39 Over Current Critical | RW | 2 bytes | Unit:0.01A
14757 | Slave03 Outlet Port40 Over Current Critical | RW | 2 bytes | Unit:0.01A
14758 | Slave03 Outlet Port41 Over Current Critical | RW | 2 bytes | Unit:0.01A
14759 | Slave03 Outlet Port42 Over Current Critical | RW | 2 bytes | Unit:0.01A
14760 | Slave04 Outlet Port01 Over Current Critical | RW | 2 bytes | Unit:0.01A
14761 | Slave04 Outlet Port02 Over Current Critical | RW | 2 bytes | Unit:0.01A
14762 | Slave04 Outlet Port03 Over Current Critical | RW | 2 bytes | Unit:0.01A
14763 | Slave04 Outlet Port04 Over Current Critical | RW | 2 bytes | Unit:0.01A
14764 | Slave04 Outlet Port05 Over Current Critical | RW | 2 bytes | Unit:0.01A
14765 | Slave04 Outlet Port06 Over Current Critical | RW | 2 bytes | Unit:0.01A
14766 | Slave04 Outlet Port07 Over Current Critical | RW | 2 bytes | Unit:0.01A
14767 | Slave04 Outlet Port08 Over Current Critical | RW | 2 bytes | Unit:0.01A
14768 | Slave04 Outlet Port09 Over Current Critical | RW | 2 bytes | Unit:0.01A
14769 | Slave04 Outlet Port10 Over Current Critical | RW | 2 bytes | Unit:0.01A
14770 | Slave04 Outlet Port11 Over Current Critical | RW | 2 bytes | Unit:0.01A
14771 | Slave04 Outlet Port12 Over Current Critical | RW | 2 bytes | Unit:0.01A
14772 | Slave04 Outlet Port13 Over Current Critical | RW | 2 bytes | Unit:0.01A
14773 | Slave04 Outlet Port14 Over Current Critical | RW | 2 bytes | Unit:0.01A
14774 | Slave04 Outlet Port15 Over Current Critical | RW | 2 bytes | Unit:0.01A
14775 | Slave04 Outlet Port16 Over Current Critical | RW | 2 bytes | Unit:0.01A
14776 | Slave04 Outlet Port17 Over Current Critical | RW | 2 bytes | Unit:0.01A
14777 | Slave04 Outlet Port18 Over Current Critical | RW | 2 bytes | Unit:0.01A
14778 | Slave04 Outlet Port19 Over Current Critical | RW | 2 bytes | Unit:0.01A
14779 | Slave04 Outlet Port20 Over Current Critical | RW | 2 bytes | Unit:0.01A
14780 | Slave04 Outlet Port21 Over Current Critical | RW | 2 bytes | Unit:0.01A
14781 | Slave04 Outlet Port22 Over Current Critical | RW | 2 bytes | Unit:0.01A
14782 | Slave04 Outlet Port23 Over Current Critical | RW | 2 bytes | Unit:0.01A
14783 | Slave04 Outlet Port24 Over Current Critical | RW | 2 bytes | Unit:0.01A
14784 | Slave04 Outlet Port25 Over Current Critical | RW | 2 bytes | Unit:0.01A
14785 | Slave04 Outlet Port26 Over Current Critical | RW | 2 bytes | Unit:0.01A
14786 | Slave04 Outlet Port27 Over Current Critical | RW | 2 bytes | Unit:0.01A
14787 | Slave04 Outlet Port28 Over Current Critical | RW | 2 bytes | Unit:0.01A
14788 | Slave04 Outlet Port29 Over Current Critical | RW | 2 bytes | Unit:0.01A
14789 | Slave04 Outlet Port30 Over Current Critical | RW | 2 bytes | Unit:0.01A
14790 | Slave04 Outlet Port31 Over Current Critical | RW | 2 bytes | Unit:0.01A
14791 | Slave04 Outlet Port32 Over Current Critical | RW | 2 bytes | Unit:0.01A
14792 | Slave04 Outlet Port33 Over Current Critical | RW | 2 bytes | Unit:0.01A
14793 | Slave04 Outlet Port34 Over Current Critical | RW | 2 bytes | Unit:0.01A
14794 | Slave04 Outlet Port35 Over Current Critical | RW | 2 bytes | Unit:0.01A
14795 | Slave04 Outlet Port36 Over Current Critical | RW | 2 bytes | Unit:0.01A
14796 | Slave04 Outlet Port37 Over Current Critical | RW | 2 bytes | Unit:0.01A
14797 | Slave04 Outlet Port38 Over Current Critical | RW | 2 bytes | Unit:0.01A
14798 | Slave04 Outlet Port39 Over Current Critical | RW | 2 bytes | Unit:0.01A
14799 | Slave04 Outlet Port40 Over Current Critical | RW | 2 bytes | Unit:0.01A
14800 | Slave04 Outlet Port41 Over Current Critical | RW | 2 bytes | Unit:0.01A
14801 | Slave04 Outlet Port42 Over Current Critical | RW | 2 bytes | Unit:0.01A
14802 | Slave05 Outlet Port01 Over Current Critical | RW | 2 bytes | Unit:0.01A
14803 | Slave05 Outlet Port02 Over Current Critical | RW | 2 bytes | Unit:0.01A
14804 | Slave05 Outlet Port03 Over Current Critical | RW | 2 bytes | Unit:0.01A
14805 | Slave05 Outlet Port04 Over Current Critical | RW | 2 bytes | Unit:0.01A
14806 | Slave05 Outlet Port05 Over Current Critical | RW | 2 bytes | Unit:0.01A
14807 | Slave05 Outlet Port06 Over Current Critical | RW | 2 bytes | Unit:0.01A
14808 | Slave05 Outlet Port07 Over Current Critical | RW | 2 bytes | Unit:0.01A
14809 | Slave05 Outlet Port08 Over Current Critical | RW | 2 bytes | Unit:0.01A
14810 | Slave05 Outlet Port09 Over Current Critical | RW | 2 bytes | Unit:0.01A
14811 | Slave05 Outlet Port10 Over Current Critical | RW | 2 bytes | Unit:0.01A
14812 | Slave05 Outlet Port11 Over Current Critical | RW | 2 bytes | Unit:0.01A
14813 | Slave05 Outlet Port12 Over Current Critical | RW | 2 bytes | Unit:0.01A
14814 | Slave05 Outlet Port13 Over Current Critical | RW | 2 bytes | Unit:0.01A
14815 | Slave05 Outlet Port14 Over Current Critical | RW | 2 bytes | Unit:0.01A
14816 | Slave05 Outlet Port15 Over Current Critical | RW | 2 bytes | Unit:0.01A
14817 | Slave05 Outlet Port16 Over Current Critical | RW | 2 bytes | Unit:0.01A
14818 | Slave05 Outlet Port17 Over Current Critical | RW | 2 bytes | Unit:0.01A
14819 | Slave05 Outlet Port18 Over Current Critical | RW | 2 bytes | Unit:0.01A
14820 | Slave05 Outlet Port19 Over Current Critical | RW | 2 bytes | Unit:0.01A
14821 | Slave05 Outlet Port20 Over Current Critical | RW | 2 bytes | Unit:0.01A
14822 | Slave05 Outlet Port21 Over Current Critical | RW | 2 bytes | Unit:0.01A
14823 | Slave05 Outlet Port22 Over Current Critical | RW | 2 bytes | Unit:0.01A
14824 | Slave05 Outlet Port23 Over Current Critical | RW | 2 bytes | Unit:0.01A
14825 | Slave05 Outlet Port24 Over Current Critical | RW | 2 bytes | Unit:0.01A
14826 | Slave05 Outlet Port25 Over Current Critical | RW | 2 bytes | Unit:0.01A
14827 | Slave05 Outlet Port26 Over Current Critical | RW | 2 bytes | Unit:0.01A
14828 | Slave05 Outlet Port27 Over Current Critical | RW | 2 bytes | Unit:0.01A
14829 | Slave05 Outlet Port28 Over Current Critical | RW | 2 bytes | Unit:0.01A
14830 | Slave05 Outlet Port29 Over Current Critical | RW | 2 bytes | Unit:0.01A
14831 | Slave05 Outlet Port30 Over Current Critical | RW | 2 bytes | Unit:0.01A
14832 | Slave05 Outlet Port31 Over Current Critical | RW | 2 bytes | Unit:0.01A
14833 | Slave05 Outlet Port32 Over Current Critical | RW | 2 bytes | Unit:0.01A
14834 | Slave05 Outlet Port33 Over Current Critical | RW | 2 bytes | Unit:0.01A
14835 | Slave05 Outlet Port34 Over Current Critical | RW | 2 bytes | Unit:0.01A
14836 | Slave05 Outlet Port35 Over Current Critical | RW | 2 bytes | Unit:0.01A
14837 | Slave05 Outlet Port36 Over Current Critical | RW | 2 bytes | Unit:0.01A
14838 | Slave05 Outlet Port37 Over Current Critical | RW | 2 bytes | Unit:0.01A
14839 | Slave05 Outlet Port38 Over Current Critical | RW | 2 bytes | Unit:0.01A
14840 | Slave05 Outlet Port39 Over Current Critical | RW | 2 bytes | Unit:0.01A
14841 | Slave05 Outlet Port40 Over Current Critical | RW | 2 bytes | Unit:0.01A
14842 | Slave05 Outlet Port41 Over Current Critical | RW | 2 bytes | Unit:0.01A
14843 | Slave05 Outlet Port42 Over Current Critical | RW | 2 bytes | Unit:0.01A
14844 | Slave06 Outlet Port01 Over Current Critical | RW | 2 bytes | Unit:0.01A
14845 | Slave06 Outlet Port02 Over Current Critical | RW | 2 bytes | Unit:0.01A
14846 | Slave06 Outlet Port03 Over Current Critical | RW | 2 bytes | Unit:0.01A
14847 | Slave06 Outlet Port04 Over Current Critical | RW | 2 bytes | Unit:0.01A
14848 | Slave06 Outlet Port05 Over Current Critical | RW | 2 bytes | Unit:0.01A
14849 | Slave06 Outlet Port06 Over Current Critical | RW | 2 bytes | Unit:0.01A
14850 | Slave06 Outlet Port07 Over Current Critical | RW | 2 bytes | Unit:0.01A
14851 | Slave06 Outlet Port08 Over Current Critical | RW | 2 bytes | Unit:0.01A
14852 | Slave06 Outlet Port09 Over Current Critical | RW | 2 bytes | Unit:0.01A
14853 | Slave06 Outlet Port10 Over Current Critical | RW | 2 bytes | Unit:0.01A
14854 | Slave06 Outlet Port11 Over Current Critical | RW | 2 bytes | Unit:0.01A
14855 | Slave06 Outlet Port12 Over Current Critical | RW | 2 bytes | Unit:0.01A
14856 | Slave06 Outlet Port13 Over Current Critical | RW | 2 bytes | Unit:0.01A
14857 | Slave06 Outlet Port14 Over Current Critical | RW | 2 bytes | Unit:0.01A
14858 | Slave06 Outlet Port15 Over Current Critical | RW | 2 bytes | Unit:0.01A
14859 | Slave06 Outlet Port16 Over Current Critical | RW | 2 bytes | Unit:0.01A
14860 | Slave06 Outlet Port17 Over Current Critical | RW | 2 bytes | Unit:0.01A
14861 | Slave06 Outlet Port18 Over Current Critical | RW | 2 bytes | Unit:0.01A
14862 | Slave06 Outlet Port19 Over Current Critical | RW | 2 bytes | Unit:0.01A
14863 | Slave06 Outlet Port20 Over Current Critical | RW | 2 bytes | Unit:0.01A
14864 | Slave06 Outlet Port21 Over Current Critical | RW | 2 bytes | Unit:0.01A
14865 | Slave06 Outlet Port22 Over Current Critical | RW | 2 bytes | Unit:0.01A
14866 | Slave06 Outlet Port23 Over Current Critical | RW | 2 bytes | Unit:0.01A
14867 | Slave06 Outlet Port24 Over Current Critical | RW | 2 bytes | Unit:0.01A
14868 | Slave06 Outlet Port25 Over Current Critical | RW | 2 bytes | Unit:0.01A
14869 | Slave06 Outlet Port26 Over Current Critical | RW | 2 bytes | Unit:0.01A
14870 | Slave06 Outlet Port27 Over Current Critical | RW | 2 bytes | Unit:0.01A
14871 | Slave06 Outlet Port28 Over Current Critical | RW | 2 bytes | Unit:0.01A
14872 | Slave06 Outlet Port29 Over Current Critical | RW | 2 bytes | Unit:0.01A
14873 | Slave06 Outlet Port30 Over Current Critical | RW | 2 bytes | Unit:0.01A
14874 | Slave06 Outlet Port31 Over Current Critical | RW | 2 bytes | Unit:0.01A
14875 | Slave06 Outlet Port32 Over Current Critical | RW | 2 bytes | Unit:0.01A
14876 | Slave06 Outlet Port33 Over Current Critical | RW | 2 bytes | Unit:0.01A
14877 | Slave06 Outlet Port34 Over Current Critical | RW | 2 bytes | Unit:0.01A
14878 | Slave06 Outlet Port35 Over Current Critical | RW | 2 bytes | Unit:0.01A
14879 | Slave06 Outlet Port36 Over Current Critical | RW | 2 bytes | Unit:0.01A
14880 | Slave06 Outlet Port37 Over Current Critical | RW | 2 bytes | Unit:0.01A
14881 | Slave06 Outlet Port38 Over Current Critical | RW | 2 bytes | Unit:0.01A
14882 | Slave06 Outlet Port39 Over Current Critical | RW | 2 bytes | Unit:0.01A
14883 | Slave06 Outlet Port40 Over Current Critical | RW | 2 bytes | Unit:0.01A
14884 | Slave06 Outlet Port41 Over Current Critical | RW | 2 bytes | Unit:0.01A
14885 | Slave06 Outlet Port42 Over Current Critical | RW | 2 bytes | Unit:0.01A
14886 | Slave07 Outlet Port01 Over Current Critical | RW | 2 bytes | Unit:0.01A
14887 | Slave07 Outlet Port02 Over Current Critical | RW | 2 bytes | Unit:0.01A
14888 | Slave07 Outlet Port03 Over Current Critical | RW | 2 bytes | Unit:0.01A
14889 | Slave07 Outlet Port04 Over Current Critical | RW | 2 bytes | Unit:0.01A
14890 | Slave07 Outlet Port05 Over Current Critical | RW | 2 bytes | Unit:0.01A
14891 | Slave07 Outlet Port06 Over Current Critical | RW | 2 bytes | Unit:0.01A
14892 | Slave07 Outlet Port07 Over Current Critical | RW | 2 bytes | Unit:0.01A
14893 | Slave07 Outlet Port08 Over Current Critical | RW | 2 bytes | Unit:0.01A
14894 | Slave07 Outlet Port09 Over Current Critical | RW | 2 bytes | Unit:0.01A
14895 | Slave07 Outlet Port10 Over Current Critical | RW | 2 bytes | Unit:0.01A
14896 | Slave07 Outlet Port11 Over Current Critical | RW | 2 bytes | Unit:0.01A
14897 | Slave07 Outlet Port12 Over Current Critical | RW | 2 bytes | Unit:0.01A
14898 | Slave07 Outlet Port13 Over Current Critical | RW | 2 bytes | Unit:0.01A
14899 | Slave07 Outlet Port14 Over Current Critical | RW | 2 bytes | Unit:0.01A
14900 | Slave07 Outlet Port15 Over Current Critical | RW | 2 bytes | Unit:0.01A
14901 | Slave07 Outlet Port16 Over Current Critical | RW | 2 bytes | Unit:0.01A
14902 | Slave07 Outlet Port17 Over Current Critical | RW | 2 bytes | Unit:0.01A
14903 | Slave07 Outlet Port18 Over Current Critical | RW | 2 bytes | Unit:0.01A
14904 | Slave07 Outlet Port19 Over Current Critical | RW | 2 bytes | Unit:0.01A
14905 | Slave07 Outlet Port20 Over Current Critical | RW | 2 bytes | Unit:0.01A
14906 | Slave07 Outlet Port21 Over Current Critical | RW | 2 bytes | Unit:0.01A
14907 | Slave07 Outlet Port22 Over Current Critical | RW | 2 bytes | Unit:0.01A
14908 | Slave07 Outlet Port23 Over Current Critical | RW | 2 bytes | Unit:0.01A
14909 | Slave07 Outlet Port24 Over Current Critical | RW | 2 bytes | Unit:0.01A
14910 | Slave07 Outlet Port25 Over Current Critical | RW | 2 bytes | Unit:0.01A
14911 | Slave07 Outlet Port26 Over Current Critical | RW | 2 bytes | Unit:0.01A
14912 | Slave07 Outlet Port27 Over Current Critical | RW | 2 bytes | Unit:0.01A
14913 | Slave07 Outlet Port28 Over Current Critical | RW | 2 bytes | Unit:0.01A
14914 | Slave07 Outlet Port29 Over Current Critical | RW | 2 bytes | Unit:0.01A
14915 | Slave07 Outlet Port30 Over Current Critical | RW | 2 bytes | Unit:0.01A
14916 | Slave07 Outlet Port31 Over Current Critical | RW | 2 bytes | Unit:0.01A
14917 | Slave07 Outlet Port32 Over Current Critical | RW | 2 bytes | Unit:0.01A
14918 | Slave07 Outlet Port33 Over Current Critical | RW | 2 bytes | Unit:0.01A
14919 | Slave07 Outlet Port34 Over Current Critical | RW | 2 bytes | Unit:0.01A
14920 | Slave07 Outlet Port35 Over Current Critical | RW | 2 bytes | Unit:0.01A
14921 | Slave07 Outlet Port36 Over Current Critical | RW | 2 bytes | Unit:0.01A
14922 | Slave07 Outlet Port37 Over Current Critical | RW | 2 bytes | Unit:0.01A
14923 | Slave07 Outlet Port38 Over Current Critical | RW | 2 bytes | Unit:0.01A
14924 | Slave07 Outlet Port39 Over Current Critical | RW | 2 bytes | Unit:0.01A
14925 | Slave07 Outlet Port40 Over Current Critical | RW | 2 bytes | Unit:0.01A
14926 | Slave07 Outlet Port41 Over Current Critical | RW | 2 bytes | Unit:0.01A
14927 | Slave07 Outlet Port42 Over Current Critical | RW | 2 bytes | Unit:0.01A
14928 | Slave08 Outlet Port01 Over Current Critical | RW | 2 bytes | Unit:0.01A
14929 | Slave08 Outlet Port02 Over Current Critical | RW | 2 bytes | Unit:0.01A
14930 | Slave08 Outlet Port03 Over Current Critical | RW | 2 bytes | Unit:0.01A
14931 | Slave08 Outlet Port04 Over Current Critical | RW | 2 bytes | Unit:0.01A
14932 | Slave08 Outlet Port05 Over Current Critical | RW | 2 bytes | Unit:0.01A
14933 | Slave08 Outlet Port06 Over Current Critical | RW | 2 bytes | Unit:0.01A
14934 | Slave08 Outlet Port07 Over Current Critical | RW | 2 bytes | Unit:0.01A
14935 | Slave08 Outlet Port08 Over Current Critical | RW | 2 bytes | Unit:0.01A
14936 | Slave08 Outlet Port09 Over Current Critical | RW | 2 bytes | Unit:0.01A
14937 | Slave08 Outlet Port10 Over Current Critical | RW | 2 bytes | Unit:0.01A
14938 | Slave08 Outlet Port11 Over Current Critical | RW | 2 bytes | Unit:0.01A
14939 | Slave08 Outlet Port12 Over Current Critical | RW | 2 bytes | Unit:0.01A
14940 | Slave08 Outlet Port13 Over Current Critical | RW | 2 bytes | Unit:0.01A
14941 | Slave08 Outlet Port14 Over Current Critical | RW | 2 bytes | Unit:0.01A
14942 | Slave08 Outlet Port15 Over Current Critical | RW | 2 bytes | Unit:0.01A
14943 | Slave08 Outlet Port16 Over Current Critical | RW | 2 bytes | Unit:0.01A
14944 | Slave08 Outlet Port17 Over Current Critical | RW | 2 bytes | Unit:0.01A
14945 | Slave08 Outlet Port18 Over Current Critical | RW | 2 bytes | Unit:0.01A
14946 | Slave08 Outlet Port19 Over Current Critical | RW | 2 bytes | Unit:0.01A
14947 | Slave08 Outlet Port20 Over Current Critical | RW | 2 bytes | Unit:0.01A
14948 | Slave08 Outlet Port21 Over Current Critical | RW | 2 bytes | Unit:0.01A
14949 | Slave08 Outlet Port22 Over Current Critical | RW | 2 bytes | Unit:0.01A
14950 | Slave08 Outlet Port23 Over Current Critical | RW | 2 bytes | Unit:0.01A
14951 | Slave08 Outlet Port24 Over Current Critical | RW | 2 bytes | Unit:0.01A
14952 | Slave08 Outlet Port25 Over Current Critical | RW | 2 bytes | Unit:0.01A
14953 | Slave08 Outlet Port26 Over Current Critical | RW | 2 bytes | Unit:0.01A
14954 | Slave08 Outlet Port27 Over Current Critical | RW | 2 bytes | Unit:0.01A
14955 | Slave08 Outlet Port28 Over Current Critical | RW | 2 bytes | Unit:0.01A
14956 | Slave08 Outlet Port29 Over Current Critical | RW | 2 bytes | Unit:0.01A
14957 | Slave08 Outlet Port30 Over Current Critical | RW | 2 bytes | Unit:0.01A
14958 | Slave08 Outlet Port31 Over Current Critical | RW | 2 bytes | Unit:0.01A
14959 | Slave08 Outlet Port32 Over Current Critical | RW | 2 bytes | Unit:0.01A
14960 | Slave08 Outlet Port33 Over Current Critical | RW | 2 bytes | Unit:0.01A
14961 | Slave08 Outlet Port34 Over Current Critical | RW | 2 bytes | Unit:0.01A
14962 | Slave08 Outlet Port35 Over Current Critical | RW | 2 bytes | Unit:0.01A
14963 | Slave08 Outlet Port36 Over Current Critical | RW | 2 bytes | Unit:0.01A
14964 | Slave08 Outlet Port37 Over Current Critical | RW | 2 bytes | Unit:0.01A
14965 | Slave08 Outlet Port38 Over Current Critical | RW | 2 bytes | Unit:0.01A
14966 | Slave08 Outlet Port39 Over Current Critical | RW | 2 bytes | Unit:0.01A
14967 | Slave08 Outlet Port40 Over Current Critical | RW | 2 bytes | Unit:0.01A
14968 | Slave08 Outlet Port41 Over Current Critical | RW | 2 bytes | Unit:0.01A
14969 | Slave08 Outlet Port42 Over Current Critical | RW | 2 bytes | Unit:0.01A
14970 | Slave09 Outlet Port01 Over Current Critical | RW | 2 bytes | Unit:0.01A
14971 | Slave09 Outlet Port02 Over Current Critical | RW | 2 bytes | Unit:0.01A
14972 | Slave09 Outlet Port03 Over Current Critical | RW | 2 bytes | Unit:0.01A
14973 | Slave09 Outlet Port04 Over Current Critical | RW | 2 bytes | Unit:0.01A
14974 | Slave09 Outlet Port05 Over Current Critical | RW | 2 bytes | Unit:0.01A
14975 | Slave09 Outlet Port06 Over Current Critical | RW | 2 bytes | Unit:0.01A
14976 | Slave09 Outlet Port07 Over Current Critical | RW | 2 bytes | Unit:0.01A
14977 | Slave09 Outlet Port08 Over Current Critical | RW | 2 bytes | Unit:0.01A
14978 | Slave09 Outlet Port09 Over Current Critical | RW | 2 bytes | Unit:0.01A
14979 | Slave09 Outlet Port10 Over Current Critical | RW | 2 bytes | Unit:0.01A
14980 | Slave09 Outlet Port11 Over Current Critical | RW | 2 bytes | Unit:0.01A
14981 | Slave09 Outlet Port12 Over Current Critical | RW | 2 bytes | Unit:0.01A
14982 | Slave09 Outlet Port13 Over Current Critical | RW | 2 bytes | Unit:0.01A
14983 | Slave09 Outlet Port14 Over Current Critical | RW | 2 bytes | Unit:0.01A
14984 | Slave09 Outlet Port15 Over Current Critical | RW | 2 bytes | Unit:0.01A
14985 | Slave09 Outlet Port16 Over Current Critical | RW | 2 bytes | Unit:0.01A
14986 | Slave09 Outlet Port17 Over Current Critical | RW | 2 bytes | Unit:0.01A
14987 | Slave09 Outlet Port18 Over Current Critical | RW | 2 bytes | Unit:0.01A
14988 | Slave09 Outlet Port19 Over Current Critical | RW | 2 bytes | Unit:0.01A
14989 | Slave09 Outlet Port20 Over Current Critical | RW | 2 bytes | Unit:0.01A
14990 | Slave09 Outlet Port21 Over Current Critical | RW | 2 bytes | Unit:0.01A
14991 | Slave09 Outlet Port22 Over Current Critical | RW | 2 bytes | Unit:0.01A
14992 | Slave09 Outlet Port23 Over Current Critical | RW | 2 bytes | Unit:0.01A
14993 | Slave09 Outlet Port24 Over Current Critical | RW | 2 bytes | Unit:0.01A
14994 | Slave09 Outlet Port25 Over Current Critical | RW | 2 bytes | Unit:0.01A
14995 | Slave09 Outlet Port26 Over Current Critical | RW | 2 bytes | Unit:0.01A
14996 | Slave09 Outlet Port27 Over Current Critical | RW | 2 bytes | Unit:0.01A
14997 | Slave09 Outlet Port28 Over Current Critical | RW | 2 bytes | Unit:0.01A
14998 | Slave09 Outlet Port29 Over Current Critical | RW | 2 bytes | Unit:0.01A
14999 | Slave09 Outlet Port30 Over Current Critical | RW | 2 bytes | Unit:0.01A
15000 | Slave09 Outlet Port31 Over Current Critical | RW | 2 bytes | Unit:0.01A
15001 | Slave09 Outlet Port32 Over Current Critical | RW | 2 bytes | Unit:0.01A
15002 | Slave09 Outlet Port33 Over Current Critical | RW | 2 bytes | Unit:0.01A
15003 | Slave09 Outlet Port34 Over Current Critical | RW | 2 bytes | Unit:0.01A
15004 | Slave09 Outlet Port35 Over Current Critical | RW | 2 bytes | Unit:0.01A
15005 | Slave09 Outlet Port36 Over Current Critical | RW | 2 bytes | Unit:0.01A
15006 | Slave09 Outlet Port37 Over Current Critical | RW | 2 bytes | Unit:0.01A
15007 | Slave09 Outlet Port38 Over Current Critical | RW | 2 bytes | Unit:0.01A
15008 | Slave09 Outlet Port39 Over Current Critical | RW | 2 bytes | Unit:0.01A
15009 | Slave09 Outlet Port40 Over Current Critical | RW | 2 bytes | Unit:0.01A
15010 | Slave09 Outlet Port41 Over Current Critical | RW | 2 bytes | Unit:0.01A
15011 | Slave09 Outlet Port42 Over Current Critical | RW | 2 bytes | Unit:0.01A
15012 | Slave10 Outlet Port01 Over Current Critical | RW | 2 bytes | Unit:0.01A
15013 | Slave10 Outlet Port02 Over Current Critical | RW | 2 bytes | Unit:0.01A
15014 | Slave10 Outlet Port03 Over Current Critical | RW | 2 bytes | Unit:0.01A
15015 | Slave10 Outlet Port04 Over Current Critical | RW | 2 bytes | Unit:0.01A
15016 | Slave10 Outlet Port05 Over Current Critical | RW | 2 bytes | Unit:0.01A
15017 | Slave10 Outlet Port06 Over Current Critical | RW | 2 bytes | Unit:0.01A
15018 | Slave10 Outlet Port07 Over Current Critical | RW | 2 bytes | Unit:0.01A
15019 | Slave10 Outlet Port08 Over Current Critical | RW | 2 bytes | Unit:0.01A
15020 | Slave10 Outlet Port09 Over Current Critical | RW | 2 bytes | Unit:0.01A
15021 | Slave10 Outlet Port10 Over Current Critical | RW | 2 bytes | Unit:0.01A
15022 | Slave10 Outlet Port11 Over Current Critical | RW | 2 bytes | Unit:0.01A
15023 | Slave10 Outlet Port12 Over Current Critical | RW | 2 bytes | Unit:0.01A
15024 | Slave10 Outlet Port13 Over Current Critical | RW | 2 bytes | Unit:0.01A
15025 | Slave10 Outlet Port14 Over Current Critical | RW | 2 bytes | Unit:0.01A
15026 | Slave10 Outlet Port15 Over Current Critical | RW | 2 bytes | Unit:0.01A
15027 | Slave10 Outlet Port16 Over Current Critical | RW | 2 bytes | Unit:0.01A
15028 | Slave10 Outlet Port17 Over Current Critical | RW | 2 bytes | Unit:0.01A
15029 | Slave10 Outlet Port18 Over Current Critical | RW | 2 bytes | Unit:0.01A
15030 | Slave10 Outlet Port19 Over Current Critical | RW | 2 bytes | Unit:0.01A
15031 | Slave10 Outlet Port20 Over Current Critical | RW | 2 bytes | Unit:0.01A
15032 | Slave10 Outlet Port21 Over Current Critical | RW | 2 bytes | Unit:0.01A
15033 | Slave10 Outlet Port22 Over Current Critical | RW | 2 bytes | Unit:0.01A
15034 | Slave10 Outlet Port23 Over Current Critical | RW | 2 bytes | Unit:0.01A
15035 | Slave10 Outlet Port24 Over Current Critical | RW | 2 bytes | Unit:0.01A
15036 | Slave10 Outlet Port25 Over Current Critical | RW | 2 bytes | Unit:0.01A
15037 | Slave10 Outlet Port26 Over Current Critical | RW | 2 bytes | Unit:0.01A
15038 | Slave10 Outlet Port27 Over Current Critical | RW | 2 bytes | Unit:0.01A
15039 | Slave10 Outlet Port28 Over Current Critical | RW | 2 bytes | Unit:0.01A
15040 | Slave10 Outlet Port29 Over Current Critical | RW | 2 bytes | Unit:0.01A
15041 | Slave10 Outlet Port30 Over Current Critical | RW | 2 bytes | Unit:0.01A
15042 | Slave10 Outlet Port31 Over Current Critical | RW | 2 bytes | Unit:0.01A
15043 | Slave10 Outlet Port32 Over Current Critical | RW | 2 bytes | Unit:0.01A
15044 | Slave10 Outlet Port33 Over Current Critical | RW | 2 bytes | Unit:0.01A
15045 | Slave10 Outlet Port34 Over Current Critical | RW | 2 bytes | Unit:0.01A
15046 | Slave10 Outlet Port35 Over Current Critical | RW | 2 bytes | Unit:0.01A
15047 | Slave10 Outlet Port36 Over Current Critical | RW | 2 bytes | Unit:0.01A
15048 | Slave10 Outlet Port37 Over Current Critical | RW | 2 bytes | Unit:0.01A
15049 | Slave10 Outlet Port38 Over Current Critical | RW | 2 bytes | Unit:0.01A
15050 | Slave10 Outlet Port39 Over Current Critical | RW | 2 bytes | Unit:0.01A
15051 | Slave10 Outlet Port40 Over Current Critical | RW | 2 bytes | Unit:0.01A
15052 | Slave10 Outlet Port41 Over Current Critical | RW | 2 bytes | Unit:0.01A
15053 | Slave10 Outlet Port42 Over Current Critical | RW | 2 bytes | Unit:0.01A
15054 | Slave11 Outlet Port01 Over Current Critical | RW | 2 bytes | Unit:0.01A
15055 | Slave11 Outlet Port02 Over Current Critical | RW | 2 bytes | Unit:0.01A
15056 | Slave11 Outlet Port03 Over Current Critical | RW | 2 bytes | Unit:0.01A
15057 | Slave11 Outlet Port04 Over Current Critical | RW | 2 bytes | Unit:0.01A
15058 | Slave11 Outlet Port05 Over Current Critical | RW | 2 bytes | Unit:0.01A
15059 | Slave11 Outlet Port06 Over Current Critical | RW | 2 bytes | Unit:0.01A
15060 | Slave11 Outlet Port07 Over Current Critical | RW | 2 bytes | Unit:0.01A
15061 | Slave11 Outlet Port08 Over Current Critical | RW | 2 bytes | Unit:0.01A
15062 | Slave11 Outlet Port09 Over Current Critical | RW | 2 bytes | Unit:0.01A
15063 | Slave11 Outlet Port10 Over Current Critical | RW | 2 bytes | Unit:0.01A
15064 | Slave11 Outlet Port11 Over Current Critical | RW | 2 bytes | Unit:0.01A
15065 | Slave11 Outlet Port12 Over Current Critical | RW | 2 bytes | Unit:0.01A
15066 | Slave11 Outlet Port13 Over Current Critical | RW | 2 bytes | Unit:0.01A
15067 | Slave11 Outlet Port14 Over Current Critical | RW | 2 bytes | Unit:0.01A
15068 | Slave11 Outlet Port15 Over Current Critical | RW | 2 bytes | Unit:0.01A
15069 | Slave11 Outlet Port16 Over Current Critical | RW | 2 bytes | Unit:0.01A
15070 | Slave11 Outlet Port17 Over Current Critical | RW | 2 bytes | Unit:0.01A
15071 | Slave11 Outlet Port18 Over Current Critical | RW | 2 bytes | Unit:0.01A
15072 | Slave11 Outlet Port19 Over Current Critical | RW | 2 bytes | Unit:0.01A
15073 | Slave11 Outlet Port20 Over Current Critical | RW | 2 bytes | Unit:0.01A
15074 | Slave11 Outlet Port21 Over Current Critical | RW | 2 bytes | Unit:0.01A
15075 | Slave11 Outlet Port22 Over Current Critical | RW | 2 bytes | Unit:0.01A
15076 | Slave11 Outlet Port23 Over Current Critical | RW | 2 bytes | Unit:0.01A
15077 | Slave11 Outlet Port24 Over Current Critical | RW | 2 bytes | Unit:0.01A
15078 | Slave11 Outlet Port25 Over Current Critical | RW | 2 bytes | Unit:0.01A
15079 | Slave11 Outlet Port26 Over Current Critical | RW | 2 bytes | Unit:0.01A
15080 | Slave11 Outlet Port27 Over Current Critical | RW | 2 bytes | Unit:0.01A
15081 | Slave11 Outlet Port28 Over Current Critical | RW | 2 bytes | Unit:0.01A
15082 | Slave11 Outlet Port29 Over Current Critical | RW | 2 bytes | Unit:0.01A
15083 | Slave11 Outlet Port30 Over Current Critical | RW | 2 bytes | Unit:0.01A
15084 | Slave11 Outlet Port31 Over Current Critical | RW | 2 bytes | Unit:0.01A
15085 | Slave11 Outlet Port32 Over Current Critical | RW | 2 bytes | Unit:0.01A
15086 | Slave11 Outlet Port33 Over Current Critical | RW | 2 bytes | Unit:0.01A
15087 | Slave11 Outlet Port34 Over Current Critical | RW | 2 bytes | Unit:0.01A
15088 | Slave11 Outlet Port35 Over Current Critical | RW | 2 bytes | Unit:0.01A
15089 | Slave11 Outlet Port36 Over Current Critical | RW | 2 bytes | Unit:0.01A
15090 | Slave11 Outlet Port37 Over Current Critical | RW | 2 bytes | Unit:0.01A
15091 | Slave11 Outlet Port38 Over Current Critical | RW | 2 bytes | Unit:0.01A
15092 | Slave11 Outlet Port39 Over Current Critical | RW | 2 bytes | Unit:0.01A
15093 | Slave11 Outlet Port40 Over Current Critical | RW | 2 bytes | Unit:0.01A
15094 | Slave11 Outlet Port41 Over Current Critical | RW | 2 bytes | Unit:0.01A
15095 | Slave11 Outlet Port42 Over Current Critical | RW | 2 bytes | Unit:0.01A
15096 | Slave12 Outlet Port01 Over Current Critical | RW | 2 bytes | Unit:0.01A
15097 | Slave12 Outlet Port02 Over Current Critical | RW | 2 bytes | Unit:0.01A
15098 | Slave12 Outlet Port03 Over Current Critical | RW | 2 bytes | Unit:0.01A
15099 | Slave12 Outlet Port04 Over Current Critical | RW | 2 bytes | Unit:0.01A
15100 | Slave12 Outlet Port05 Over Current Critical | RW | 2 bytes | Unit:0.01A
15101 | Slave12 Outlet Port06 Over Current Critical | RW | 2 bytes | Unit:0.01A
15102 | Slave12 Outlet Port07 Over Current Critical | RW | 2 bytes | Unit:0.01A
15103 | Slave12 Outlet Port08 Over Current Critical | RW | 2 bytes | Unit:0.01A
15104 | Slave12 Outlet Port09 Over Current Critical | RW | 2 bytes | Unit:0.01A
15105 | Slave12 Outlet Port10 Over Current Critical | RW | 2 bytes | Unit:0.01A
15106 | Slave12 Outlet Port11 Over Current Critical | RW | 2 bytes | Unit:0.01A
15107 | Slave12 Outlet Port12 Over Current Critical | RW | 2 bytes | Unit:0.01A
15108 | Slave12 Outlet Port13 Over Current Critical | RW | 2 bytes | Unit:0.01A
15109 | Slave12 Outlet Port14 Over Current Critical | RW | 2 bytes | Unit:0.01A
15110 | Slave12 Outlet Port15 Over Current Critical | RW | 2 bytes | Unit:0.01A
15111 | Slave12 Outlet Port16 Over Current Critical | RW | 2 bytes | Unit:0.01A
15112 | Slave12 Outlet Port17 Over Current Critical | RW | 2 bytes | Unit:0.01A
15113 | Slave12 Outlet Port18 Over Current Critical | RW | 2 bytes | Unit:0.01A
15114 | Slave12 Outlet Port19 Over Current Critical | RW | 2 bytes | Unit:0.01A
15115 | Slave12 Outlet Port20 Over Current Critical | RW | 2 bytes | Unit:0.01A
15116 | Slave12 Outlet Port21 Over Current Critical | RW | 2 bytes | Unit:0.01A
15117 | Slave12 Outlet Port22 Over Current Critical | RW | 2 bytes | Unit:0.01A
15118 | Slave12 Outlet Port23 Over Current Critical | RW | 2 bytes | Unit:0.01A
15119 | Slave12 Outlet Port24 Over Current Critical | RW | 2 bytes | Unit:0.01A
15120 | Slave12 Outlet Port25 Over Current Critical | RW | 2 bytes | Unit:0.01A
15121 | Slave12 Outlet Port26 Over Current Critical | RW | 2 bytes | Unit:0.01A
15122 | Slave12 Outlet Port27 Over Current Critical | RW | 2 bytes | Unit:0.01A
15123 | Slave12 Outlet Port28 Over Current Critical | RW | 2 bytes | Unit:0.01A
15124 | Slave12 Outlet Port29 Over Current Critical | RW | 2 bytes | Unit:0.01A
15125 | Slave12 Outlet Port30 Over Current Critical | RW | 2 bytes | Unit:0.01A
15126 | Slave12 Outlet Port31 Over Current Critical | RW | 2 bytes | Unit:0.01A
15127 | Slave12 Outlet Port32 Over Current Critical | RW | 2 bytes | Unit:0.01A
15128 | Slave12 Outlet Port33 Over Current Critical | RW | 2 bytes | Unit:0.01A
15129 | Slave12 Outlet Port34 Over Current Critical | RW | 2 bytes | Unit:0.01A
15130 | Slave12 Outlet Port35 Over Current Critical | RW | 2 bytes | Unit:0.01A
15131 | Slave12 Outlet Port36 Over Current Critical | RW | 2 bytes | Unit:0.01A
15132 | Slave12 Outlet Port37 Over Current Critical | RW | 2 bytes | Unit:0.01A
15133 | Slave12 Outlet Port38 Over Current Critical | RW | 2 bytes | Unit:0.01A
15134 | Slave12 Outlet Port39 Over Current Critical | RW | 2 bytes | Unit:0.01A
15135 | Slave12 Outlet Port40 Over Current Critical | RW | 2 bytes | Unit:0.01A
15136 | Slave12 Outlet Port41 Over Current Critical | RW | 2 bytes | Unit:0.01A
15137 | Slave12 Outlet Port42 Over Current Critical | RW | 2 bytes | Unit:0.01A
15138 | Slave13 Outlet Port01 Over Current Critical | RW | 2 bytes | Unit:0.01A
15139 | Slave13 Outlet Port02 Over Current Critical | RW | 2 bytes | Unit:0.01A
15140 | Slave13 Outlet Port03 Over Current Critical | RW | 2 bytes | Unit:0.01A
15141 | Slave13 Outlet Port04 Over Current Critical | RW | 2 bytes | Unit:0.01A
15142 | Slave13 Outlet Port05 Over Current Critical | RW | 2 bytes | Unit:0.01A
15143 | Slave13 Outlet Port06 Over Current Critical | RW | 2 bytes | Unit:0.01A
15144 | Slave13 Outlet Port07 Over Current Critical | RW | 2 bytes | Unit:0.01A
15145 | Slave13 Outlet Port08 Over Current Critical | RW | 2 bytes | Unit:0.01A
15146 | Slave13 Outlet Port09 Over Current Critical | RW | 2 bytes | Unit:0.01A
15147 | Slave13 Outlet Port10 Over Current Critical | RW | 2 bytes | Unit:0.01A
15148 | Slave13 Outlet Port11 Over Current Critical | RW | 2 bytes | Unit:0.01A
15149 | Slave13 Outlet Port12 Over Current Critical | RW | 2 bytes | Unit:0.01A
15150 | Slave13 Outlet Port13 Over Current Critical | RW | 2 bytes | Unit:0.01A
15151 | Slave13 Outlet Port14 Over Current Critical | RW | 2 bytes | Unit:0.01A
15152 | Slave13 Outlet Port15 Over Current Critical | RW | 2 bytes | Unit:0.01A
15153 | Slave13 Outlet Port16 Over Current Critical | RW | 2 bytes | Unit:0.01A
15154 | Slave13 Outlet Port17 Over Current Critical | RW | 2 bytes | Unit:0.01A
15155 | Slave13 Outlet Port18 Over Current Critical | RW | 2 bytes | Unit:0.01A
15156 | Slave13 Outlet Port19 Over Current Critical | RW | 2 bytes | Unit:0.01A
15157 | Slave13 Outlet Port20 Over Current Critical | RW | 2 bytes | Unit:0.01A
15158 | Slave13 Outlet Port21 Over Current Critical | RW | 2 bytes | Unit:0.01A
15159 | Slave13 Outlet Port22 Over Current Critical | RW | 2 bytes | Unit:0.01A
15160 | Slave13 Outlet Port23 Over Current Critical | RW | 2 bytes | Unit:0.01A
15161 | Slave13 Outlet Port24 Over Current Critical | RW | 2 bytes | Unit:0.01A
15162 | Slave13 Outlet Port25 Over Current Critical | RW | 2 bytes | Unit:0.01A
15163 | Slave13 Outlet Port26 Over Current Critical | RW | 2 bytes | Unit:0.01A
15164 | Slave13 Outlet Port27 Over Current Critical | RW | 2 bytes | Unit:0.01A
15165 | Slave13 Outlet Port28 Over Current Critical | RW | 2 bytes | Unit:0.01A
15166 | Slave13 Outlet Port29 Over Current Critical | RW | 2 bytes | Unit:0.01A
15167 | Slave13 Outlet Port30 Over Current Critical | RW | 2 bytes | Unit:0.01A
15168 | Slave13 Outlet Port31 Over Current Critical | RW | 2 bytes | Unit:0.01A
15169 | Slave13 Outlet Port32 Over Current Critical | RW | 2 bytes | Unit:0.01A
15170 | Slave13 Outlet Port33 Over Current Critical | RW | 2 bytes | Unit:0.01A
15171 | Slave13 Outlet Port34 Over Current Critical | RW | 2 bytes | Unit:0.01A
15172 | Slave13 Outlet Port35 Over Current Critical | RW | 2 bytes | Unit:0.01A
15173 | Slave13 Outlet Port36 Over Current Critical | RW | 2 bytes | Unit:0.01A
15174 | Slave13 Outlet Port37 Over Current Critical | RW | 2 bytes | Unit:0.01A
15175 | Slave13 Outlet Port38 Over Current Critical | RW | 2 bytes | Unit:0.01A
15176 | Slave13 Outlet Port39 Over Current Critical | RW | 2 bytes | Unit:0.01A
15177 | Slave13 Outlet Port40 Over Current Critical | RW | 2 bytes | Unit:0.01A
15178 | Slave13 Outlet Port41 Over Current Critical | RW | 2 bytes | Unit:0.01A
15179 | Slave13 Outlet Port42 Over Current Critical | RW | 2 bytes | Unit:0.01A
15180 | Slave14 Outlet Port01 Over Current Critical | RW | 2 bytes | Unit:0.01A
15181 | Slave14 Outlet Port02 Over Current Critical | RW | 2 bytes | Unit:0.01A
15182 | Slave14 Outlet Port03 Over Current Critical | RW | 2 bytes | Unit:0.01A
15183 | Slave14 Outlet Port04 Over Current Critical | RW | 2 bytes | Unit:0.01A
15184 | Slave14 Outlet Port05 Over Current Critical | RW | 2 bytes | Unit:0.01A
15185 | Slave14 Outlet Port06 Over Current Critical | RW | 2 bytes | Unit:0.01A
15186 | Slave14 Outlet Port07 Over Current Critical | RW | 2 bytes | Unit:0.01A
15187 | Slave14 Outlet Port08 Over Current Critical | RW | 2 bytes | Unit:0.01A
15188 | Slave14 Outlet Port09 Over Current Critical | RW | 2 bytes | Unit:0.01A
15189 | Slave14 Outlet Port10 Over Current Critical | RW | 2 bytes | Unit:0.01A
15190 | Slave14 Outlet Port11 Over Current Critical | RW | 2 bytes | Unit:0.01A
15191 | Slave14 Outlet Port12 Over Current Critical | RW | 2 bytes | Unit:0.01A
15192 | Slave14 Outlet Port13 Over Current Critical | RW | 2 bytes | Unit:0.01A
15193 | Slave14 Outlet Port14 Over Current Critical | RW | 2 bytes | Unit:0.01A
15194 | Slave14 Outlet Port15 Over Current Critical | RW | 2 bytes | Unit:0.01A
15195 | Slave14 Outlet Port16 Over Current Critical | RW | 2 bytes | Unit:0.01A
15196 | Slave14 Outlet Port17 Over Current Critical | RW | 2 bytes | Unit:0.01A
15197 | Slave14 Outlet Port18 Over Current Critical | RW | 2 bytes | Unit:0.01A
15198 | Slave14 Outlet Port19 Over Current Critical | RW | 2 bytes | Unit:0.01A
15199 | Slave14 Outlet Port20 Over Current Critical | RW | 2 bytes | Unit:0.01A
15200 | Slave14 Outlet Port21 Over Current Critical | RW | 2 bytes | Unit:0.01A
15201 | Slave14 Outlet Port22 Over Current Critical | RW | 2 bytes | Unit:0.01A
15202 | Slave14 Outlet Port23 Over Current Critical | RW | 2 bytes | Unit:0.01A
15203 | Slave14 Outlet Port24 Over Current Critical | RW | 2 bytes | Unit:0.01A
15204 | Slave14 Outlet Port25 Over Current Critical | RW | 2 bytes | Unit:0.01A
15205 | Slave14 Outlet Port26 Over Current Critical | RW | 2 bytes | Unit:0.01A
15206 | Slave14 Outlet Port27 Over Current Critical | RW | 2 bytes | Unit:0.01A
15207 | Slave14 Outlet Port28 Over Current Critical | RW | 2 bytes | Unit:0.01A
15208 | Slave14 Outlet Port29 Over Current Critical | RW | 2 bytes | Unit:0.01A
15209 | Slave14 Outlet Port30 Over Current Critical | RW | 2 bytes | Unit:0.01A
15210 | Slave14 Outlet Port31 Over Current Critical | RW | 2 bytes | Unit:0.01A
15211 | Slave14 Outlet Port32 Over Current Critical | RW | 2 bytes | Unit:0.01A
15212 | Slave14 Outlet Port33 Over Current Critical | RW | 2 bytes | Unit:0.01A
15213 | Slave14 Outlet Port34 Over Current Critical | RW | 2 bytes | Unit:0.01A
15214 | Slave14 Outlet Port35 Over Current Critical | RW | 2 bytes | Unit:0.01A
15215 | Slave14 Outlet Port36 Over Current Critical | RW | 2 bytes | Unit:0.01A
15216 | Slave14 Outlet Port37 Over Current Critical | RW | 2 bytes | Unit:0.01A
15217 | Slave14 Outlet Port38 Over Current Critical | RW | 2 bytes | Unit:0.01A
15218 | Slave14 Outlet Port39 Over Current Critical | RW | 2 bytes | Unit:0.01A
15219 | Slave14 Outlet Port40 Over Current Critical | RW | 2 bytes | Unit:0.01A
15220 | Slave14 Outlet Port41 Over Current Critical | RW | 2 bytes | Unit:0.01A
15221 | Slave14 Outlet Port42 Over Current Critical | RW | 2 bytes | Unit:0.01A
15222 | Slave15 Outlet Port01 Over Current Critical | RW | 2 bytes | Unit:0.01A
15223 | Slave15 Outlet Port02 Over Current Critical | RW | 2 bytes | Unit:0.01A
15224 | Slave15 Outlet Port03 Over Current Critical | RW | 2 bytes | Unit:0.01A
15225 | Slave15 Outlet Port04 Over Current Critical | RW | 2 bytes | Unit:0.01A
15226 | Slave15 Outlet Port05 Over Current Critical | RW | 2 bytes | Unit:0.01A
15227 | Slave15 Outlet Port06 Over Current Critical | RW | 2 bytes | Unit:0.01A
15228 | Slave15 Outlet Port07 Over Current Critical | RW | 2 bytes | Unit:0.01A
15229 | Slave15 Outlet Port08 Over Current Critical | RW | 2 bytes | Unit:0.01A
15230 | Slave15 Outlet Port09 Over Current Critical | RW | 2 bytes | Unit:0.01A
15231 | Slave15 Outlet Port10 Over Current Critical | RW | 2 bytes | Unit:0.01A
15232 | Slave15 Outlet Port11 Over Current Critical | RW | 2 bytes | Unit:0.01A
15233 | Slave15 Outlet Port12 Over Current Critical | RW | 2 bytes | Unit:0.01A
15234 | Slave15 Outlet Port13 Over Current Critical | RW | 2 bytes | Unit:0.01A
15235 | Slave15 Outlet Port14 Over Current Critical | RW | 2 bytes | Unit:0.01A
15236 | Slave15 Outlet Port15 Over Current Critical | RW | 2 bytes | Unit:0.01A
15237 | Slave15 Outlet Port16 Over Current Critical | RW | 2 bytes | Unit:0.01A
15238 | Slave15 Outlet Port17 Over Current Critical | RW | 2 bytes | Unit:0.01A
15239 | Slave15 Outlet Port18 Over Current Critical | RW | 2 bytes | Unit:0.01A
15240 | Slave15 Outlet Port19 Over Current Critical | RW | 2 bytes | Unit:0.01A
15241 | Slave15 Outlet Port20 Over Current Critical | RW | 2 bytes | Unit:0.01A
15242 | Slave15 Outlet Port21 Over Current Critical | RW | 2 bytes | Unit:0.01A
15243 | Slave15 Outlet Port22 Over Current Critical | RW | 2 bytes | Unit:0.01A
15244 | Slave15 Outlet Port23 Over Current Critical | RW | 2 bytes | Unit:0.01A
15245 | Slave15 Outlet Port24 Over Current Critical | RW | 2 bytes | Unit:0.01A
15246 | Slave15 Outlet Port25 Over Current Critical | RW | 2 bytes | Unit:0.01A
15247 | Slave15 Outlet Port26 Over Current Critical | RW | 2 bytes | Unit:0.01A
15248 | Slave15 Outlet Port27 Over Current Critical | RW | 2 bytes | Unit:0.01A
15249 | Slave15 Outlet Port28 Over Current Critical | RW | 2 bytes | Unit:0.01A
15250 | Slave15 Outlet Port29 Over Current Critical | RW | 2 bytes | Unit:0.01A
15251 | Slave15 Outlet Port30 Over Current Critical | RW | 2 bytes | Unit:0.01A
15252 | Slave15 Outlet Port31 Over Current Critical | RW | 2 bytes | Unit:0.01A
15253 | Slave15 Outlet Port32 Over Current Critical | RW | 2 bytes | Unit:0.01A
15254 | Slave15 Outlet Port33 Over Current Critical | RW | 2 bytes | Unit:0.01A
15255 | Slave15 Outlet Port34 Over Current Critical | RW | 2 bytes | Unit:0.01A
15256 | Slave15 Outlet Port35 Over Current Critical | RW | 2 bytes | Unit:0.01A
15257 | Slave15 Outlet Port36 Over Current Critical | RW | 2 bytes | Unit:0.01A
15258 | Slave15 Outlet Port37 Over Current Critical | RW | 2 bytes | Unit:0.01A
15259 | Slave15 Outlet Port38 Over Current Critical | RW | 2 bytes | Unit:0.01A
15260 | Slave15 Outlet Port39 Over Current Critical | RW | 2 bytes | Unit:0.01A
15261 | Slave15 Outlet Port40 Over Current Critical | RW | 2 bytes | Unit:0.01A
15262 | Slave15 Outlet Port41 Over Current Critical | RW | 2 bytes | Unit:0.01A
15263 | Slave15 Outlet Port42 Over Current Critical | RW | 2 bytes | Unit:0.01A
15264 | Master Outlet Port01 Over Power Warning | RW | 2 bytes | Unit:1
15265 | Master Outlet Port02 Over Power Warning | RW | 2 bytes | Unit:1
15266 | Master Outlet Port03 Over Power Warning | RW | 2 bytes | Unit:1
15267 | Master Outlet Port04 Over Power Warning | RW | 2 bytes | Unit:1
15268 | Master Outlet Port05 Over Power Warning | RW | 2 bytes | Unit:1
15269 | Master Outlet Port06 Over Power Warning | RW | 2 bytes | Unit:1
15270 | Master Outlet Port07 Over Power Warning | RW | 2 bytes | Unit:1
15271 | Master Outlet Port08 Over Power Warning | RW | 2 bytes | Unit:1
15272 | Master Outlet Port09 Over Power Warning | RW | 2 bytes | Unit:1
15273 | Master Outlet Port10 Over Power Warning | RW | 2 bytes | Unit:1
15274 | Master Outlet Port11 Over Power Warning | RW | 2 bytes | Unit:1
15275 | Master Outlet Port12 Over Power Warning | RW | 2 bytes | Unit:1
15276 | Master Outlet Port13 Over Power Warning | RW | 2 bytes | Unit:1
15277 | Master Outlet Port14 Over Power Warning | RW | 2 bytes | Unit:1
15278 | Master Outlet Port15 Over Power Warning | RW | 2 bytes | Unit:1
15279 | Master Outlet Port16 Over Power Warning | RW | 2 bytes | Unit:1
15280 | Master Outlet Port17 Over Power Warning | RW | 2 bytes | Unit:1
15281 | Master Outlet Port18 Over Power Warning | RW | 2 bytes | Unit:1
15282 | Master Outlet Port19 Over Power Warning | RW | 2 bytes | Unit:1
15283 | Master Outlet Port20 Over Power Warning | RW | 2 bytes | Unit:1
15284 | Master Outlet Port21 Over Power Warning | RW | 2 bytes | Unit:1
15285 | Master Outlet Port22 Over Power Warning | RW | 2 bytes | Unit:1
15286 | Master Outlet Port23 Over Power Warning | RW | 2 bytes | Unit:1
15287 | Master Outlet Port24 Over Power Warning | RW | 2 bytes | Unit:1
15288 | Master Outlet Port25 Over Power Warning | RW | 2 bytes | Unit:1
15289 | Master Outlet Port26 Over Power Warning | RW | 2 bytes | Unit:1
15290 | Master Outlet Port27 Over Power Warning | RW | 2 bytes | Unit:1
15291 | Master Outlet Port28 Over Power Warning | RW | 2 bytes | Unit:1
15292 | Master Outlet Port29 Over Power Warning | RW | 2 bytes | Unit:1
15293 | Master Outlet Port30 Over Power Warning | RW | 2 bytes | Unit:1
15294 | Master Outlet Port31 Over Power Warning | RW | 2 bytes | Unit:1
15295 | Master Outlet Port32 Over Power Warning | RW | 2 bytes | Unit:1
15296 | Master Outlet Port33 Over Power Warning | RW | 2 bytes | Unit:1
15297 | Master Outlet Port34 Over Power Warning | RW | 2 bytes | Unit:1
15298 | Master Outlet Port35 Over Power Warning | RW | 2 bytes | Unit:1
15299 | Master Outlet Port36 Over Power Warning | RW | 2 bytes | Unit:1
15300 | Master Outlet Port37 Over Power Warning | RW | 2 bytes | Unit:1
15301 | Master Outlet Port38 Over Power Warning | RW | 2 bytes | Unit:1
15302 | Master Outlet Port39 Over Power Warning | RW | 2 bytes | Unit:1
15303 | Master Outlet Port40 Over Power Warning | RW | 2 bytes | Unit:1
15304 | Master Outlet Port41 Over Power Warning | RW | 2 bytes | Unit:1
15305 | Master Outlet Port42 Over Power Warning | RW | 2 bytes | Unit:1
15306 | Slave01 Outlet Port01 Over Power Warning | RW | 2 bytes | Unit:1
15307 | Slave01 Outlet Port02 Over Power Warning | RW | 2 bytes | Unit:1
15308 | Slave01 Outlet Port03 Over Power Warning | RW | 2 bytes | Unit:1
15309 | Slave01 Outlet Port04 Over Power Warning | RW | 2 bytes | Unit:1
15310 | Slave01 Outlet Port05 Over Power Warning | RW | 2 bytes | Unit:1
15311 | Slave01 Outlet Port06 Over Power Warning | RW | 2 bytes | Unit:1
15312 | Slave01 Outlet Port07 Over Power Warning | RW | 2 bytes | Unit:1
15313 | Slave01 Outlet Port08 Over Power Warning | RW | 2 bytes | Unit:1
15314 | Slave01 Outlet Port09 Over Power Warning | RW | 2 bytes | Unit:1
15315 | Slave01 Outlet Port10 Over Power Warning | RW | 2 bytes | Unit:1
15316 | Slave01 Outlet Port11 Over Power Warning | RW | 2 bytes | Unit:1
15317 | Slave01 Outlet Port12 Over Power Warning | RW | 2 bytes | Unit:1
15318 | Slave01 Outlet Port13 Over Power Warning | RW | 2 bytes | Unit:1
15319 | Slave01 Outlet Port14 Over Power Warning | RW | 2 bytes | Unit:1
15320 | Slave01 Outlet Port15 Over Power Warning | RW | 2 bytes | Unit:1
15321 | Slave01 Outlet Port16 Over Power Warning | RW | 2 bytes | Unit:1
15322 | Slave01 Outlet Port17 Over Power Warning | RW | 2 bytes | Unit:1
15323 | Slave01 Outlet Port18 Over Power Warning | RW | 2 bytes | Unit:1
15324 | Slave01 Outlet Port19 Over Power Warning | RW | 2 bytes | Unit:1
15325 | Slave01 Outlet Port20 Over Power Warning | RW | 2 bytes | Unit:1
15326 | Slave01 Outlet Port21 Over Power Warning | RW | 2 bytes | Unit:1
15327 | Slave01 Outlet Port22 Over Power Warning | RW | 2 bytes | Unit:1
15328 | Slave01 Outlet Port23 Over Power Warning | RW | 2 bytes | Unit:1
15329 | Slave01 Outlet Port24 Over Power Warning | RW | 2 bytes | Unit:1
15330 | Slave01 Outlet Port25 Over Power Warning | RW | 2 bytes | Unit:1
15331 | Slave01 Outlet Port26 Over Power Warning | RW | 2 bytes | Unit:1
15332 | Slave01 Outlet Port27 Over Power Warning | RW | 2 bytes | Unit:1
15333 | Slave01 Outlet Port28 Over Power Warning | RW | 2 bytes | Unit:1
15334 | Slave01 Outlet Port29 Over Power Warning | RW | 2 bytes | Unit:1
15335 | Slave01 Outlet Port30 Over Power Warning | RW | 2 bytes | Unit:1
15336 | Slave01 Outlet Port31 Over Power Warning | RW | 2 bytes | Unit:1
15337 | Slave01 Outlet Port32 Over Power Warning | RW | 2 bytes | Unit:1
15338 | Slave01 Outlet Port33 Over Power Warning | RW | 2 bytes | Unit:1
15339 | Slave01 Outlet Port34 Over Power Warning | RW | 2 bytes | Unit:1
15340 | Slave01 Outlet Port35 Over Power Warning | RW | 2 bytes | Unit:1
15341 | Slave01 Outlet Port36 Over Power Warning | RW | 2 bytes | Unit:1
15342 | Slave01 Outlet Port37 Over Power Warning | RW | 2 bytes | Unit:1
15343 | Slave01 Outlet Port38 Over Power Warning | RW | 2 bytes | Unit:1
15344 | Slave01 Outlet Port39 Over Power Warning | RW | 2 bytes | Unit:1
15345 | Slave01 Outlet Port40 Over Power Warning | RW | 2 bytes | Unit:1
15346 | Slave01 Outlet Port41 Over Power Warning | RW | 2 bytes | Unit:1
15347 | Slave01 Outlet Port42 Over Power Warning | RW | 2 bytes | Unit:1
15348 | Slave02 Outlet Port01 Over Power Warning | RW | 2 bytes | Unit:1
15349 | Slave02 Outlet Port02 Over Power Warning | RW | 2 bytes | Unit:1
15350 | Slave02 Outlet Port03 Over Power Warning | RW | 2 bytes | Unit:1
15351 | Slave02 Outlet Port04 Over Power Warning | RW | 2 bytes | Unit:1
15352 | Slave02 Outlet Port05 Over Power Warning | RW | 2 bytes | Unit:1
15353 | Slave02 Outlet Port06 Over Power Warning | RW | 2 bytes | Unit:1
15354 | Slave02 Outlet Port07 Over Power Warning | RW | 2 bytes | Unit:1
15355 | Slave02 Outlet Port08 Over Power Warning | RW | 2 bytes | Unit:1
15356 | Slave02 Outlet Port09 Over Power Warning | RW | 2 bytes | Unit:1
15357 | Slave02 Outlet Port10 Over Power Warning | RW | 2 bytes | Unit:1
15358 | Slave02 Outlet Port11 Over Power Warning | RW | 2 bytes | Unit:1
15359 | Slave02 Outlet Port12 Over Power Warning | RW | 2 bytes | Unit:1
15360 | Slave02 Outlet Port13 Over Power Warning | RW | 2 bytes | Unit:1
15361 | Slave02 Outlet Port14 Over Power Warning | RW | 2 bytes | Unit:1
15362 | Slave02 Outlet Port15 Over Power Warning | RW | 2 bytes | Unit:1
15363 | Slave02 Outlet Port16 Over Power Warning | RW | 2 bytes | Unit:1
15364 | Slave02 Outlet Port17 Over Power Warning | RW | 2 bytes | Unit:1
15365 | Slave02 Outlet Port18 Over Power Warning | RW | 2 bytes | Unit:1
15366 | Slave02 Outlet Port19 Over Power Warning | RW | 2 bytes | Unit:1
15367 | Slave02 Outlet Port20 Over Power Warning | RW | 2 bytes | Unit:1
15368 | Slave02 Outlet Port21 Over Power Warning | RW | 2 bytes | Unit:1
15369 | Slave02 Outlet Port22 Over Power Warning | RW | 2 bytes | Unit:1
15370 | Slave02 Outlet Port23 Over Power Warning | RW | 2 bytes | Unit:1
15371 | Slave02 Outlet Port24 Over Power Warning | RW | 2 bytes | Unit:1
15372 | Slave02 Outlet Port25 Over Power Warning | RW | 2 bytes | Unit:1
15373 | Slave02 Outlet Port26 Over Power Warning | RW | 2 bytes | Unit:1
15374 | Slave02 Outlet Port27 Over Power Warning | RW | 2 bytes | Unit:1
15375 | Slave02 Outlet Port28 Over Power Warning | RW | 2 bytes | Unit:1
15376 | Slave02 Outlet Port29 Over Power Warning | RW | 2 bytes | Unit:1
15377 | Slave02 Outlet Port30 Over Power Warning | RW | 2 bytes | Unit:1
15378 | Slave02 Outlet Port31 Over Power Warning | RW | 2 bytes | Unit:1
15379 | Slave02 Outlet Port32 Over Power Warning | RW | 2 bytes | Unit:1
15380 | Slave02 Outlet Port33 Over Power Warning | RW | 2 bytes | Unit:1
15381 | Slave02 Outlet Port34 Over Power Warning | RW | 2 bytes | Unit:1
15382 | Slave02 Outlet Port35 Over Power Warning | RW | 2 bytes | Unit:1
15383 | Slave02 Outlet Port36 Over Power Warning | RW | 2 bytes | Unit:1
15384 | Slave02 Outlet Port37 Over Power Warning | RW | 2 bytes | Unit:1
15385 | Slave02 Outlet Port38 Over Power Warning | RW | 2 bytes | Unit:1
15386 | Slave02 Outlet Port39 Over Power Warning | RW | 2 bytes | Unit:1
15387 | Slave02 Outlet Port40 Over Power Warning | RW | 2 bytes | Unit:1
15388 | Slave02 Outlet Port41 Over Power Warning | RW | 2 bytes | Unit:1
15389 | Slave02 Outlet Port42 Over Power Warning | RW | 2 bytes | Unit:1
15390 | Slave03 Outlet Port01 Over Power Warning | RW | 2 bytes | Unit:1
15391 | Slave03 Outlet Port02 Over Power Warning | RW | 2 bytes | Unit:1
15392 | Slave03 Outlet Port03 Over Power Warning | RW | 2 bytes | Unit:1
15393 | Slave03 Outlet Port04 Over Power Warning | RW | 2 bytes | Unit:1
15394 | Slave03 Outlet Port05 Over Power Warning | RW | 2 bytes | Unit:1
15395 | Slave03 Outlet Port06 Over Power Warning | RW | 2 bytes | Unit:1
15396 | Slave03 Outlet Port07 Over Power Warning | RW | 2 bytes | Unit:1
15397 | Slave03 Outlet Port08 Over Power Warning | RW | 2 bytes | Unit:1
15398 | Slave03 Outlet Port09 Over Power Warning | RW | 2 bytes | Unit:1
15399 | Slave03 Outlet Port10 Over Power Warning | RW | 2 bytes | Unit:1
15400 | Slave03 Outlet Port11 Over Power Warning | RW | 2 bytes | Unit:1
15401 | Slave03 Outlet Port12 Over Power Warning | RW | 2 bytes | Unit:1
15402 | Slave03 Outlet Port13 Over Power Warning | RW | 2 bytes | Unit:1
15403 | Slave03 Outlet Port14 Over Power Warning | RW | 2 bytes | Unit:1
15404 | Slave03 Outlet Port15 Over Power Warning | RW | 2 bytes | Unit:1
15405 | Slave03 Outlet Port16 Over Power Warning | RW | 2 bytes | Unit:1
15406 | Slave03 Outlet Port17 Over Power Warning | RW | 2 bytes | Unit:1
15407 | Slave03 Outlet Port18 Over Power Warning | RW | 2 bytes | Unit:1
15408 | Slave03 Outlet Port19 Over Power Warning | RW | 2 bytes | Unit:1
15409 | Slave03 Outlet Port20 Over Power Warning | RW | 2 bytes | Unit:1
15410 | Slave03 Outlet Port21 Over Power Warning | RW | 2 bytes | Unit:1
15411 | Slave03 Outlet Port22 Over Power Warning | RW | 2 bytes | Unit:1
15412 | Slave03 Outlet Port23 Over Power Warning | RW | 2 bytes | Unit:1
15413 | Slave03 Outlet Port24 Over Power Warning | RW | 2 bytes | Unit:1
15414 | Slave03 Outlet Port25 Over Power Warning | RW | 2 bytes | Unit:1
15415 | Slave03 Outlet Port26 Over Power Warning | RW | 2 bytes | Unit:1
15416 | Slave03 Outlet Port27 Over Power Warning | RW | 2 bytes | Unit:1
15417 | Slave03 Outlet Port28 Over Power Warning | RW | 2 bytes | Unit:1
15418 | Slave03 Outlet Port29 Over Power Warning | RW | 2 bytes | Unit:1
15419 | Slave03 Outlet Port30 Over Power Warning | RW | 2 bytes | Unit:1
15420 | Slave03 Outlet Port31 Over Power Warning | RW | 2 bytes | Unit:1
15421 | Slave03 Outlet Port32 Over Power Warning | RW | 2 bytes | Unit:1
15422 | Slave03 Outlet Port33 Over Power Warning | RW | 2 bytes | Unit:1
15423 | Slave03 Outlet Port34 Over Power Warning | RW | 2 bytes | Unit:1
15424 | Slave03 Outlet Port35 Over Power Warning | RW | 2 bytes | Unit:1
15425 | Slave03 Outlet Port36 Over Power Warning | RW | 2 bytes | Unit:1
15426 | Slave03 Outlet Port37 Over Power Warning | RW | 2 bytes | Unit:1
15427 | Slave03 Outlet Port38 Over Power Warning | RW | 2 bytes | Unit:1
15428 | Slave03 Outlet Port39 Over Power Warning | RW | 2 bytes | Unit:1
15429 | Slave03 Outlet Port40 Over Power Warning | RW | 2 bytes | Unit:1
15430 | Slave03 Outlet Port41 Over Power Warning | RW | 2 bytes | Unit:1
15431 | Slave03 Outlet Port42 Over Power Warning | RW | 2 bytes | Unit:1
15432 | Slave04 Outlet Port01 Over Power Warning | RW | 2 bytes | Unit:1
15433 | Slave04 Outlet Port02 Over Power Warning | RW | 2 bytes | Unit:1
15434 | Slave04 Outlet Port03 Over Power Warning | RW | 2 bytes | Unit:1
15435 | Slave04 Outlet Port04 Over Power Warning | RW | 2 bytes | Unit:1
15436 | Slave04 Outlet Port05 Over Power Warning | RW | 2 bytes | Unit:1
15437 | Slave04 Outlet Port06 Over Power Warning | RW | 2 bytes | Unit:1
15438 | Slave04 Outlet Port07 Over Power Warning | RW | 2 bytes | Unit:1
15439 | Slave04 Outlet Port08 Over Power Warning | RW | 2 bytes | Unit:1
15440 | Slave04 Outlet Port09 Over Power Warning | RW | 2 bytes | Unit:1
15441 | Slave04 Outlet Port10 Over Power Warning | RW | 2 bytes | Unit:1
15442 | Slave04 Outlet Port11 Over Power Warning | RW | 2 bytes | Unit:1
15443 | Slave04 Outlet Port12 Over Power Warning | RW | 2 bytes | Unit:1
15444 | Slave04 Outlet Port13 Over Power Warning | RW | 2 bytes | Unit:1
15445 | Slave04 Outlet Port14 Over Power Warning | RW | 2 bytes | Unit:1
15446 | Slave04 Outlet Port15 Over Power Warning | RW | 2 bytes | Unit:1
15447 | Slave04 Outlet Port16 Over Power Warning | RW | 2 bytes | Unit:1
15448 | Slave04 Outlet Port17 Over Power Warning | RW | 2 bytes | Unit:1
15449 | Slave04 Outlet Port18 Over Power Warning | RW | 2 bytes | Unit:1
15450 | Slave04 Outlet Port19 Over Power Warning | RW | 2 bytes | Unit:1
15451 | Slave04 Outlet Port20 Over Power Warning | RW | 2 bytes | Unit:1
15452 | Slave04 Outlet Port21 Over Power Warning | RW | 2 bytes | Unit:1
15453 | Slave04 Outlet Port22 Over Power Warning | RW | 2 bytes | Unit:1
15454 | Slave04 Outlet Port23 Over Power Warning | RW | 2 bytes | Unit:1
15455 | Slave04 Outlet Port24 Over Power Warning | RW | 2 bytes | Unit:1
15456 | Slave04 Outlet Port25 Over Power Warning | RW | 2 bytes | Unit:1
15457 | Slave04 Outlet Port26 Over Power Warning | RW | 2 bytes | Unit:1
15458 | Slave04 Outlet Port27 Over Power Warning | RW | 2 bytes | Unit:1
15459 | Slave04 Outlet Port28 Over Power Warning | RW | 2 bytes | Unit:1
15460 | Slave04 Outlet Port29 Over Power Warning | RW | 2 bytes | Unit:1
15461 | Slave04 Outlet Port30 Over Power Warning | RW | 2 bytes | Unit:1
15462 | Slave04 Outlet Port31 Over Power Warning | RW | 2 bytes | Unit:1
15463 | Slave04 Outlet Port32 Over Power Warning | RW | 2 bytes | Unit:1
15464 | Slave04 Outlet Port33 Over Power Warning | RW | 2 bytes | Unit:1
15465 | Slave04 Outlet Port34 Over Power Warning | RW | 2 bytes | Unit:1
15466 | Slave04 Outlet Port35 Over Power Warning | RW | 2 bytes | Unit:1
15467 | Slave04 Outlet Port36 Over Power Warning | RW | 2 bytes | Unit:1
15468 | Slave04 Outlet Port37 Over Power Warning | RW | 2 bytes | Unit:1
15469 | Slave04 Outlet Port38 Over Power Warning | RW | 2 bytes | Unit:1
15470 | Slave04 Outlet Port39 Over Power Warning | RW | 2 bytes | Unit:1
15471 | Slave04 Outlet Port40 Over Power Warning | RW | 2 bytes | Unit:1
15472 | Slave04 Outlet Port41 Over Power Warning | RW | 2 bytes | Unit:1
15473 | Slave04 Outlet Port42 Over Power Warning | RW | 2 bytes | Unit:1
15474 | Slave05 Outlet Port01 Over Power Warning | RW | 2 bytes | Unit:1
15475 | Slave05 Outlet Port02 Over Power Warning | RW | 2 bytes | Unit:1
15476 | Slave05 Outlet Port03 Over Power Warning | RW | 2 bytes | Unit:1
15477 | Slave05 Outlet Port04 Over Power Warning | RW | 2 bytes | Unit:1
15478 | Slave05 Outlet Port05 Over Power Warning | RW | 2 bytes | Unit:1
15479 | Slave05 Outlet Port06 Over Power Warning | RW | 2 bytes | Unit:1
15480 | Slave05 Outlet Port07 Over Power Warning | RW | 2 bytes | Unit:1
15481 | Slave05 Outlet Port08 Over Power Warning | RW | 2 bytes | Unit:1
15482 | Slave05 Outlet Port09 Over Power Warning | RW | 2 bytes | Unit:1
15483 | Slave05 Outlet Port10 Over Power Warning | RW | 2 bytes | Unit:1
15484 | Slave05 Outlet Port11 Over Power Warning | RW | 2 bytes | Unit:1
15485 | Slave05 Outlet Port12 Over Power Warning | RW | 2 bytes | Unit:1
15486 | Slave05 Outlet Port13 Over Power Warning | RW | 2 bytes | Unit:1
15487 | Slave05 Outlet Port14 Over Power Warning | RW | 2 bytes | Unit:1
15488 | Slave05 Outlet Port15 Over Power Warning | RW | 2 bytes | Unit:1
15489 | Slave05 Outlet Port16 Over Power Warning | RW | 2 bytes | Unit:1
15490 | Slave05 Outlet Port17 Over Power Warning | RW | 2 bytes | Unit:1
15491 | Slave05 Outlet Port18 Over Power Warning | RW | 2 bytes | Unit:1
15492 | Slave05 Outlet Port19 Over Power Warning | RW | 2 bytes | Unit:1
15493 | Slave05 Outlet Port20 Over Power Warning | RW | 2 bytes | Unit:1
15494 | Slave05 Outlet Port21 Over Power Warning | RW | 2 bytes | Unit:1
15495 | Slave05 Outlet Port22 Over Power Warning | RW | 2 bytes | Unit:1
15496 | Slave05 Outlet Port23 Over Power Warning | RW | 2 bytes | Unit:1
15497 | Slave05 Outlet Port24 Over Power Warning | RW | 2 bytes | Unit:1
15498 | Slave05 Outlet Port25 Over Power Warning | RW | 2 bytes | Unit:1
15499 | Slave05 Outlet Port26 Over Power Warning | RW | 2 bytes | Unit:1
15500 | Slave05 Outlet Port27 Over Power Warning | RW | 2 bytes | Unit:1
15501 | Slave05 Outlet Port28 Over Power Warning | RW | 2 bytes | Unit:1
15502 | Slave05 Outlet Port29 Over Power Warning | RW | 2 bytes | Unit:1
15503 | Slave05 Outlet Port30 Over Power Warning | RW | 2 bytes | Unit:1
15504 | Slave05 Outlet Port31 Over Power Warning | RW | 2 bytes | Unit:1
15505 | Slave05 Outlet Port32 Over Power Warning | RW | 2 bytes | Unit:1
15506 | Slave05 Outlet Port33 Over Power Warning | RW | 2 bytes | Unit:1
15507 | Slave05 Outlet Port34 Over Power Warning | RW | 2 bytes | Unit:1
15508 | Slave05 Outlet Port35 Over Power Warning | RW | 2 bytes | Unit:1
15509 | Slave05 Outlet Port36 Over Power Warning | RW | 2 bytes | Unit:1
15510 | Slave05 Outlet Port37 Over Power Warning | RW | 2 bytes | Unit:1
15511 | Slave05 Outlet Port38 Over Power Warning | RW | 2 bytes | Unit:1
15512 | Slave05 Outlet Port39 Over Power Warning | RW | 2 bytes | Unit:1
15513 | Slave05 Outlet Port40 Over Power Warning | RW | 2 bytes | Unit:1
15514 | Slave05 Outlet Port41 Over Power Warning | RW | 2 bytes | Unit:1
15515 | Slave05 Outlet Port42 Over Power Warning | RW | 2 bytes | Unit:1
15516 | Slave06 Outlet Port01 Over Power Warning | RW | 2 bytes | Unit:1
15517 | Slave06 Outlet Port02 Over Power Warning | RW | 2 bytes | Unit:1
15518 | Slave06 Outlet Port03 Over Power Warning | RW | 2 bytes | Unit:1
15519 | Slave06 Outlet Port04 Over Power Warning | RW | 2 bytes | Unit:1
15520 | Slave06 Outlet Port05 Over Power Warning | RW | 2 bytes | Unit:1
15521 | Slave06 Outlet Port06 Over Power Warning | RW | 2 bytes | Unit:1
15522 | Slave06 Outlet Port07 Over Power Warning | RW | 2 bytes | Unit:1
15523 | Slave06 Outlet Port08 Over Power Warning | RW | 2 bytes | Unit:1
15524 | Slave06 Outlet Port09 Over Power Warning | RW | 2 bytes | Unit:1
15525 | Slave06 Outlet Port10 Over Power Warning | RW | 2 bytes | Unit:1
15526 | Slave06 Outlet Port11 Over Power Warning | RW | 2 bytes | Unit:1
15527 | Slave06 Outlet Port12 Over Power Warning | RW | 2 bytes | Unit:1
15528 | Slave06 Outlet Port13 Over Power Warning | RW | 2 bytes | Unit:1
15529 | Slave06 Outlet Port14 Over Power Warning | RW | 2 bytes | Unit:1
15530 | Slave06 Outlet Port15 Over Power Warning | RW | 2 bytes | Unit:1
15531 | Slave06 Outlet Port16 Over Power Warning | RW | 2 bytes | Unit:1
15532 | Slave06 Outlet Port17 Over Power Warning | RW | 2 bytes | Unit:1
15533 | Slave06 Outlet Port18 Over Power Warning | RW | 2 bytes | Unit:1
15534 | Slave06 Outlet Port19 Over Power Warning | RW | 2 bytes | Unit:1
15535 | Slave06 Outlet Port20 Over Power Warning | RW | 2 bytes | Unit:1
15536 | Slave06 Outlet Port21 Over Power Warning | RW | 2 bytes | Unit:1
15537 | Slave06 Outlet Port22 Over Power Warning | RW | 2 bytes | Unit:1
15538 | Slave06 Outlet Port23 Over Power Warning | RW | 2 bytes | Unit:1
15539 | Slave06 Outlet Port24 Over Power Warning | RW | 2 bytes | Unit:1
15540 | Slave06 Outlet Port25 Over Power Warning | RW | 2 bytes | Unit:1
15541 | Slave06 Outlet Port26 Over Power Warning | RW | 2 bytes | Unit:1
15542 | Slave06 Outlet Port27 Over Power Warning | RW | 2 bytes | Unit:1
15543 | Slave06 Outlet Port28 Over Power Warning | RW | 2 bytes | Unit:1
15544 | Slave06 Outlet Port29 Over Power Warning | RW | 2 bytes | Unit:1
15545 | Slave06 Outlet Port30 Over Power Warning | RW | 2 bytes | Unit:1
15546 | Slave06 Outlet Port31 Over Power Warning | RW | 2 bytes | Unit:1
15547 | Slave06 Outlet Port32 Over Power Warning | RW | 2 bytes | Unit:1
15548 | Slave06 Outlet Port33 Over Power Warning | RW | 2 bytes | Unit:1
15549 | Slave06 Outlet Port34 Over Power Warning | RW | 2 bytes | Unit:1
15550 | Slave06 Outlet Port35 Over Power Warning | RW | 2 bytes | Unit:1
15551 | Slave06 Outlet Port36 Over Power Warning | RW | 2 bytes | Unit:1
15552 | Slave06 Outlet Port37 Over Power Warning | RW | 2 bytes | Unit:1
15553 | Slave06 Outlet Port38 Over Power Warning | RW | 2 bytes | Unit:1
15554 | Slave06 Outlet Port39 Over Power Warning | RW | 2 bytes | Unit:1
15555 | Slave06 Outlet Port40 Over Power Warning | RW | 2 bytes | Unit:1
15556 | Slave06 Outlet Port41 Over Power Warning | RW | 2 bytes | Unit:1
15557 | Slave06 Outlet Port42 Over Power Warning | RW | 2 bytes | Unit:1
15558 | Slave07 Outlet Port01 Over Power Warning | RW | 2 bytes | Unit:1
15559 | Slave07 Outlet Port02 Over Power Warning | RW | 2 bytes | Unit:1
15560 | Slave07 Outlet Port03 Over Power Warning | RW | 2 bytes | Unit:1
15561 | Slave07 Outlet Port04 Over Power Warning | RW | 2 bytes | Unit:1
15562 | Slave07 Outlet Port05 Over Power Warning | RW | 2 bytes | Unit:1
15563 | Slave07 Outlet Port06 Over Power Warning | RW | 2 bytes | Unit:1
15564 | Slave07 Outlet Port07 Over Power Warning | RW | 2 bytes | Unit:1
15565 | Slave07 Outlet Port08 Over Power Warning | RW | 2 bytes | Unit:1
15566 | Slave07 Outlet Port09 Over Power Warning | RW | 2 bytes | Unit:1
15567 | Slave07 Outlet Port10 Over Power Warning | RW | 2 bytes | Unit:1
15568 | Slave07 Outlet Port11 Over Power Warning | RW | 2 bytes | Unit:1
15569 | Slave07 Outlet Port12 Over Power Warning | RW | 2 bytes | Unit:1
15570 | Slave07 Outlet Port13 Over Power Warning | RW | 2 bytes | Unit:1
15571 | Slave07 Outlet Port14 Over Power Warning | RW | 2 bytes | Unit:1
15572 | Slave07 Outlet Port15 Over Power Warning | RW | 2 bytes | Unit:1
15573 | Slave07 Outlet Port16 Over Power Warning | RW | 2 bytes | Unit:1
15574 | Slave07 Outlet Port17 Over Power Warning | RW | 2 bytes | Unit:1
15575 | Slave07 Outlet Port18 Over Power Warning | RW | 2 bytes | Unit:1
15576 | Slave07 Outlet Port19 Over Power Warning | RW | 2 bytes | Unit:1
15577 | Slave07 Outlet Port20 Over Power Warning | RW | 2 bytes | Unit:1
15578 | Slave07 Outlet Port21 Over Power Warning | RW | 2 bytes | Unit:1
15579 | Slave07 Outlet Port22 Over Power Warning | RW | 2 bytes | Unit:1
15580 | Slave07 Outlet Port23 Over Power Warning | RW | 2 bytes | Unit:1
15581 | Slave07 Outlet Port24 Over Power Warning | RW | 2 bytes | Unit:1
15582 | Slave07 Outlet Port25 Over Power Warning | RW | 2 bytes | Unit:1
15583 | Slave07 Outlet Port26 Over Power Warning | RW | 2 bytes | Unit:1
15584 | Slave07 Outlet Port27 Over Power Warning | RW | 2 bytes | Unit:1
15585 | Slave07 Outlet Port28 Over Power Warning | RW | 2 bytes | Unit:1
15586 | Slave07 Outlet Port29 Over Power Warning | RW | 2 bytes | Unit:1
15587 | Slave07 Outlet Port30 Over Power Warning | RW | 2 bytes | Unit:1
15588 | Slave07 Outlet Port31 Over Power Warning | RW | 2 bytes | Unit:1
15589 | Slave07 Outlet Port32 Over Power Warning | RW | 2 bytes | Unit:1
15590 | Slave07 Outlet Port33 Over Power Warning | RW | 2 bytes | Unit:1
15591 | Slave07 Outlet Port34 Over Power Warning | RW | 2 bytes | Unit:1
15592 | Slave07 Outlet Port35 Over Power Warning | RW | 2 bytes | Unit:1
15593 | Slave07 Outlet Port36 Over Power Warning | RW | 2 bytes | Unit:1
15594 | Slave07 Outlet Port37 Over Power Warning | RW | 2 bytes | Unit:1
15595 | Slave07 Outlet Port38 Over Power Warning | RW | 2 bytes | Unit:1
15596 | Slave07 Outlet Port39 Over Power Warning | RW | 2 bytes | Unit:1
15597 | Slave07 Outlet Port40 Over Power Warning | RW | 2 bytes | Unit:1
15598 | Slave07 Outlet Port41 Over Power Warning | RW | 2 bytes | Unit:1
15599 | Slave07 Outlet Port42 Over Power Warning | RW | 2 bytes | Unit:1
15600 | Slave08 Outlet Port01 Over Power Warning | RW | 2 bytes | Unit:1
15601 | Slave08 Outlet Port02 Over Power Warning | RW | 2 bytes | Unit:1
15602 | Slave08 Outlet Port03 Over Power Warning | RW | 2 bytes | Unit:1
15603 | Slave08 Outlet Port04 Over Power Warning | RW | 2 bytes | Unit:1
15604 | Slave08 Outlet Port05 Over Power Warning | RW | 2 bytes | Unit:1
15605 | Slave08 Outlet Port06 Over Power Warning | RW | 2 bytes | Unit:1
15606 | Slave08 Outlet Port07 Over Power Warning | RW | 2 bytes | Unit:1
15607 | Slave08 Outlet Port08 Over Power Warning | RW | 2 bytes | Unit:1
15608 | Slave08 Outlet Port09 Over Power Warning | RW | 2 bytes | Unit:1
15609 | Slave08 Outlet Port10 Over Power Warning | RW | 2 bytes | Unit:1
15610 | Slave08 Outlet Port11 Over Power Warning | RW | 2 bytes | Unit:1
15611 | Slave08 Outlet Port12 Over Power Warning | RW | 2 bytes | Unit:1
15612 | Slave08 Outlet Port13 Over Power Warning | RW | 2 bytes | Unit:1
15613 | Slave08 Outlet Port14 Over Power Warning | RW | 2 bytes | Unit:1
15614 | Slave08 Outlet Port15 Over Power Warning | RW | 2 bytes | Unit:1
15615 | Slave08 Outlet Port16 Over Power Warning | RW | 2 bytes | Unit:1
15616 | Slave08 Outlet Port17 Over Power Warning | RW | 2 bytes | Unit:1
15617 | Slave08 Outlet Port18 Over Power Warning | RW | 2 bytes | Unit:1
15618 | Slave08 Outlet Port19 Over Power Warning | RW | 2 bytes | Unit:1
15619 | Slave08 Outlet Port20 Over Power Warning | RW | 2 bytes | Unit:1
15620 | Slave08 Outlet Port21 Over Power Warning | RW | 2 bytes | Unit:1
15621 | Slave08 Outlet Port22 Over Power Warning | RW | 2 bytes | Unit:1
15622 | Slave08 Outlet Port23 Over Power Warning | RW | 2 bytes | Unit:1
15623 | Slave08 Outlet Port24 Over Power Warning | RW | 2 bytes | Unit:1
15624 | Slave08 Outlet Port25 Over Power Warning | RW | 2 bytes | Unit:1
15625 | Slave08 Outlet Port26 Over Power Warning | RW | 2 bytes | Unit:1
15626 | Slave08 Outlet Port27 Over Power Warning | RW | 2 bytes | Unit:1
15627 | Slave08 Outlet Port28 Over Power Warning | RW | 2 bytes | Unit:1
15628 | Slave08 Outlet Port29 Over Power Warning | RW | 2 bytes | Unit:1
15629 | Slave08 Outlet Port30 Over Power Warning | RW | 2 bytes | Unit:1
15630 | Slave08 Outlet Port31 Over Power Warning | RW | 2 bytes | Unit:1
15631 | Slave08 Outlet Port32 Over Power Warning | RW | 2 bytes | Unit:1
15632 | Slave08 Outlet Port33 Over Power Warning | RW | 2 bytes | Unit:1
15633 | Slave08 Outlet Port34 Over Power Warning | RW | 2 bytes | Unit:1
15634 | Slave08 Outlet Port35 Over Power Warning | RW | 2 bytes | Unit:1
15635 | Slave08 Outlet Port36 Over Power Warning | RW | 2 bytes | Unit:1
15636 | Slave08 Outlet Port37 Over Power Warning | RW | 2 bytes | Unit:1
15637 | Slave08 Outlet Port38 Over Power Warning | RW | 2 bytes | Unit:1
15638 | Slave08 Outlet Port39 Over Power Warning | RW | 2 bytes | Unit:1
15639 | Slave08 Outlet Port40 Over Power Warning | RW | 2 bytes | Unit:1
15640 | Slave08 Outlet Port41 Over Power Warning | RW | 2 bytes | Unit:1
15641 | Slave08 Outlet Port42 Over Power Warning | RW | 2 bytes | Unit:1
15642 | Slave09 Outlet Port01 Over Power Warning | RW | 2 bytes | Unit:1
15643 | Slave09 Outlet Port02 Over Power Warning | RW | 2 bytes | Unit:1
15644 | Slave09 Outlet Port03 Over Power Warning | RW | 2 bytes | Unit:1
15645 | Slave09 Outlet Port04 Over Power Warning | RW | 2 bytes | Unit:1
15646 | Slave09 Outlet Port05 Over Power Warning | RW | 2 bytes | Unit:1
15647 | Slave09 Outlet Port06 Over Power Warning | RW | 2 bytes | Unit:1
15648 | Slave09 Outlet Port07 Over Power Warning | RW | 2 bytes | Unit:1
15649 | Slave09 Outlet Port08 Over Power Warning | RW | 2 bytes | Unit:1
15650 | Slave09 Outlet Port09 Over Power Warning | RW | 2 bytes | Unit:1
15651 | Slave09 Outlet Port10 Over Power Warning | RW | 2 bytes | Unit:1
15652 | Slave09 Outlet Port11 Over Power Warning | RW | 2 bytes | Unit:1
15653 | Slave09 Outlet Port12 Over Power Warning | RW | 2 bytes | Unit:1
15654 | Slave09 Outlet Port13 Over Power Warning | RW | 2 bytes | Unit:1
15655 | Slave09 Outlet Port14 Over Power Warning | RW | 2 bytes | Unit:1
15656 | Slave09 Outlet Port15 Over Power Warning | RW | 2 bytes | Unit:1
15657 | Slave09 Outlet Port16 Over Power Warning | RW | 2 bytes | Unit:1
15658 | Slave09 Outlet Port17 Over Power Warning | RW | 2 bytes | Unit:1
15659 | Slave09 Outlet Port18 Over Power Warning | RW | 2 bytes | Unit:1
15660 | Slave09 Outlet Port19 Over Power Warning | RW | 2 bytes | Unit:1
15661 | Slave09 Outlet Port20 Over Power Warning | RW | 2 bytes | Unit:1
15662 | Slave09 Outlet Port21 Over Power Warning | RW | 2 bytes | Unit:1
15663 | Slave09 Outlet Port22 Over Power Warning | RW | 2 bytes | Unit:1
15664 | Slave09 Outlet Port23 Over Power Warning | RW | 2 bytes | Unit:1
15665 | Slave09 Outlet Port24 Over Power Warning | RW | 2 bytes | Unit:1
15666 | Slave09 Outlet Port25 Over Power Warning | RW | 2 bytes | Unit:1
15667 | Slave09 Outlet Port26 Over Power Warning | RW | 2 bytes | Unit:1
15668 | Slave09 Outlet Port27 Over Power Warning | RW | 2 bytes | Unit:1
15669 | Slave09 Outlet Port28 Over Power Warning | RW | 2 bytes | Unit:1
15670 | Slave09 Outlet Port29 Over Power Warning | RW | 2 bytes | Unit:1
15671 | Slave09 Outlet Port30 Over Power Warning | RW | 2 bytes | Unit:1
15672 | Slave09 Outlet Port31 Over Power Warning | RW | 2 bytes | Unit:1
15673 | Slave09 Outlet Port32 Over Power Warning | RW | 2 bytes | Unit:1
15674 | Slave09 Outlet Port33 Over Power Warning | RW | 2 bytes | Unit:1
15675 | Slave09 Outlet Port34 Over Power Warning | RW | 2 bytes | Unit:1
15676 | Slave09 Outlet Port35 Over Power Warning | RW | 2 bytes | Unit:1
15677 | Slave09 Outlet Port36 Over Power Warning | RW | 2 bytes | Unit:1
15678 | Slave09 Outlet Port37 Over Power Warning | RW | 2 bytes | Unit:1
15679 | Slave09 Outlet Port38 Over Power Warning | RW | 2 bytes | Unit:1
15680 | Slave09 Outlet Port39 Over Power Warning | RW | 2 bytes | Unit:1
15681 | Slave09 Outlet Port40 Over Power Warning | RW | 2 bytes | Unit:1
15682 | Slave09 Outlet Port41 Over Power Warning | RW | 2 bytes | Unit:1
15683 | Slave09 Outlet Port42 Over Power Warning | RW | 2 bytes | Unit:1
15684 | Slave10 Outlet Port01 Over Power Warning | RW | 2 bytes | Unit:1
15685 | Slave10 Outlet Port02 Over Power Warning | RW | 2 bytes | Unit:1
15686 | Slave10 Outlet Port03 Over Power Warning | RW | 2 bytes | Unit:1
15687 | Slave10 Outlet Port04 Over Power Warning | RW | 2 bytes | Unit:1
15688 | Slave10 Outlet Port05 Over Power Warning | RW | 2 bytes | Unit:1
15689 | Slave10 Outlet Port06 Over Power Warning | RW | 2 bytes | Unit:1
15690 | Slave10 Outlet Port07 Over Power Warning | RW | 2 bytes | Unit:1
15691 | Slave10 Outlet Port08 Over Power Warning | RW | 2 bytes | Unit:1
15692 | Slave10 Outlet Port09 Over Power Warning | RW | 2 bytes | Unit:1
15693 | Slave10 Outlet Port10 Over Power Warning | RW | 2 bytes | Unit:1
15694 | Slave10 Outlet Port11 Over Power Warning | RW | 2 bytes | Unit:1
15695 | Slave10 Outlet Port12 Over Power Warning | RW | 2 bytes | Unit:1
15696 | Slave10 Outlet Port13 Over Power Warning | RW | 2 bytes | Unit:1
15697 | Slave10 Outlet Port14 Over Power Warning | RW | 2 bytes | Unit:1
15698 | Slave10 Outlet Port15 Over Power Warning | RW | 2 bytes | Unit:1
15699 | Slave10 Outlet Port16 Over Power Warning | RW | 2 bytes | Unit:1
15700 | Slave10 Outlet Port17 Over Power Warning | RW | 2 bytes | Unit:1
15701 | Slave10 Outlet Port18 Over Power Warning | RW | 2 bytes | Unit:1
15702 | Slave10 Outlet Port19 Over Power Warning | RW | 2 bytes | Unit:1
15703 | Slave10 Outlet Port20 Over Power Warning | RW | 2 bytes | Unit:1
15704 | Slave10 Outlet Port21 Over Power Warning | RW | 2 bytes | Unit:1
15705 | Slave10 Outlet Port22 Over Power Warning | RW | 2 bytes | Unit:1
15706 | Slave10 Outlet Port23 Over Power Warning | RW | 2 bytes | Unit:1
15707 | Slave10 Outlet Port24 Over Power Warning | RW | 2 bytes | Unit:1
15708 | Slave10 Outlet Port25 Over Power Warning | RW | 2 bytes | Unit:1
15709 | Slave10 Outlet Port26 Over Power Warning | RW | 2 bytes | Unit:1
15710 | Slave10 Outlet Port27 Over Power Warning | RW | 2 bytes | Unit:1
15711 | Slave10 Outlet Port28 Over Power Warning | RW | 2 bytes | Unit:1
15712 | Slave10 Outlet Port29 Over Power Warning | RW | 2 bytes | Unit:1
15713 | Slave10 Outlet Port30 Over Power Warning | RW | 2 bytes | Unit:1
15714 | Slave10 Outlet Port31 Over Power Warning | RW | 2 bytes | Unit:1
15715 | Slave10 Outlet Port32 Over Power Warning | RW | 2 bytes | Unit:1
15716 | Slave10 Outlet Port33 Over Power Warning | RW | 2 bytes | Unit:1
15717 | Slave10 Outlet Port34 Over Power Warning | RW | 2 bytes | Unit:1
15718 | Slave10 Outlet Port35 Over Power Warning | RW | 2 bytes | Unit:1
15719 | Slave10 Outlet Port36 Over Power Warning | RW | 2 bytes | Unit:1
15720 | Slave10 Outlet Port37 Over Power Warning | RW | 2 bytes | Unit:1
15721 | Slave10 Outlet Port38 Over Power Warning | RW | 2 bytes | Unit:1
15722 | Slave10 Outlet Port39 Over Power Warning | RW | 2 bytes | Unit:1
15723 | Slave10 Outlet Port40 Over Power Warning | RW | 2 bytes | Unit:1
15724 | Slave10 Outlet Port41 Over Power Warning | RW | 2 bytes | Unit:1
15725 | Slave10 Outlet Port42 Over Power Warning | RW | 2 bytes | Unit:1
15726 | Slave11 Outlet Port01 Over Power Warning | RW | 2 bytes | Unit:1
15727 | Slave11 Outlet Port02 Over Power Warning | RW | 2 bytes | Unit:1
15728 | Slave11 Outlet Port03 Over Power Warning | RW | 2 bytes | Unit:1
15729 | Slave11 Outlet Port04 Over Power Warning | RW | 2 bytes | Unit:1
15730 | Slave11 Outlet Port05 Over Power Warning | RW | 2 bytes | Unit:1
15731 | Slave11 Outlet Port06 Over Power Warning | RW | 2 bytes | Unit:1
15732 | Slave11 Outlet Port07 Over Power Warning | RW | 2 bytes | Unit:1
15733 | Slave11 Outlet Port08 Over Power Warning | RW | 2 bytes | Unit:1
15734 | Slave11 Outlet Port09 Over Power Warning | RW | 2 bytes | Unit:1
15735 | Slave11 Outlet Port10 Over Power Warning | RW | 2 bytes | Unit:1
15736 | Slave11 Outlet Port11 Over Power Warning | RW | 2 bytes | Unit:1
15737 | Slave11 Outlet Port12 Over Power Warning | RW | 2 bytes | Unit:1
15738 | Slave11 Outlet Port13 Over Power Warning | RW | 2 bytes | Unit:1
15739 | Slave11 Outlet Port14 Over Power Warning | RW | 2 bytes | Unit:1
15740 | Slave11 Outlet Port15 Over Power Warning | RW | 2 bytes | Unit:1
15741 | Slave11 Outlet Port16 Over Power Warning | RW | 2 bytes | Unit:1
15742 | Slave11 Outlet Port17 Over Power Warning | RW | 2 bytes | Unit:1
15743 | Slave11 Outlet Port18 Over Power Warning | RW | 2 bytes | Unit:1
15744 | Slave11 Outlet Port19 Over Power Warning | RW | 2 bytes | Unit:1
15745 | Slave11 Outlet Port20 Over Power Warning | RW | 2 bytes | Unit:1
15746 | Slave11 Outlet Port21 Over Power Warning | RW | 2 bytes | Unit:1
15747 | Slave11 Outlet Port22 Over Power Warning | RW | 2 bytes | Unit:1
15748 | Slave11 Outlet Port23 Over Power Warning | RW | 2 bytes | Unit:1
15749 | Slave11 Outlet Port24 Over Power Warning | RW | 2 bytes | Unit:1
15750 | Slave11 Outlet Port25 Over Power Warning | RW | 2 bytes | Unit:1
15751 | Slave11 Outlet Port26 Over Power Warning | RW | 2 bytes | Unit:1
15752 | Slave11 Outlet Port27 Over Power Warning | RW | 2 bytes | Unit:1
15753 | Slave11 Outlet Port28 Over Power Warning | RW | 2 bytes | Unit:1
15754 | Slave11 Outlet Port29 Over Power Warning | RW | 2 bytes | Unit:1
15755 | Slave11 Outlet Port30 Over Power Warning | RW | 2 bytes | Unit:1
15756 | Slave11 Outlet Port31 Over Power Warning | RW | 2 bytes | Unit:1
15757 | Slave11 Outlet Port32 Over Power Warning | RW | 2 bytes | Unit:1
15758 | Slave11 Outlet Port33 Over Power Warning | RW | 2 bytes | Unit:1
15759 | Slave11 Outlet Port34 Over Power Warning | RW | 2 bytes | Unit:1
15760 | Slave11 Outlet Port35 Over Power Warning | RW | 2 bytes | Unit:1
15761 | Slave11 Outlet Port36 Over Power Warning | RW | 2 bytes | Unit:1
15762 | Slave11 Outlet Port37 Over Power Warning | RW | 2 bytes | Unit:1
15763 | Slave11 Outlet Port38 Over Power Warning | RW | 2 bytes | Unit:1
15764 | Slave11 Outlet Port39 Over Power Warning | RW | 2 bytes | Unit:1
15765 | Slave11 Outlet Port40 Over Power Warning | RW | 2 bytes | Unit:1
15766 | Slave11 Outlet Port41 Over Power Warning | RW | 2 bytes | Unit:1
15767 | Slave11 Outlet Port42 Over Power Warning | RW | 2 bytes | Unit:1
15768 | Slave12 Outlet Port01 Over Power Warning | RW | 2 bytes | Unit:1
15769 | Slave12 Outlet Port02 Over Power Warning | RW | 2 bytes | Unit:1
15770 | Slave12 Outlet Port03 Over Power Warning | RW | 2 bytes | Unit:1
15771 | Slave12 Outlet Port04 Over Power Warning | RW | 2 bytes | Unit:1
15772 | Slave12 Outlet Port05 Over Power Warning | RW | 2 bytes | Unit:1
15773 | Slave12 Outlet Port06 Over Power Warning | RW | 2 bytes | Unit:1
15774 | Slave12 Outlet Port07 Over Power Warning | RW | 2 bytes | Unit:1
15775 | Slave12 Outlet Port08 Over Power Warning | RW | 2 bytes | Unit:1
15776 | Slave12 Outlet Port09 Over Power Warning | RW | 2 bytes | Unit:1
15777 | Slave12 Outlet Port10 Over Power Warning | RW | 2 bytes | Unit:1
15778 | Slave12 Outlet Port11 Over Power Warning | RW | 2 bytes | Unit:1
15779 | Slave12 Outlet Port12 Over Power Warning | RW | 2 bytes | Unit:1
15780 | Slave12 Outlet Port13 Over Power Warning | RW | 2 bytes | Unit:1
15781 | Slave12 Outlet Port14 Over Power Warning | RW | 2 bytes | Unit:1
15782 | Slave12 Outlet Port15 Over Power Warning | RW | 2 bytes | Unit:1
15783 | Slave12 Outlet Port16 Over Power Warning | RW | 2 bytes | Unit:1
15784 | Slave12 Outlet Port17 Over Power Warning | RW | 2 bytes | Unit:1
15785 | Slave12 Outlet Port18 Over Power Warning | RW | 2 bytes | Unit:1
15786 | Slave12 Outlet Port19 Over Power Warning | RW | 2 bytes | Unit:1
15787 | Slave12 Outlet Port20 Over Power Warning | RW | 2 bytes | Unit:1
15788 | Slave12 Outlet Port21 Over Power Warning | RW | 2 bytes | Unit:1
15789 | Slave12 Outlet Port22 Over Power Warning | RW | 2 bytes | Unit:1
15790 | Slave12 Outlet Port23 Over Power Warning | RW | 2 bytes | Unit:1
15791 | Slave12 Outlet Port24 Over Power Warning | RW | 2 bytes | Unit:1
15792 | Slave12 Outlet Port25 Over Power Warning | RW | 2 bytes | Unit:1
15793 | Slave12 Outlet Port26 Over Power Warning | RW | 2 bytes | Unit:1
15794 | Slave12 Outlet Port27 Over Power Warning | RW | 2 bytes | Unit:1
15795 | Slave12 Outlet Port28 Over Power Warning | RW | 2 bytes | Unit:1
15796 | Slave12 Outlet Port29 Over Power Warning | RW | 2 bytes | Unit:1
15797 | Slave12 Outlet Port30 Over Power Warning | RW | 2 bytes | Unit:1
15798 | Slave12 Outlet Port31 Over Power Warning | RW | 2 bytes | Unit:1
15799 | Slave12 Outlet Port32 Over Power Warning | RW | 2 bytes | Unit:1
15800 | Slave12 Outlet Port33 Over Power Warning | RW | 2 bytes | Unit:1
15801 | Slave12 Outlet Port34 Over Power Warning | RW | 2 bytes | Unit:1
15802 | Slave12 Outlet Port35 Over Power Warning | RW | 2 bytes | Unit:1
15803 | Slave12 Outlet Port36 Over Power Warning | RW | 2 bytes | Unit:1
15804 | Slave12 Outlet Port37 Over Power Warning | RW | 2 bytes | Unit:1
15805 | Slave12 Outlet Port38 Over Power Warning | RW | 2 bytes | Unit:1
15806 | Slave12 Outlet Port39 Over Power Warning | RW | 2 bytes | Unit:1
15807 | Slave12 Outlet Port40 Over Power Warning | RW | 2 bytes | Unit:1
15808 | Slave12 Outlet Port41 Over Power Warning | RW | 2 bytes | Unit:1
15809 | Slave12 Outlet Port42 Over Power Warning | RW | 2 bytes | Unit:1
15810 | Slave13 Outlet Port01 Over Power Warning | RW | 2 bytes | Unit:1
15811 | Slave13 Outlet Port02 Over Power Warning | RW | 2 bytes | Unit:1
15812 | Slave13 Outlet Port03 Over Power Warning | RW | 2 bytes | Unit:1
15813 | Slave13 Outlet Port04 Over Power Warning | RW | 2 bytes | Unit:1
15814 | Slave13 Outlet Port05 Over Power Warning | RW | 2 bytes | Unit:1
15815 | Slave13 Outlet Port06 Over Power Warning | RW | 2 bytes | Unit:1
15816 | Slave13 Outlet Port07 Over Power Warning | RW | 2 bytes | Unit:1
15817 | Slave13 Outlet Port08 Over Power Warning | RW | 2 bytes | Unit:1
15818 | Slave13 Outlet Port09 Over Power Warning | RW | 2 bytes | Unit:1
15819 | Slave13 Outlet Port10 Over Power Warning | RW | 2 bytes | Unit:1
15820 | Slave13 Outlet Port11 Over Power Warning | RW | 2 bytes | Unit:1
15821 | Slave13 Outlet Port12 Over Power Warning | RW | 2 bytes | Unit:1
15822 | Slave13 Outlet Port13 Over Power Warning | RW | 2 bytes | Unit:1
15823 | Slave13 Outlet Port14 Over Power Warning | RW | 2 bytes | Unit:1
15824 | Slave13 Outlet Port15 Over Power Warning | RW | 2 bytes | Unit:1
15825 | Slave13 Outlet Port16 Over Power Warning | RW | 2 bytes | Unit:1
15826 | Slave13 Outlet Port17 Over Power Warning | RW | 2 bytes | Unit:1
15827 | Slave13 Outlet Port18 Over Power Warning | RW | 2 bytes | Unit:1
15828 | Slave13 Outlet Port19 Over Power Warning | RW | 2 bytes | Unit:1
15829 | Slave13 Outlet Port20 Over Power Warning | RW | 2 bytes | Unit:1
15830 | Slave13 Outlet Port21 Over Power Warning | RW | 2 bytes | Unit:1
15831 | Slave13 Outlet Port22 Over Power Warning | RW | 2 bytes | Unit:1
15832 | Slave13 Outlet Port23 Over Power Warning | RW | 2 bytes | Unit:1
15833 | Slave13 Outlet Port24 Over Power Warning | RW | 2 bytes | Unit:1
15834 | Slave13 Outlet Port25 Over Power Warning | RW | 2 bytes | Unit:1
15835 | Slave13 Outlet Port26 Over Power Warning | RW | 2 bytes | Unit:1
15836 | Slave13 Outlet Port27 Over Power Warning | RW | 2 bytes | Unit:1
15837 | Slave13 Outlet Port28 Over Power Warning | RW | 2 bytes | Unit:1
15838 | Slave13 Outlet Port29 Over Power Warning | RW | 2 bytes | Unit:1
15839 | Slave13 Outlet Port30 Over Power Warning | RW | 2 bytes | Unit:1
15840 | Slave13 Outlet Port31 Over Power Warning | RW | 2 bytes | Unit:1
15841 | Slave13 Outlet Port32 Over Power Warning | RW | 2 bytes | Unit:1
15842 | Slave13 Outlet Port33 Over Power Warning | RW | 2 bytes | Unit:1
15843 | Slave13 Outlet Port34 Over Power Warning | RW | 2 bytes | Unit:1
15844 | Slave13 Outlet Port35 Over Power Warning | RW | 2 bytes | Unit:1
15845 | Slave13 Outlet Port36 Over Power Warning | RW | 2 bytes | Unit:1
15846 | Slave13 Outlet Port37 Over Power Warning | RW | 2 bytes | Unit:1
15847 | Slave13 Outlet Port38 Over Power Warning | RW | 2 bytes | Unit:1
15848 | Slave13 Outlet Port39 Over Power Warning | RW | 2 bytes | Unit:1
15849 | Slave13 Outlet Port40 Over Power Warning | RW | 2 bytes | Unit:1
15850 | Slave13 Outlet Port41 Over Power Warning | RW | 2 bytes | Unit:1
15851 | Slave13 Outlet Port42 Over Power Warning | RW | 2 bytes | Unit:1
15852 | Slave14 Outlet Port01 Over Power Warning | RW | 2 bytes | Unit:1
15853 | Slave14 Outlet Port02 Over Power Warning | RW | 2 bytes | Unit:1
15854 | Slave14 Outlet Port03 Over Power Warning | RW | 2 bytes | Unit:1
15855 | Slave14 Outlet Port04 Over Power Warning | RW | 2 bytes | Unit:1
15856 | Slave14 Outlet Port05 Over Power Warning | RW | 2 bytes | Unit:1
15857 | Slave14 Outlet Port06 Over Power Warning | RW | 2 bytes | Unit:1
15858 | Slave14 Outlet Port07 Over Power Warning | RW | 2 bytes | Unit:1
15859 | Slave14 Outlet Port08 Over Power Warning | RW | 2 bytes | Unit:1
15860 | Slave14 Outlet Port09 Over Power Warning | RW | 2 bytes | Unit:1
15861 | Slave14 Outlet Port10 Over Power Warning | RW | 2 bytes | Unit:1
15862 | Slave14 Outlet Port11 Over Power Warning | RW | 2 bytes | Unit:1
15863 | Slave14 Outlet Port12 Over Power Warning | RW | 2 bytes | Unit:1
15864 | Slave14 Outlet Port13 Over Power Warning | RW | 2 bytes | Unit:1
15865 | Slave14 Outlet Port14 Over Power Warning | RW | 2 bytes | Unit:1
15866 | Slave14 Outlet Port15 Over Power Warning | RW | 2 bytes | Unit:1
15867 | Slave14 Outlet Port16 Over Power Warning | RW | 2 bytes | Unit:1
15868 | Slave14 Outlet Port17 Over Power Warning | RW | 2 bytes | Unit:1
15869 | Slave14 Outlet Port18 Over Power Warning | RW | 2 bytes | Unit:1
15870 | Slave14 Outlet Port19 Over Power Warning | RW | 2 bytes | Unit:1
15871 | Slave14 Outlet Port20 Over Power Warning | RW | 2 bytes | Unit:1
15872 | Slave14 Outlet Port21 Over Power Warning | RW | 2 bytes | Unit:1
15873 | Slave14 Outlet Port22 Over Power Warning | RW | 2 bytes | Unit:1
15874 | Slave14 Outlet Port23 Over Power Warning | RW | 2 bytes | Unit:1
15875 | Slave14 Outlet Port24 Over Power Warning | RW | 2 bytes | Unit:1
15876 | Slave14 Outlet Port25 Over Power Warning | RW | 2 bytes | Unit:1
15877 | Slave14 Outlet Port26 Over Power Warning | RW | 2 bytes | Unit:1
15878 | Slave14 Outlet Port27 Over Power Warning | RW | 2 bytes | Unit:1
15879 | Slave14 Outlet Port28 Over Power Warning | RW | 2 bytes | Unit:1
15880 | Slave14 Outlet Port29 Over Power Warning | RW | 2 bytes | Unit:1
15881 | Slave14 Outlet Port30 Over Power Warning | RW | 2 bytes | Unit:1
15882 | Slave14 Outlet Port31 Over Power Warning | RW | 2 bytes | Unit:1
15883 | Slave14 Outlet Port32 Over Power Warning | RW | 2 bytes | Unit:1
15884 | Slave14 Outlet Port33 Over Power Warning | RW | 2 bytes | Unit:1
15885 | Slave14 Outlet Port34 Over Power Warning | RW | 2 bytes | Unit:1
15886 | Slave14 Outlet Port35 Over Power Warning | RW | 2 bytes | Unit:1
15887 | Slave14 Outlet Port36 Over Power Warning | RW | 2 bytes | Unit:1
15888 | Slave14 Outlet Port37 Over Power Warning | RW | 2 bytes | Unit:1
15889 | Slave14 Outlet Port38 Over Power Warning | RW | 2 bytes | Unit:1
15890 | Slave14 Outlet Port39 Over Power Warning | RW | 2 bytes | Unit:1
15891 | Slave14 Outlet Port40 Over Power Warning | RW | 2 bytes | Unit:1
15892 | Slave14 Outlet Port41 Over Power Warning | RW | 2 bytes | Unit:1
15893 | Slave14 Outlet Port42 Over Power Warning | RW | 2 bytes | Unit:1
15894 | Slave15 Outlet Port01 Over Power Warning | RW | 2 bytes | Unit:1
15895 | Slave15 Outlet Port02 Over Power Warning | RW | 2 bytes | Unit:1
15896 | Slave15 Outlet Port03 Over Power Warning | RW | 2 bytes | Unit:1
15897 | Slave15 Outlet Port04 Over Power Warning | RW | 2 bytes | Unit:1
15898 | Slave15 Outlet Port05 Over Power Warning | RW | 2 bytes | Unit:1
15899 | Slave15 Outlet Port06 Over Power Warning | RW | 2 bytes | Unit:1
15900 | Slave15 Outlet Port07 Over Power Warning | RW | 2 bytes | Unit:1
15901 | Slave15 Outlet Port08 Over Power Warning | RW | 2 bytes | Unit:1
15902 | Slave15 Outlet Port09 Over Power Warning | RW | 2 bytes | Unit:1
15903 | Slave15 Outlet Port10 Over Power Warning | RW | 2 bytes | Unit:1
15904 | Slave15 Outlet Port11 Over Power Warning | RW | 2 bytes | Unit:1
15905 | Slave15 Outlet Port12 Over Power Warning | RW | 2 bytes | Unit:1
15906 | Slave15 Outlet Port13 Over Power Warning | RW | 2 bytes | Unit:1
15907 | Slave15 Outlet Port14 Over Power Warning | RW | 2 bytes | Unit:1
15908 | Slave15 Outlet Port15 Over Power Warning | RW | 2 bytes | Unit:1
15909 | Slave15 Outlet Port16 Over Power Warning | RW | 2 bytes | Unit:1
15910 | Slave15 Outlet Port17 Over Power Warning | RW | 2 bytes | Unit:1
15911 | Slave15 Outlet Port18 Over Power Warning | RW | 2 bytes | Unit:1
15912 | Slave15 Outlet Port19 Over Power Warning | RW | 2 bytes | Unit:1
15913 | Slave15 Outlet Port20 Over Power Warning | RW | 2 bytes | Unit:1
15914 | Slave15 Outlet Port21 Over Power Warning | RW | 2 bytes | Unit:1
15915 | Slave15 Outlet Port22 Over Power Warning | RW | 2 bytes | Unit:1
15916 | Slave15 Outlet Port23 Over Power Warning | RW | 2 bytes | Unit:1
15917 | Slave15 Outlet Port24 Over Power Warning | RW | 2 bytes | Unit:1
15918 | Slave15 Outlet Port25 Over Power Warning | RW | 2 bytes | Unit:1
15919 | Slave15 Outlet Port26 Over Power Warning | RW | 2 bytes | Unit:1
15920 | Slave15 Outlet Port27 Over Power Warning | RW | 2 bytes | Unit:1
15921 | Slave15 Outlet Port28 Over Power Warning | RW | 2 bytes | Unit:1
15922 | Slave15 Outlet Port29 Over Power Warning | RW | 2 bytes | Unit:1
15923 | Slave15 Outlet Port30 Over Power Warning | RW | 2 bytes | Unit:1
15924 | Slave15 Outlet Port31 Over Power Warning | RW | 2 bytes | Unit:1
15925 | Slave15 Outlet Port32 Over Power Warning | RW | 2 bytes | Unit:1
15926 | Slave15 Outlet Port33 Over Power Warning | RW | 2 bytes | Unit:1
15927 | Slave15 Outlet Port34 Over Power Warning | RW | 2 bytes | Unit:1
15928 | Slave15 Outlet Port35 Over Power Warning | RW | 2 bytes | Unit:1
15929 | Slave15 Outlet Port36 Over Power Warning | RW | 2 bytes | Unit:1
15930 | Slave15 Outlet Port37 Over Power Warning | RW | 2 bytes | Unit:1
15931 | Slave15 Outlet Port38 Over Power Warning | RW | 2 bytes | Unit:1
15932 | Slave15 Outlet Port39 Over Power Warning | RW | 2 bytes | Unit:1
15933 | Slave15 Outlet Port40 Over Power Warning | RW | 2 bytes | Unit:1
15934 | Slave15 Outlet Port41 Over Power Warning | RW | 2 bytes | Unit:1
15935 | Slave15 Outlet Port42 Over Power Warning | RW | 2 bytes | Unit:1
15936 | Master Outlet Port01 Over Power Critical | RW | 2 bytes | Unit:1
15937 | Master Outlet Port02 Over Power Critical | RW | 2 bytes | Unit:1
15938 | Master Outlet Port03 Over Power Critical | RW | 2 bytes | Unit:1
15939 | Master Outlet Port04 Over Power Critical | RW | 2 bytes | Unit:1
15940 | Master Outlet Port05 Over Power Critical | RW | 2 bytes | Unit:1
15941 | Master Outlet Port06 Over Power Critical | RW | 2 bytes | Unit:1
15942 | Master Outlet Port07 Over Power Critical | RW | 2 bytes | Unit:1
15943 | Master Outlet Port08 Over Power Critical | RW | 2 bytes | Unit:1
15944 | Master Outlet Port09 Over Power Critical | RW | 2 bytes | Unit:1
15945 | Master Outlet Port10 Over Power Critical | RW | 2 bytes | Unit:1
15946 | Master Outlet Port11 Over Power Critical | RW | 2 bytes | Unit:1
15947 | Master Outlet Port12 Over Power Critical | RW | 2 bytes | Unit:1
15948 | Master Outlet Port13 Over Power Critical | RW | 2 bytes | Unit:1
15949 | Master Outlet Port14 Over Power Critical | RW | 2 bytes | Unit:1
15950 | Master Outlet Port15 Over Power Critical | RW | 2 bytes | Unit:1
15951 | Master Outlet Port16 Over Power Critical | RW | 2 bytes | Unit:1
15952 | Master Outlet Port17 Over Power Critical | RW | 2 bytes | Unit:1
15953 | Master Outlet Port18 Over Power Critical | RW | 2 bytes | Unit:1
15954 | Master Outlet Port19 Over Power Critical | RW | 2 bytes | Unit:1
15955 | Master Outlet Port20 Over Power Critical | RW | 2 bytes | Unit:1
15956 | Master Outlet Port21 Over Power Critical | RW | 2 bytes | Unit:1
15957 | Master Outlet Port22 Over Power Critical | RW | 2 bytes | Unit:1
15958 | Master Outlet Port23 Over Power Critical | RW | 2 bytes | Unit:1
15959 | Master Outlet Port24 Over Power Critical | RW | 2 bytes | Unit:1
15960 | Master Outlet Port25 Over Power Critical | RW | 2 bytes | Unit:1
15961 | Master Outlet Port26 Over Power Critical | RW | 2 bytes | Unit:1
15962 | Master Outlet Port27 Over Power Critical | RW | 2 bytes | Unit:1
15963 | Master Outlet Port28 Over Power Critical | RW | 2 bytes | Unit:1
15964 | Master Outlet Port29 Over Power Critical | RW | 2 bytes | Unit:1
15965 | Master Outlet Port30 Over Power Critical | RW | 2 bytes | Unit:1
15966 | Master Outlet Port31 Over Power Critical | RW | 2 bytes | Unit:1
15967 | Master Outlet Port32 Over Power Critical | RW | 2 bytes | Unit:1
15968 | Master Outlet Port33 Over Power Critical | RW | 2 bytes | Unit:1
15969 | Master Outlet Port34 Over Power Critical | RW | 2 bytes | Unit:1
15970 | Master Outlet Port35 Over Power Critical | RW | 2 bytes | Unit:1
15971 | Master Outlet Port36 Over Power Critical | RW | 2 bytes | Unit:1
15972 | Master Outlet Port37 Over Power Critical | RW | 2 bytes | Unit:1
15973 | Master Outlet Port38 Over Power Critical | RW | 2 bytes | Unit:1
15974 | Master Outlet Port39 Over Power Critical | RW | 2 bytes | Unit:1
15975 | Master Outlet Port40 Over Power Critical | RW | 2 bytes | Unit:1
15976 | Master Outlet Port41 Over Power Critical | RW | 2 bytes | Unit:1
15977 | Master Outlet Port42 Over Power Critical | RW | 2 bytes | Unit:1
15978 | Slave01 Outlet Port01 Over Power Critical | RW | 2 bytes | Unit:1
15979 | Slave01 Outlet Port02 Over Power Critical | RW | 2 bytes | Unit:1
15980 | Slave01 Outlet Port03 Over Power Critical | RW | 2 bytes | Unit:1
15981 | Slave01 Outlet Port04 Over Power Critical | RW | 2 bytes | Unit:1
15982 | Slave01 Outlet Port05 Over Power Critical | RW | 2 bytes | Unit:1
15983 | Slave01 Outlet Port06 Over Power Critical | RW | 2 bytes | Unit:1
15984 | Slave01 Outlet Port07 Over Power Critical | RW | 2 bytes | Unit:1
15985 | Slave01 Outlet Port08 Over Power Critical | RW | 2 bytes | Unit:1
15986 | Slave01 Outlet Port09 Over Power Critical | RW | 2 bytes | Unit:1
15987 | Slave01 Outlet Port10 Over Power Critical | RW | 2 bytes | Unit:1
15988 | Slave01 Outlet Port11 Over Power Critical | RW | 2 bytes | Unit:1
15989 | Slave01 Outlet Port12 Over Power Critical | RW | 2 bytes | Unit:1
15990 | Slave01 Outlet Port13 Over Power Critical | RW | 2 bytes | Unit:1
15991 | Slave01 Outlet Port14 Over Power Critical | RW | 2 bytes | Unit:1
15992 | Slave01 Outlet Port15 Over Power Critical | RW | 2 bytes | Unit:1
15993 | Slave01 Outlet Port16 Over Power Critical | RW | 2 bytes | Unit:1
15994 | Slave01 Outlet Port17 Over Power Critical | RW | 2 bytes | Unit:1
15995 | Slave01 Outlet Port18 Over Power Critical | RW | 2 bytes | Unit:1
15996 | Slave01 Outlet Port19 Over Power Critical | RW | 2 bytes | Unit:1
15997 | Slave01 Outlet Port20 Over Power Critical | RW | 2 bytes | Unit:1
15998 | Slave01 Outlet Port21 Over Power Critical | RW | 2 bytes | Unit:1
15999 | Slave01 Outlet Port22 Over Power Critical | RW | 2 bytes | Unit:1
16000 | Slave01 Outlet Port23 Over Power Critical | RW | 2 bytes | Unit:1
16001 | Slave01 Outlet Port24 Over Power Critical | RW | 2 bytes | Unit:1
16002 | Slave01 Outlet Port25 Over Power Critical | RW | 2 bytes | Unit:1
16003 | Slave01 Outlet Port26 Over Power Critical | RW | 2 bytes | Unit:1
16004 | Slave01 Outlet Port27 Over Power Critical | RW | 2 bytes | Unit:1
16005 | Slave01 Outlet Port28 Over Power Critical | RW | 2 bytes | Unit:1
16006 | Slave01 Outlet Port29 Over Power Critical | RW | 2 bytes | Unit:1
16007 | Slave01 Outlet Port30 Over Power Critical | RW | 2 bytes | Unit:1
16008 | Slave01 Outlet Port31 Over Power Critical | RW | 2 bytes | Unit:1
16009 | Slave01 Outlet Port32 Over Power Critical | RW | 2 bytes | Unit:1
16010 | Slave01 Outlet Port33 Over Power Critical | RW | 2 bytes | Unit:1
16011 | Slave01 Outlet Port34 Over Power Critical | RW | 2 bytes | Unit:1
16012 | Slave01 Outlet Port35 Over Power Critical | RW | 2 bytes | Unit:1
16013 | Slave01 Outlet Port36 Over Power Critical | RW | 2 bytes | Unit:1
16014 | Slave01 Outlet Port37 Over Power Critical | RW | 2 bytes | Unit:1
16015 | Slave01 Outlet Port38 Over Power Critical | RW | 2 bytes | Unit:1
16016 | Slave01 Outlet Port39 Over Power Critical | RW | 2 bytes | Unit:1
16017 | Slave01 Outlet Port40 Over Power Critical | RW | 2 bytes | Unit:1
16018 | Slave01 Outlet Port41 Over Power Critical | RW | 2 bytes | Unit:1
16019 | Slave01 Outlet Port42 Over Power Critical | RW | 2 bytes | Unit:1
16020 | Slave02 Outlet Port01 Over Power Critical | RW | 2 bytes | Unit:1
16021 | Slave02 Outlet Port02 Over Power Critical | RW | 2 bytes | Unit:1
16022 | Slave02 Outlet Port03 Over Power Critical | RW | 2 bytes | Unit:1
16023 | Slave02 Outlet Port04 Over Power Critical | RW | 2 bytes | Unit:1
16024 | Slave02 Outlet Port05 Over Power Critical | RW | 2 bytes | Unit:1
16025 | Slave02 Outlet Port06 Over Power Critical | RW | 2 bytes | Unit:1
16026 | Slave02 Outlet Port07 Over Power Critical | RW | 2 bytes | Unit:1
16027 | Slave02 Outlet Port08 Over Power Critical | RW | 2 bytes | Unit:1
16028 | Slave02 Outlet Port09 Over Power Critical | RW | 2 bytes | Unit:1
16029 | Slave02 Outlet Port10 Over Power Critical | RW | 2 bytes | Unit:1
16030 | Slave02 Outlet Port11 Over Power Critical | RW | 2 bytes | Unit:1
16031 | Slave02 Outlet Port12 Over Power Critical | RW | 2 bytes | Unit:1
16032 | Slave02 Outlet Port13 Over Power Critical | RW | 2 bytes | Unit:1
16033 | Slave02 Outlet Port14 Over Power Critical | RW | 2 bytes | Unit:1
16034 | Slave02 Outlet Port15 Over Power Critical | RW | 2 bytes | Unit:1
16035 | Slave02 Outlet Port16 Over Power Critical | RW | 2 bytes | Unit:1
16036 | Slave02 Outlet Port17 Over Power Critical | RW | 2 bytes | Unit:1
16037 | Slave02 Outlet Port18 Over Power Critical | RW | 2 bytes | Unit:1
16038 | Slave02 Outlet Port19 Over Power Critical | RW | 2 bytes | Unit:1
16039 | Slave02 Outlet Port20 Over Power Critical | RW | 2 bytes | Unit:1
16040 | Slave02 Outlet Port21 Over Power Critical | RW | 2 bytes | Unit:1
16041 | Slave02 Outlet Port22 Over Power Critical | RW | 2 bytes | Unit:1
16042 | Slave02 Outlet Port23 Over Power Critical | RW | 2 bytes | Unit:1
16043 | Slave02 Outlet Port24 Over Power Critical | RW | 2 bytes | Unit:1
16044 | Slave02 Outlet Port25 Over Power Critical | RW | 2 bytes | Unit:1
16045 | Slave02 Outlet Port26 Over Power Critical | RW | 2 bytes | Unit:1
16046 | Slave02 Outlet Port27 Over Power Critical | RW | 2 bytes | Unit:1
16047 | Slave02 Outlet Port28 Over Power Critical | RW | 2 bytes | Unit:1
16048 | Slave02 Outlet Port29 Over Power Critical | RW | 2 bytes | Unit:1
16049 | Slave02 Outlet Port30 Over Power Critical | RW | 2 bytes | Unit:1
16050 | Slave02 Outlet Port31 Over Power Critical | RW | 2 bytes | Unit:1
16051 | Slave02 Outlet Port32 Over Power Critical | RW | 2 bytes | Unit:1
16052 | Slave02 Outlet Port33 Over Power Critical | RW | 2 bytes | Unit:1
16053 | Slave02 Outlet Port34 Over Power Critical | RW | 2 bytes | Unit:1
16054 | Slave02 Outlet Port35 Over Power Critical | RW | 2 bytes | Unit:1
16055 | Slave02 Outlet Port36 Over Power Critical | RW | 2 bytes | Unit:1
16056 | Slave02 Outlet Port37 Over Power Critical | RW | 2 bytes | Unit:1
16057 | Slave02 Outlet Port38 Over Power Critical | RW | 2 bytes | Unit:1
16058 | Slave02 Outlet Port39 Over Power Critical | RW | 2 bytes | Unit:1
16059 | Slave02 Outlet Port40 Over Power Critical | RW | 2 bytes | Unit:1
16060 | Slave02 Outlet Port41 Over Power Critical | RW | 2 bytes | Unit:1
16061 | Slave02 Outlet Port42 Over Power Critical | RW | 2 bytes | Unit:1
16062 | Slave03 Outlet Port01 Over Power Critical | RW | 2 bytes | Unit:1
16063 | Slave03 Outlet Port02 Over Power Critical | RW | 2 bytes | Unit:1
16064 | Slave03 Outlet Port03 Over Power Critical | RW | 2 bytes | Unit:1
16065 | Slave03 Outlet Port04 Over Power Critical | RW | 2 bytes | Unit:1
16066 | Slave03 Outlet Port05 Over Power Critical | RW | 2 bytes | Unit:1
16067 | Slave03 Outlet Port06 Over Power Critical | RW | 2 bytes | Unit:1
16068 | Slave03 Outlet Port07 Over Power Critical | RW | 2 bytes | Unit:1
16069 | Slave03 Outlet Port08 Over Power Critical | RW | 2 bytes | Unit:1
16070 | Slave03 Outlet Port09 Over Power Critical | RW | 2 bytes | Unit:1
16071 | Slave03 Outlet Port10 Over Power Critical | RW | 2 bytes | Unit:1
16072 | Slave03 Outlet Port11 Over Power Critical | RW | 2 bytes | Unit:1
16073 | Slave03 Outlet Port12 Over Power Critical | RW | 2 bytes | Unit:1
16074 | Slave03 Outlet Port13 Over Power Critical | RW | 2 bytes | Unit:1
16075 | Slave03 Outlet Port14 Over Power Critical | RW | 2 bytes | Unit:1
16076 | Slave03 Outlet Port15 Over Power Critical | RW | 2 bytes | Unit:1
16077 | Slave03 Outlet Port16 Over Power Critical | RW | 2 bytes | Unit:1
16078 | Slave03 Outlet Port17 Over Power Critical | RW | 2 bytes | Unit:1
16079 | Slave03 Outlet Port18 Over Power Critical | RW | 2 bytes | Unit:1
16080 | Slave03 Outlet Port19 Over Power Critical | RW | 2 bytes | Unit:1
16081 | Slave03 Outlet Port20 Over Power Critical | RW | 2 bytes | Unit:1
16082 | Slave03 Outlet Port21 Over Power Critical | RW | 2 bytes | Unit:1
16083 | Slave03 Outlet Port22 Over Power Critical | RW | 2 bytes | Unit:1
16084 | Slave03 Outlet Port23 Over Power Critical | RW | 2 bytes | Unit:1
16085 | Slave03 Outlet Port24 Over Power Critical | RW | 2 bytes | Unit:1
16086 | Slave03 Outlet Port25 Over Power Critical | RW | 2 bytes | Unit:1
16087 | Slave03 Outlet Port26 Over Power Critical | RW | 2 bytes | Unit:1
16088 | Slave03 Outlet Port27 Over Power Critical | RW | 2 bytes | Unit:1
16089 | Slave03 Outlet Port28 Over Power Critical | RW | 2 bytes | Unit:1
16090 | Slave03 Outlet Port29 Over Power Critical | RW | 2 bytes | Unit:1
16091 | Slave03 Outlet Port30 Over Power Critical | RW | 2 bytes | Unit:1
16092 | Slave03 Outlet Port31 Over Power Critical | RW | 2 bytes | Unit:1
16093 | Slave03 Outlet Port32 Over Power Critical | RW | 2 bytes | Unit:1
16094 | Slave03 Outlet Port33 Over Power Critical | RW | 2 bytes | Unit:1
16095 | Slave03 Outlet Port34 Over Power Critical | RW | 2 bytes | Unit:1
16096 | Slave03 Outlet Port35 Over Power Critical | RW | 2 bytes | Unit:1
16097 | Slave03 Outlet Port36 Over Power Critical | RW | 2 bytes | Unit:1
16098 | Slave03 Outlet Port37 Over Power Critical | RW | 2 bytes | Unit:1
16099 | Slave03 Outlet Port38 Over Power Critical | RW | 2 bytes | Unit:1
16100 | Slave03 Outlet Port39 Over Power Critical | RW | 2 bytes | Unit:1
16101 | Slave03 Outlet Port40 Over Power Critical | RW | 2 bytes | Unit:1
16102 | Slave03 Outlet Port41 Over Power Critical | RW | 2 bytes | Unit:1
16103 | Slave03 Outlet Port42 Over Power Critical | RW | 2 bytes | Unit:1
16104 | Slave04 Outlet Port01 Over Power Critical | RW | 2 bytes | Unit:1
16105 | Slave04 Outlet Port02 Over Power Critical | RW | 2 bytes | Unit:1
16106 | Slave04 Outlet Port03 Over Power Critical | RW | 2 bytes | Unit:1
16107 | Slave04 Outlet Port04 Over Power Critical | RW | 2 bytes | Unit:1
16108 | Slave04 Outlet Port05 Over Power Critical | RW | 2 bytes | Unit:1
16109 | Slave04 Outlet Port06 Over Power Critical | RW | 2 bytes | Unit:1
16110 | Slave04 Outlet Port07 Over Power Critical | RW | 2 bytes | Unit:1
16111 | Slave04 Outlet Port08 Over Power Critical | RW | 2 bytes | Unit:1
16112 | Slave04 Outlet Port09 Over Power Critical | RW | 2 bytes | Unit:1
16113 | Slave04 Outlet Port10 Over Power Critical | RW | 2 bytes | Unit:1
16114 | Slave04 Outlet Port11 Over Power Critical | RW | 2 bytes | Unit:1
16115 | Slave04 Outlet Port12 Over Power Critical | RW | 2 bytes | Unit:1
16116 | Slave04 Outlet Port13 Over Power Critical | RW | 2 bytes | Unit:1
16117 | Slave04 Outlet Port14 Over Power Critical | RW | 2 bytes | Unit:1
16118 | Slave04 Outlet Port15 Over Power Critical | RW | 2 bytes | Unit:1
16119 | Slave04 Outlet Port16 Over Power Critical | RW | 2 bytes | Unit:1
16120 | Slave04 Outlet Port17 Over Power Critical | RW | 2 bytes | Unit:1
16121 | Slave04 Outlet Port18 Over Power Critical | RW | 2 bytes | Unit:1
16122 | Slave04 Outlet Port19 Over Power Critical | RW | 2 bytes | Unit:1
16123 | Slave04 Outlet Port20 Over Power Critical | RW | 2 bytes | Unit:1
16124 | Slave04 Outlet Port21 Over Power Critical | RW | 2 bytes | Unit:1
16125 | Slave04 Outlet Port22 Over Power Critical | RW | 2 bytes | Unit:1
16126 | Slave04 Outlet Port23 Over Power Critical | RW | 2 bytes | Unit:1
16127 | Slave04 Outlet Port24 Over Power Critical | RW | 2 bytes | Unit:1
16128 | Slave04 Outlet Port25 Over Power Critical | RW | 2 bytes | Unit:1
16129 | Slave04 Outlet Port26 Over Power Critical | RW | 2 bytes | Unit:1
16130 | Slave04 Outlet Port27 Over Power Critical | RW | 2 bytes | Unit:1
16131 | Slave04 Outlet Port28 Over Power Critical | RW | 2 bytes | Unit:1
16132 | Slave04 Outlet Port29 Over Power Critical | RW | 2 bytes | Unit:1
16133 | Slave04 Outlet Port30 Over Power Critical | RW | 2 bytes | Unit:1
16134 | Slave04 Outlet Port31 Over Power Critical | RW | 2 bytes | Unit:1
16135 | Slave04 Outlet Port32 Over Power Critical | RW | 2 bytes | Unit:1
16136 | Slave04 Outlet Port33 Over Power Critical | RW | 2 bytes | Unit:1
16137 | Slave04 Outlet Port34 Over Power Critical | RW | 2 bytes | Unit:1
16138 | Slave04 Outlet Port35 Over Power Critical | RW | 2 bytes | Unit:1
16139 | Slave04 Outlet Port36 Over Power Critical | RW | 2 bytes | Unit:1
16140 | Slave04 Outlet Port37 Over Power Critical | RW | 2 bytes | Unit:1
16141 | Slave04 Outlet Port38 Over Power Critical | RW | 2 bytes | Unit:1
16142 | Slave04 Outlet Port39 Over Power Critical | RW | 2 bytes | Unit:1
16143 | Slave04 Outlet Port40 Over Power Critical | RW | 2 bytes | Unit:1
16144 | Slave04 Outlet Port41 Over Power Critical | RW | 2 bytes | Unit:1
16145 | Slave04 Outlet Port42 Over Power Critical | RW | 2 bytes | Unit:1
16146 | Slave05 Outlet Port01 Over Power Critical | RW | 2 bytes | Unit:1
16147 | Slave05 Outlet Port02 Over Power Critical | RW | 2 bytes | Unit:1
16148 | Slave05 Outlet Port03 Over Power Critical | RW | 2 bytes | Unit:1
16149 | Slave05 Outlet Port04 Over Power Critical | RW | 2 bytes | Unit:1
16150 | Slave05 Outlet Port05 Over Power Critical | RW | 2 bytes | Unit:1
16151 | Slave05 Outlet Port06 Over Power Critical | RW | 2 bytes | Unit:1
16152 | Slave05 Outlet Port07 Over Power Critical | RW | 2 bytes | Unit:1
16153 | Slave05 Outlet Port08 Over Power Critical | RW | 2 bytes | Unit:1
16154 | Slave05 Outlet Port09 Over Power Critical | RW | 2 bytes | Unit:1
16155 | Slave05 Outlet Port10 Over Power Critical | RW | 2 bytes | Unit:1
16156 | Slave05 Outlet Port11 Over Power Critical | RW | 2 bytes | Unit:1
16157 | Slave05 Outlet Port12 Over Power Critical | RW | 2 bytes | Unit:1
16158 | Slave05 Outlet Port13 Over Power Critical | RW | 2 bytes | Unit:1
16159 | Slave05 Outlet Port14 Over Power Critical | RW | 2 bytes | Unit:1
16160 | Slave05 Outlet Port15 Over Power Critical | RW | 2 bytes | Unit:1
16161 | Slave05 Outlet Port16 Over Power Critical | RW | 2 bytes | Unit:1
16162 | Slave05 Outlet Port17 Over Power Critical | RW | 2 bytes | Unit:1
16163 | Slave05 Outlet Port18 Over Power Critical | RW | 2 bytes | Unit:1
16164 | Slave05 Outlet Port19 Over Power Critical | RW | 2 bytes | Unit:1
16165 | Slave05 Outlet Port20 Over Power Critical | RW | 2 bytes | Unit:1
16166 | Slave05 Outlet Port21 Over Power Critical | RW | 2 bytes | Unit:1
16167 | Slave05 Outlet Port22 Over Power Critical | RW | 2 bytes | Unit:1
16168 | Slave05 Outlet Port23 Over Power Critical | RW | 2 bytes | Unit:1
16169 | Slave05 Outlet Port24 Over Power Critical | RW | 2 bytes | Unit:1
16170 | Slave05 Outlet Port25 Over Power Critical | RW | 2 bytes | Unit:1
16171 | Slave05 Outlet Port26 Over Power Critical | RW | 2 bytes | Unit:1
16172 | Slave05 Outlet Port27 Over Power Critical | RW | 2 bytes | Unit:1
16173 | Slave05 Outlet Port28 Over Power Critical | RW | 2 bytes | Unit:1
16174 | Slave05 Outlet Port29 Over Power Critical | RW | 2 bytes | Unit:1
16175 | Slave05 Outlet Port30 Over Power Critical | RW | 2 bytes | Unit:1
16176 | Slave05 Outlet Port31 Over Power Critical | RW | 2 bytes | Unit:1
16177 | Slave05 Outlet Port32 Over Power Critical | RW | 2 bytes | Unit:1
16178 | Slave05 Outlet Port33 Over Power Critical | RW | 2 bytes | Unit:1
16179 | Slave05 Outlet Port34 Over Power Critical | RW | 2 bytes | Unit:1
16180 | Slave05 Outlet Port35 Over Power Critical | RW | 2 bytes | Unit:1
16181 | Slave05 Outlet Port36 Over Power Critical | RW | 2 bytes | Unit:1
16182 | Slave05 Outlet Port37 Over Power Critical | RW | 2 bytes | Unit:1
16183 | Slave05 Outlet Port38 Over Power Critical | RW | 2 bytes | Unit:1
16184 | Slave05 Outlet Port39 Over Power Critical | RW | 2 bytes | Unit:1
16185 | Slave05 Outlet Port40 Over Power Critical | RW | 2 bytes | Unit:1
16186 | Slave05 Outlet Port41 Over Power Critical | RW | 2 bytes | Unit:1
16187 | Slave05 Outlet Port42 Over Power Critical | RW | 2 bytes | Unit:1
16188 | Slave06 Outlet Port01 Over Power Critical | RW | 2 bytes | Unit:1
16189 | Slave06 Outlet Port02 Over Power Critical | RW | 2 bytes | Unit:1
16190 | Slave06 Outlet Port03 Over Power Critical | RW | 2 bytes | Unit:1
16191 | Slave06 Outlet Port04 Over Power Critical | RW | 2 bytes | Unit:1
16192 | Slave06 Outlet Port05 Over Power Critical | RW | 2 bytes | Unit:1
16193 | Slave06 Outlet Port06 Over Power Critical | RW | 2 bytes | Unit:1
16194 | Slave06 Outlet Port07 Over Power Critical | RW | 2 bytes | Unit:1
16195 | Slave06 Outlet Port08 Over Power Critical | RW | 2 bytes | Unit:1
16196 | Slave06 Outlet Port09 Over Power Critical | RW | 2 bytes | Unit:1
16197 | Slave06 Outlet Port10 Over Power Critical | RW | 2 bytes | Unit:1
16198 | Slave06 Outlet Port11 Over Power Critical | RW | 2 bytes | Unit:1
16199 | Slave06 Outlet Port12 Over Power Critical | RW | 2 bytes | Unit:1
16200 | Slave06 Outlet Port13 Over Power Critical | RW | 2 bytes | Unit:1
16201 | Slave06 Outlet Port14 Over Power Critical | RW | 2 bytes | Unit:1
16202 | Slave06 Outlet Port15 Over Power Critical | RW | 2 bytes | Unit:1
16203 | Slave06 Outlet Port16 Over Power Critical | RW | 2 bytes | Unit:1
16204 | Slave06 Outlet Port17 Over Power Critical | RW | 2 bytes | Unit:1
16205 | Slave06 Outlet Port18 Over Power Critical | RW | 2 bytes | Unit:1
16206 | Slave06 Outlet Port19 Over Power Critical | RW | 2 bytes | Unit:1
16207 | Slave06 Outlet Port20 Over Power Critical | RW | 2 bytes | Unit:1
16208 | Slave06 Outlet Port21 Over Power Critical | RW | 2 bytes | Unit:1
16209 | Slave06 Outlet Port22 Over Power Critical | RW | 2 bytes | Unit:1
16210 | Slave06 Outlet Port23 Over Power Critical | RW | 2 bytes | Unit:1
16211 | Slave06 Outlet Port24 Over Power Critical | RW | 2 bytes | Unit:1
16212 | Slave06 Outlet Port25 Over Power Critical | RW | 2 bytes | Unit:1
16213 | Slave06 Outlet Port26 Over Power Critical | RW | 2 bytes | Unit:1
16214 | Slave06 Outlet Port27 Over Power Critical | RW | 2 bytes | Unit:1
16215 | Slave06 Outlet Port28 Over Power Critical | RW | 2 bytes | Unit:1
16216 | Slave06 Outlet Port29 Over Power Critical | RW | 2 bytes | Unit:1
16217 | Slave06 Outlet Port30 Over Power Critical | RW | 2 bytes | Unit:1
16218 | Slave06 Outlet Port31 Over Power Critical | RW | 2 bytes | Unit:1
16219 | Slave06 Outlet Port32 Over Power Critical | RW | 2 bytes | Unit:1
16220 | Slave06 Outlet Port33 Over Power Critical | RW | 2 bytes | Unit:1
16221 | Slave06 Outlet Port34 Over Power Critical | RW | 2 bytes | Unit:1
16222 | Slave06 Outlet Port35 Over Power Critical | RW | 2 bytes | Unit:1
16223 | Slave06 Outlet Port36 Over Power Critical | RW | 2 bytes | Unit:1
16224 | Slave06 Outlet Port37 Over Power Critical | RW | 2 bytes | Unit:1
16225 | Slave06 Outlet Port38 Over Power Critical | RW | 2 bytes | Unit:1
16226 | Slave06 Outlet Port39 Over Power Critical | RW | 2 bytes | Unit:1
16227 | Slave06 Outlet Port40 Over Power Critical | RW | 2 bytes | Unit:1
16228 | Slave06 Outlet Port41 Over Power Critical | RW | 2 bytes | Unit:1
16229 | Slave06 Outlet Port42 Over Power Critical | RW | 2 bytes | Unit:1
16230 | Slave07 Outlet Port01 Over Power Critical | RW | 2 bytes | Unit:1
16231 | Slave07 Outlet Port02 Over Power Critical | RW | 2 bytes | Unit:1
16232 | Slave07 Outlet Port03 Over Power Critical | RW | 2 bytes | Unit:1
16233 | Slave07 Outlet Port04 Over Power Critical | RW | 2 bytes | Unit:1
16234 | Slave07 Outlet Port05 Over Power Critical | RW | 2 bytes | Unit:1
16235 | Slave07 Outlet Port06 Over Power Critical | RW | 2 bytes | Unit:1
16236 | Slave07 Outlet Port07 Over Power Critical | RW | 2 bytes | Unit:1
16237 | Slave07 Outlet Port08 Over Power Critical | RW | 2 bytes | Unit:1
16238 | Slave07 Outlet Port09 Over Power Critical | RW | 2 bytes | Unit:1
16239 | Slave07 Outlet Port10 Over Power Critical | RW | 2 bytes | Unit:1
16240 | Slave07 Outlet Port11 Over Power Critical | RW | 2 bytes | Unit:1
16241 | Slave07 Outlet Port12 Over Power Critical | RW | 2 bytes | Unit:1
16242 | Slave07 Outlet Port13 Over Power Critical | RW | 2 bytes | Unit:1
16243 | Slave07 Outlet Port14 Over Power Critical | RW | 2 bytes | Unit:1
16244 | Slave07 Outlet Port15 Over Power Critical | RW | 2 bytes | Unit:1
16245 | Slave07 Outlet Port16 Over Power Critical | RW | 2 bytes | Unit:1
16246 | Slave07 Outlet Port17 Over Power Critical | RW | 2 bytes | Unit:1
16247 | Slave07 Outlet Port18 Over Power Critical | RW | 2 bytes | Unit:1
16248 | Slave07 Outlet Port19 Over Power Critical | RW | 2 bytes | Unit:1
16249 | Slave07 Outlet Port20 Over Power Critical | RW | 2 bytes | Unit:1
16250 | Slave07 Outlet Port21 Over Power Critical | RW | 2 bytes | Unit:1
16251 | Slave07 Outlet Port22 Over Power Critical | RW | 2 bytes | Unit:1
16252 | Slave07 Outlet Port23 Over Power Critical | RW | 2 bytes | Unit:1
16253 | Slave07 Outlet Port24 Over Power Critical | RW | 2 bytes | Unit:1
16254 | Slave07 Outlet Port25 Over Power Critical | RW | 2 bytes | Unit:1
16255 | Slave07 Outlet Port26 Over Power Critical | RW | 2 bytes | Unit:1
16256 | Slave07 Outlet Port27 Over Power Critical | RW | 2 bytes | Unit:1
16257 | Slave07 Outlet Port28 Over Power Critical | RW | 2 bytes | Unit:1
16258 | Slave07 Outlet Port29 Over Power Critical | RW | 2 bytes | Unit:1
16259 | Slave07 Outlet Port30 Over Power Critical | RW | 2 bytes | Unit:1
16260 | Slave07 Outlet Port31 Over Power Critical | RW | 2 bytes | Unit:1
16261 | Slave07 Outlet Port32 Over Power Critical | RW | 2 bytes | Unit:1
16262 | Slave07 Outlet Port33 Over Power Critical | RW | 2 bytes | Unit:1
16263 | Slave07 Outlet Port34 Over Power Critical | RW | 2 bytes | Unit:1
16264 | Slave07 Outlet Port35 Over Power Critical | RW | 2 bytes | Unit:1
16265 | Slave07 Outlet Port36 Over Power Critical | RW | 2 bytes | Unit:1
16266 | Slave07 Outlet Port37 Over Power Critical | RW | 2 bytes | Unit:1
16267 | Slave07 Outlet Port38 Over Power Critical | RW | 2 bytes | Unit:1
16268 | Slave07 Outlet Port39 Over Power Critical | RW | 2 bytes | Unit:1
16269 | Slave07 Outlet Port40 Over Power Critical | RW | 2 bytes | Unit:1
16270 | Slave07 Outlet Port41 Over Power Critical | RW | 2 bytes | Unit:1
16271 | Slave07 Outlet Port42 Over Power Critical | RW | 2 bytes | Unit:1
16272 | Slave08 Outlet Port01 Over Power Critical | RW | 2 bytes | Unit:1
16273 | Slave08 Outlet Port02 Over Power Critical | RW | 2 bytes | Unit:1
16274 | Slave08 Outlet Port03 Over Power Critical | RW | 2 bytes | Unit:1
16275 | Slave08 Outlet Port04 Over Power Critical | RW | 2 bytes | Unit:1
16276 | Slave08 Outlet Port05 Over Power Critical | RW | 2 bytes | Unit:1
16277 | Slave08 Outlet Port06 Over Power Critical | RW | 2 bytes | Unit:1
16278 | Slave08 Outlet Port07 Over Power Critical | RW | 2 bytes | Unit:1
16279 | Slave08 Outlet Port08 Over Power Critical | RW | 2 bytes | Unit:1
16280 | Slave08 Outlet Port09 Over Power Critical | RW | 2 bytes | Unit:1
16281 | Slave08 Outlet Port10 Over Power Critical | RW | 2 bytes | Unit:1
16282 | Slave08 Outlet Port11 Over Power Critical | RW | 2 bytes | Unit:1
16283 | Slave08 Outlet Port12 Over Power Critical | RW | 2 bytes | Unit:1
16284 | Slave08 Outlet Port13 Over Power Critical | RW | 2 bytes | Unit:1
16285 | Slave08 Outlet Port14 Over Power Critical | RW | 2 bytes | Unit:1
16286 | Slave08 Outlet Port15 Over Power Critical | RW | 2 bytes | Unit:1
16287 | Slave08 Outlet Port16 Over Power Critical | RW | 2 bytes | Unit:1
16288 | Slave08 Outlet Port17 Over Power Critical | RW | 2 bytes | Unit:1
16289 | Slave08 Outlet Port18 Over Power Critical | RW | 2 bytes | Unit:1
16290 | Slave08 Outlet Port19 Over Power Critical | RW | 2 bytes | Unit:1
16291 | Slave08 Outlet Port20 Over Power Critical | RW | 2 bytes | Unit:1
16292 | Slave08 Outlet Port21 Over Power Critical | RW | 2 bytes | Unit:1
16293 | Slave08 Outlet Port22 Over Power Critical | RW | 2 bytes | Unit:1
16294 | Slave08 Outlet Port23 Over Power Critical | RW | 2 bytes | Unit:1
16295 | Slave08 Outlet Port24 Over Power Critical | RW | 2 bytes | Unit:1
16296 | Slave08 Outlet Port25 Over Power Critical | RW | 2 bytes | Unit:1
16297 | Slave08 Outlet Port26 Over Power Critical | RW | 2 bytes | Unit:1
16298 | Slave08 Outlet Port27 Over Power Critical | RW | 2 bytes | Unit:1
16299 | Slave08 Outlet Port28 Over Power Critical | RW | 2 bytes | Unit:1
16300 | Slave08 Outlet Port29 Over Power Critical | RW | 2 bytes | Unit:1
16301 | Slave08 Outlet Port30 Over Power Critical | RW | 2 bytes | Unit:1
16302 | Slave08 Outlet Port31 Over Power Critical | RW | 2 bytes | Unit:1
16303 | Slave08 Outlet Port32 Over Power Critical | RW | 2 bytes | Unit:1
16304 | Slave08 Outlet Port33 Over Power Critical | RW | 2 bytes | Unit:1
16305 | Slave08 Outlet Port34 Over Power Critical | RW | 2 bytes | Unit:1
16306 | Slave08 Outlet Port35 Over Power Critical | RW | 2 bytes | Unit:1
16307 | Slave08 Outlet Port36 Over Power Critical | RW | 2 bytes | Unit:1
16308 | Slave08 Outlet Port37 Over Power Critical | RW | 2 bytes | Unit:1
16309 | Slave08 Outlet Port38 Over Power Critical | RW | 2 bytes | Unit:1
16310 | Slave08 Outlet Port39 Over Power Critical | RW | 2 bytes | Unit:1
16311 | Slave08 Outlet Port40 Over Power Critical | RW | 2 bytes | Unit:1
16312 | Slave08 Outlet Port41 Over Power Critical | RW | 2 bytes | Unit:1
16313 | Slave08 Outlet Port42 Over Power Critical | RW | 2 bytes | Unit:1
16314 | Slave09 Outlet Port01 Over Power Critical | RW | 2 bytes | Unit:1
16315 | Slave09 Outlet Port02 Over Power Critical | RW | 2 bytes | Unit:1
16316 | Slave09 Outlet Port03 Over Power Critical | RW | 2 bytes | Unit:1
16317 | Slave09 Outlet Port04 Over Power Critical | RW | 2 bytes | Unit:1
16318 | Slave09 Outlet Port05 Over Power Critical | RW | 2 bytes | Unit:1
16319 | Slave09 Outlet Port06 Over Power Critical | RW | 2 bytes | Unit:1
16320 | Slave09 Outlet Port07 Over Power Critical | RW | 2 bytes | Unit:1
16321 | Slave09 Outlet Port08 Over Power Critical | RW | 2 bytes | Unit:1
16322 | Slave09 Outlet Port09 Over Power Critical | RW | 2 bytes | Unit:1
16323 | Slave09 Outlet Port10 Over Power Critical | RW | 2 bytes | Unit:1
16324 | Slave09 Outlet Port11 Over Power Critical | RW | 2 bytes | Unit:1
16325 | Slave09 Outlet Port12 Over Power Critical | RW | 2 bytes | Unit:1
16326 | Slave09 Outlet Port13 Over Power Critical | RW | 2 bytes | Unit:1
16327 | Slave09 Outlet Port14 Over Power Critical | RW | 2 bytes | Unit:1
16328 | Slave09 Outlet Port15 Over Power Critical | RW | 2 bytes | Unit:1
16329 | Slave09 Outlet Port16 Over Power Critical | RW | 2 bytes | Unit:1
16330 | Slave09 Outlet Port17 Over Power Critical | RW | 2 bytes | Unit:1
16331 | Slave09 Outlet Port18 Over Power Critical | RW | 2 bytes | Unit:1
16332 | Slave09 Outlet Port19 Over Power Critical | RW | 2 bytes | Unit:1
16333 | Slave09 Outlet Port20 Over Power Critical | RW | 2 bytes | Unit:1
16334 | Slave09 Outlet Port21 Over Power Critical | RW | 2 bytes | Unit:1
16335 | Slave09 Outlet Port22 Over Power Critical | RW | 2 bytes | Unit:1
16336 | Slave09 Outlet Port23 Over Power Critical | RW | 2 bytes | Unit:1
16337 | Slave09 Outlet Port24 Over Power Critical | RW | 2 bytes | Unit:1
16338 | Slave09 Outlet Port25 Over Power Critical | RW | 2 bytes | Unit:1
16339 | Slave09 Outlet Port26 Over Power Critical | RW | 2 bytes | Unit:1
16340 | Slave09 Outlet Port27 Over Power Critical | RW | 2 bytes | Unit:1
16341 | Slave09 Outlet Port28 Over Power Critical | RW | 2 bytes | Unit:1
16342 | Slave09 Outlet Port29 Over Power Critical | RW | 2 bytes | Unit:1
16343 | Slave09 Outlet Port30 Over Power Critical | RW | 2 bytes | Unit:1
16344 | Slave09 Outlet Port31 Over Power Critical | RW | 2 bytes | Unit:1
16345 | Slave09 Outlet Port32 Over Power Critical | RW | 2 bytes | Unit:1
16346 | Slave09 Outlet Port33 Over Power Critical | RW | 2 bytes | Unit:1
16347 | Slave09 Outlet Port34 Over Power Critical | RW | 2 bytes | Unit:1
16348 | Slave09 Outlet Port35 Over Power Critical | RW | 2 bytes | Unit:1
16349 | Slave09 Outlet Port36 Over Power Critical | RW | 2 bytes | Unit:1
16350 | Slave09 Outlet Port37 Over Power Critical | RW | 2 bytes | Unit:1
16351 | Slave09 Outlet Port38 Over Power Critical | RW | 2 bytes | Unit:1
16352 | Slave09 Outlet Port39 Over Power Critical | RW | 2 bytes | Unit:1
16353 | Slave09 Outlet Port40 Over Power Critical | RW | 2 bytes | Unit:1
16354 | Slave09 Outlet Port41 Over Power Critical | RW | 2 bytes | Unit:1
16355 | Slave09 Outlet Port42 Over Power Critical | RW | 2 bytes | Unit:1
16356 | Slave10 Outlet Port01 Over Power Critical | RW | 2 bytes | Unit:1
16357 | Slave10 Outlet Port02 Over Power Critical | RW | 2 bytes | Unit:1
16358 | Slave10 Outlet Port03 Over Power Critical | RW | 2 bytes | Unit:1
16359 | Slave10 Outlet Port04 Over Power Critical | RW | 2 bytes | Unit:1
16360 | Slave10 Outlet Port05 Over Power Critical | RW | 2 bytes | Unit:1
16361 | Slave10 Outlet Port06 Over Power Critical | RW | 2 bytes | Unit:1
16362 | Slave10 Outlet Port07 Over Power Critical | RW | 2 bytes | Unit:1
16363 | Slave10 Outlet Port08 Over Power Critical | RW | 2 bytes | Unit:1
16364 | Slave10 Outlet Port09 Over Power Critical | RW | 2 bytes | Unit:1
16365 | Slave10 Outlet Port10 Over Power Critical | RW | 2 bytes | Unit:1
16366 | Slave10 Outlet Port11 Over Power Critical | RW | 2 bytes | Unit:1
16367 | Slave10 Outlet Port12 Over Power Critical | RW | 2 bytes | Unit:1
16368 | Slave10 Outlet Port13 Over Power Critical | RW | 2 bytes | Unit:1
16369 | Slave10 Outlet Port14 Over Power Critical | RW | 2 bytes | Unit:1
16370 | Slave10 Outlet Port15 Over Power Critical | RW | 2 bytes | Unit:1
16371 | Slave10 Outlet Port16 Over Power Critical | RW | 2 bytes | Unit:1
16372 | Slave10 Outlet Port17 Over Power Critical | RW | 2 bytes | Unit:1
16373 | Slave10 Outlet Port18 Over Power Critical | RW | 2 bytes | Unit:1
16374 | Slave10 Outlet Port19 Over Power Critical | RW | 2 bytes | Unit:1
16375 | Slave10 Outlet Port20 Over Power Critical | RW | 2 bytes | Unit:1
16376 | Slave10 Outlet Port21 Over Power Critical | RW | 2 bytes | Unit:1
16377 | Slave10 Outlet Port22 Over Power Critical | RW | 2 bytes | Unit:1
16378 | Slave10 Outlet Port23 Over Power Critical | RW | 2 bytes | Unit:1
16379 | Slave10 Outlet Port24 Over Power Critical | RW | 2 bytes | Unit:1
16380 | Slave10 Outlet Port25 Over Power Critical | RW | 2 bytes | Unit:1
16381 | Slave10 Outlet Port26 Over Power Critical | RW | 2 bytes | Unit:1
16382 | Slave10 Outlet Port27 Over Power Critical | RW | 2 bytes | Unit:1
16383 | Slave10 Outlet Port28 Over Power Critical | RW | 2 bytes | Unit:1
16384 | Slave10 Outlet Port29 Over Power Critical | RW | 2 bytes | Unit:1
16385 | Slave10 Outlet Port30 Over Power Critical | RW | 2 bytes | Unit:1
16386 | Slave10 Outlet Port31 Over Power Critical | RW | 2 bytes | Unit:1
16387 | Slave10 Outlet Port32 Over Power Critical | RW | 2 bytes | Unit:1
16388 | Slave10 Outlet Port33 Over Power Critical | RW | 2 bytes | Unit:1
16389 | Slave10 Outlet Port34 Over Power Critical | RW | 2 bytes | Unit:1
16390 | Slave10 Outlet Port35 Over Power Critical | RW | 2 bytes | Unit:1
16391 | Slave10 Outlet Port36 Over Power Critical | RW | 2 bytes | Unit:1
16392 | Slave10 Outlet Port37 Over Power Critical | RW | 2 bytes | Unit:1
16393 | Slave10 Outlet Port38 Over Power Critical | RW | 2 bytes | Unit:1
16394 | Slave10 Outlet Port39 Over Power Critical | RW | 2 bytes | Unit:1
16395 | Slave10 Outlet Port40 Over Power Critical | RW | 2 bytes | Unit:1
16396 | Slave10 Outlet Port41 Over Power Critical | RW | 2 bytes | Unit:1
16397 | Slave10 Outlet Port42 Over Power Critical | RW | 2 bytes | Unit:1
16398 | Slave11 Outlet Port01 Over Power Critical | RW | 2 bytes | Unit:1
16399 | Slave11 Outlet Port02 Over Power Critical | RW | 2 bytes | Unit:1
16400 | Slave11 Outlet Port03 Over Power Critical | RW | 2 bytes | Unit:1
16401 | Slave11 Outlet Port04 Over Power Critical | RW | 2 bytes | Unit:1
16402 | Slave11 Outlet Port05 Over Power Critical | RW | 2 bytes | Unit:1
16403 | Slave11 Outlet Port06 Over Power Critical | RW | 2 bytes | Unit:1
16404 | Slave11 Outlet Port07 Over Power Critical | RW | 2 bytes | Unit:1
16405 | Slave11 Outlet Port08 Over Power Critical | RW | 2 bytes | Unit:1
16406 | Slave11 Outlet Port09 Over Power Critical | RW | 2 bytes | Unit:1
16407 | Slave11 Outlet Port10 Over Power Critical | RW | 2 bytes | Unit:1
16408 | Slave11 Outlet Port11 Over Power Critical | RW | 2 bytes | Unit:1
16409 | Slave11 Outlet Port12 Over Power Critical | RW | 2 bytes | Unit:1
16410 | Slave11 Outlet Port13 Over Power Critical | RW | 2 bytes | Unit:1
16411 | Slave11 Outlet Port14 Over Power Critical | RW | 2 bytes | Unit:1
16412 | Slave11 Outlet Port15 Over Power Critical | RW | 2 bytes | Unit:1
16413 | Slave11 Outlet Port16 Over Power Critical | RW | 2 bytes | Unit:1
16414 | Slave11 Outlet Port17 Over Power Critical | RW | 2 bytes | Unit:1
16415 | Slave11 Outlet Port18 Over Power Critical | RW | 2 bytes | Unit:1
16416 | Slave11 Outlet Port19 Over Power Critical | RW | 2 bytes | Unit:1
16417 | Slave11 Outlet Port20 Over Power Critical | RW | 2 bytes | Unit:1
16418 | Slave11 Outlet Port21 Over Power Critical | RW | 2 bytes | Unit:1
16419 | Slave11 Outlet Port22 Over Power Critical | RW | 2 bytes | Unit:1
16420 | Slave11 Outlet Port23 Over Power Critical | RW | 2 bytes | Unit:1
16421 | Slave11 Outlet Port24 Over Power Critical | RW | 2 bytes | Unit:1
16422 | Slave11 Outlet Port25 Over Power Critical | RW | 2 bytes | Unit:1
16423 | Slave11 Outlet Port26 Over Power Critical | RW | 2 bytes | Unit:1
16424 | Slave11 Outlet Port27 Over Power Critical | RW | 2 bytes | Unit:1
16425 | Slave11 Outlet Port28 Over Power Critical | RW | 2 bytes | Unit:1
16426 | Slave11 Outlet Port29 Over Power Critical | RW | 2 bytes | Unit:1
16427 | Slave11 Outlet Port30 Over Power Critical | RW | 2 bytes | Unit:1
16428 | Slave11 Outlet Port31 Over Power Critical | RW | 2 bytes | Unit:1
16429 | Slave11 Outlet Port32 Over Power Critical | RW | 2 bytes | Unit:1
16430 | Slave11 Outlet Port33 Over Power Critical | RW | 2 bytes | Unit:1
16431 | Slave11 Outlet Port34 Over Power Critical | RW | 2 bytes | Unit:1
16432 | Slave11 Outlet Port35 Over Power Critical | RW | 2 bytes | Unit:1
16433 | Slave11 Outlet Port36 Over Power Critical | RW | 2 bytes | Unit:1
16434 | Slave11 Outlet Port37 Over Power Critical | RW | 2 bytes | Unit:1
16435 | Slave11 Outlet Port38 Over Power Critical | RW | 2 bytes | Unit:1
16436 | Slave11 Outlet Port39 Over Power Critical | RW | 2 bytes | Unit:1
16437 | Slave11 Outlet Port40 Over Power Critical | RW | 2 bytes | Unit:1
16438 | Slave11 Outlet Port41 Over Power Critical | RW | 2 bytes | Unit:1
16439 | Slave11 Outlet Port42 Over Power Critical | RW | 2 bytes | Unit:1
16440 | Slave12 Outlet Port01 Over Power Critical | RW | 2 bytes | Unit:1
16441 | Slave12 Outlet Port02 Over Power Critical | RW | 2 bytes | Unit:1
16442 | Slave12 Outlet Port03 Over Power Critical | RW | 2 bytes | Unit:1
16443 | Slave12 Outlet Port04 Over Power Critical | RW | 2 bytes | Unit:1
16444 | Slave12 Outlet Port05 Over Power Critical | RW | 2 bytes | Unit:1
16445 | Slave12 Outlet Port06 Over Power Critical | RW | 2 bytes | Unit:1
16446 | Slave12 Outlet Port07 Over Power Critical | RW | 2 bytes | Unit:1
16447 | Slave12 Outlet Port08 Over Power Critical | RW | 2 bytes | Unit:1
16448 | Slave12 Outlet Port09 Over Power Critical | RW | 2 bytes | Unit:1
16449 | Slave12 Outlet Port10 Over Power Critical | RW | 2 bytes | Unit:1
16450 | Slave12 Outlet Port11 Over Power Critical | RW | 2 bytes | Unit:1
16451 | Slave12 Outlet Port12 Over Power Critical | RW | 2 bytes | Unit:1
16452 | Slave12 Outlet Port13 Over Power Critical | RW | 2 bytes | Unit:1
16453 | Slave12 Outlet Port14 Over Power Critical | RW | 2 bytes | Unit:1
16454 | Slave12 Outlet Port15 Over Power Critical | RW | 2 bytes | Unit:1
16455 | Slave12 Outlet Port16 Over Power Critical | RW | 2 bytes | Unit:1
16456 | Slave12 Outlet Port17 Over Power Critical | RW | 2 bytes | Unit:1
16457 | Slave12 Outlet Port18 Over Power Critical | RW | 2 bytes | Unit:1
16458 | Slave12 Outlet Port19 Over Power Critical | RW | 2 bytes | Unit:1
16459 | Slave12 Outlet Port20 Over Power Critical | RW | 2 bytes | Unit:1
16460 | Slave12 Outlet Port21 Over Power Critical | RW | 2 bytes | Unit:1
16461 | Slave12 Outlet Port22 Over Power Critical | RW | 2 bytes | Unit:1
16462 | Slave12 Outlet Port23 Over Power Critical | RW | 2 bytes | Unit:1
16463 | Slave12 Outlet Port24 Over Power Critical | RW | 2 bytes | Unit:1
16464 | Slave12 Outlet Port25 Over Power Critical | RW | 2 bytes | Unit:1
16465 | Slave12 Outlet Port26 Over Power Critical | RW | 2 bytes | Unit:1
16466 | Slave12 Outlet Port27 Over Power Critical | RW | 2 bytes | Unit:1
16467 | Slave12 Outlet Port28 Over Power Critical | RW | 2 bytes | Unit:1
16468 | Slave12 Outlet Port29 Over Power Critical | RW | 2 bytes | Unit:1
16469 | Slave12 Outlet Port30 Over Power Critical | RW | 2 bytes | Unit:1
16470 | Slave12 Outlet Port31 Over Power Critical | RW | 2 bytes | Unit:1
16471 | Slave12 Outlet Port32 Over Power Critical | RW | 2 bytes | Unit:1
16472 | Slave12 Outlet Port33 Over Power Critical | RW | 2 bytes | Unit:1
16473 | Slave12 Outlet Port34 Over Power Critical | RW | 2 bytes | Unit:1
16474 | Slave12 Outlet Port35 Over Power Critical | RW | 2 bytes | Unit:1
16475 | Slave12 Outlet Port36 Over Power Critical | RW | 2 bytes | Unit:1
16476 | Slave12 Outlet Port37 Over Power Critical | RW | 2 bytes | Unit:1
16477 | Slave12 Outlet Port38 Over Power Critical | RW | 2 bytes | Unit:1
16478 | Slave12 Outlet Port39 Over Power Critical | RW | 2 bytes | Unit:1
16479 | Slave12 Outlet Port40 Over Power Critical | RW | 2 bytes | Unit:1
16480 | Slave12 Outlet Port41 Over Power Critical | RW | 2 bytes | Unit:1
16481 | Slave12 Outlet Port42 Over Power Critical | RW | 2 bytes | Unit:1
16482 | Slave13 Outlet Port01 Over Power Critical | RW | 2 bytes | Unit:1
16483 | Slave13 Outlet Port02 Over Power Critical | RW | 2 bytes | Unit:1
16484 | Slave13 Outlet Port03 Over Power Critical | RW | 2 bytes | Unit:1
16485 | Slave13 Outlet Port04 Over Power Critical | RW | 2 bytes | Unit:1
16486 | Slave13 Outlet Port05 Over Power Critical | RW | 2 bytes | Unit:1
16487 | Slave13 Outlet Port06 Over Power Critical | RW | 2 bytes | Unit:1
16488 | Slave13 Outlet Port07 Over Power Critical | RW | 2 bytes | Unit:1
16489 | Slave13 Outlet Port08 Over Power Critical | RW | 2 bytes | Unit:1
16490 | Slave13 Outlet Port09 Over Power Critical | RW | 2 bytes | Unit:1
16491 | Slave13 Outlet Port10 Over Power Critical | RW | 2 bytes | Unit:1
16492 | Slave13 Outlet Port11 Over Power Critical | RW | 2 bytes | Unit:1
16493 | Slave13 Outlet Port12 Over Power Critical | RW | 2 bytes | Unit:1
16494 | Slave13 Outlet Port13 Over Power Critical | RW | 2 bytes | Unit:1
16495 | Slave13 Outlet Port14 Over Power Critical | RW | 2 bytes | Unit:1
16496 | Slave13 Outlet Port15 Over Power Critical | RW | 2 bytes | Unit:1
16497 | Slave13 Outlet Port16 Over Power Critical | RW | 2 bytes | Unit:1
16498 | Slave13 Outlet Port17 Over Power Critical | RW | 2 bytes | Unit:1
16499 | Slave13 Outlet Port18 Over Power Critical | RW | 2 bytes | Unit:1
16500 | Slave13 Outlet Port19 Over Power Critical | RW | 2 bytes | Unit:1
16501 | Slave13 Outlet Port20 Over Power Critical | RW | 2 bytes | Unit:1
16502 | Slave13 Outlet Port21 Over Power Critical | RW | 2 bytes | Unit:1
16503 | Slave13 Outlet Port22 Over Power Critical | RW | 2 bytes | Unit:1
16504 | Slave13 Outlet Port23 Over Power Critical | RW | 2 bytes | Unit:1
16505 | Slave13 Outlet Port24 Over Power Critical | RW | 2 bytes | Unit:1
16506 | Slave13 Outlet Port25 Over Power Critical | RW | 2 bytes | Unit:1
16507 | Slave13 Outlet Port26 Over Power Critical | RW | 2 bytes | Unit:1
16508 | Slave13 Outlet Port27 Over Power Critical | RW | 2 bytes | Unit:1
16509 | Slave13 Outlet Port28 Over Power Critical | RW | 2 bytes | Unit:1
16510 | Slave13 Outlet Port29 Over Power Critical | RW | 2 bytes | Unit:1
16511 | Slave13 Outlet Port30 Over Power Critical | RW | 2 bytes | Unit:1
16512 | Slave13 Outlet Port31 Over Power Critical | RW | 2 bytes | Unit:1
16513 | Slave13 Outlet Port32 Over Power Critical | RW | 2 bytes | Unit:1
16514 | Slave13 Outlet Port33 Over Power Critical | RW | 2 bytes | Unit:1
16515 | Slave13 Outlet Port34 Over Power Critical | RW | 2 bytes | Unit:1
16516 | Slave13 Outlet Port35 Over Power Critical | RW | 2 bytes | Unit:1
16517 | Slave13 Outlet Port36 Over Power Critical | RW | 2 bytes | Unit:1
16518 | Slave13 Outlet Port37 Over Power Critical | RW | 2 bytes | Unit:1
16519 | Slave13 Outlet Port38 Over Power Critical | RW | 2 bytes | Unit:1
16520 | Slave13 Outlet Port39 Over Power Critical | RW | 2 bytes | Unit:1
16521 | Slave13 Outlet Port40 Over Power Critical | RW | 2 bytes | Unit:1
16522 | Slave13 Outlet Port41 Over Power Critical | RW | 2 bytes | Unit:1
16523 | Slave13 Outlet Port42 Over Power Critical | RW | 2 bytes | Unit:1
16524 | Slave14 Outlet Port01 Over Power Critical | RW | 2 bytes | Unit:1
16525 | Slave14 Outlet Port02 Over Power Critical | RW | 2 bytes | Unit:1
16526 | Slave14 Outlet Port03 Over Power Critical | RW | 2 bytes | Unit:1
16527 | Slave14 Outlet Port04 Over Power Critical | RW | 2 bytes | Unit:1
16528 | Slave14 Outlet Port05 Over Power Critical | RW | 2 bytes | Unit:1
16529 | Slave14 Outlet Port06 Over Power Critical | RW | 2 bytes | Unit:1
16530 | Slave14 Outlet Port07 Over Power Critical | RW | 2 bytes | Unit:1
16531 | Slave14 Outlet Port08 Over Power Critical | RW | 2 bytes | Unit:1
16532 | Slave14 Outlet Port09 Over Power Critical | RW | 2 bytes | Unit:1
16533 | Slave14 Outlet Port10 Over Power Critical | RW | 2 bytes | Unit:1
16534 | Slave14 Outlet Port11 Over Power Critical | RW | 2 bytes | Unit:1
16535 | Slave14 Outlet Port12 Over Power Critical | RW | 2 bytes | Unit:1
16536 | Slave14 Outlet Port13 Over Power Critical | RW | 2 bytes | Unit:1
16537 | Slave14 Outlet Port14 Over Power Critical | RW | 2 bytes | Unit:1
16538 | Slave14 Outlet Port15 Over Power Critical | RW | 2 bytes | Unit:1
16539 | Slave14 Outlet Port16 Over Power Critical | RW | 2 bytes | Unit:1
16540 | Slave14 Outlet Port17 Over Power Critical | RW | 2 bytes | Unit:1
16541 | Slave14 Outlet Port18 Over Power Critical | RW | 2 bytes | Unit:1
16542 | Slave14 Outlet Port19 Over Power Critical | RW | 2 bytes | Unit:1
16543 | Slave14 Outlet Port20 Over Power Critical | RW | 2 bytes | Unit:1
16544 | Slave14 Outlet Port21 Over Power Critical | RW | 2 bytes | Unit:1
16545 | Slave14 Outlet Port22 Over Power Critical | RW | 2 bytes | Unit:1
16546 | Slave14 Outlet Port23 Over Power Critical | RW | 2 bytes | Unit:1
16547 | Slave14 Outlet Port24 Over Power Critical | RW | 2 bytes | Unit:1
16548 | Slave14 Outlet Port25 Over Power Critical | RW | 2 bytes | Unit:1
16549 | Slave14 Outlet Port26 Over Power Critical | RW | 2 bytes | Unit:1
16550 | Slave14 Outlet Port27 Over Power Critical | RW | 2 bytes | Unit:1
16551 | Slave14 Outlet Port28 Over Power Critical | RW | 2 bytes | Unit:1
16552 | Slave14 Outlet Port29 Over Power Critical | RW | 2 bytes | Unit:1
16553 | Slave14 Outlet Port30 Over Power Critical | RW | 2 bytes | Unit:1
16554 | Slave14 Outlet Port31 Over Power Critical | RW | 2 bytes | Unit:1
16555 | Slave14 Outlet Port32 Over Power Critical | RW | 2 bytes | Unit:1
16556 | Slave14 Outlet Port33 Over Power Critical | RW | 2 bytes | Unit:1
16557 | Slave14 Outlet Port34 Over Power Critical | RW | 2 bytes | Unit:1
16558 | Slave14 Outlet Port35 Over Power Critical | RW | 2 bytes | Unit:1
16559 | Slave14 Outlet Port36 Over Power Critical | RW | 2 bytes | Unit:1
16560 | Slave14 Outlet Port37 Over Power Critical | RW | 2 bytes | Unit:1
16561 | Slave14 Outlet Port38 Over Power Critical | RW | 2 bytes | Unit:1
16562 | Slave14 Outlet Port39 Over Power Critical | RW | 2 bytes | Unit:1
16563 | Slave14 Outlet Port40 Over Power Critical | RW | 2 bytes | Unit:1
16564 | Slave14 Outlet Port41 Over Power Critical | RW | 2 bytes | Unit:1
16565 | Slave14 Outlet Port42 Over Power Critical | RW | 2 bytes | Unit:1
16566 | Slave15 Outlet Port01 Over Power Critical | RW | 2 bytes | Unit:1
16567 | Slave15 Outlet Port02 Over Power Critical | RW | 2 bytes | Unit:1
16568 | Slave15 Outlet Port03 Over Power Critical | RW | 2 bytes | Unit:1
16569 | Slave15 Outlet Port04 Over Power Critical | RW | 2 bytes | Unit:1
16570 | Slave15 Outlet Port05 Over Power Critical | RW | 2 bytes | Unit:1
16571 | Slave15 Outlet Port06 Over Power Critical | RW | 2 bytes | Unit:1
16572 | Slave15 Outlet Port07 Over Power Critical | RW | 2 bytes | Unit:1
16573 | Slave15 Outlet Port08 Over Power Critical | RW | 2 bytes | Unit:1
16574 | Slave15 Outlet Port09 Over Power Critical | RW | 2 bytes | Unit:1
16575 | Slave15 Outlet Port10 Over Power Critical | RW | 2 bytes | Unit:1
16576 | Slave15 Outlet Port11 Over Power Critical | RW | 2 bytes | Unit:1
16577 | Slave15 Outlet Port12 Over Power Critical | RW | 2 bytes | Unit:1
16578 | Slave15 Outlet Port13 Over Power Critical | RW | 2 bytes | Unit:1
16579 | Slave15 Outlet Port14 Over Power Critical | RW | 2 bytes | Unit:1
16580 | Slave15 Outlet Port15 Over Power Critical | RW | 2 bytes | Unit:1
16581 | Slave15 Outlet Port16 Over Power Critical | RW | 2 bytes | Unit:1
16582 | Slave15 Outlet Port17 Over Power Critical | RW | 2 bytes | Unit:1
16583 | Slave15 Outlet Port18 Over Power Critical | RW | 2 bytes | Unit:1
16584 | Slave15 Outlet Port19 Over Power Critical | RW | 2 bytes | Unit:1
16585 | Slave15 Outlet Port20 Over Power Critical | RW | 2 bytes | Unit:1
16586 | Slave15 Outlet Port21 Over Power Critical | RW | 2 bytes | Unit:1
16587 | Slave15 Outlet Port22 Over Power Critical | RW | 2 bytes | Unit:1
16588 | Slave15 Outlet Port23 Over Power Critical | RW | 2 bytes | Unit:1
16589 | Slave15 Outlet Port24 Over Power Critical | RW | 2 bytes | Unit:1
16590 | Slave15 Outlet Port25 Over Power Critical | RW | 2 bytes | Unit:1
16591 | Slave15 Outlet Port26 Over Power Critical | RW | 2 bytes | Unit:1
16592 | Slave15 Outlet Port27 Over Power Critical | RW | 2 bytes | Unit:1
16593 | Slave15 Outlet Port28 Over Power Critical | RW | 2 bytes | Unit:1
16594 | Slave15 Outlet Port29 Over Power Critical | RW | 2 bytes | Unit:1
16595 | Slave15 Outlet Port30 Over Power Critical | RW | 2 bytes | Unit:1
16596 | Slave15 Outlet Port31 Over Power Critical | RW | 2 bytes | Unit:1
16597 | Slave15 Outlet Port32 Over Power Critical | RW | 2 bytes | Unit:1
16598 | Slave15 Outlet Port33 Over Power Critical | RW | 2 bytes | Unit:1
16599 | Slave15 Outlet Port34 Over Power Critical | RW | 2 bytes | Unit:1
16600 | Slave15 Outlet Port35 Over Power Critical | RW | 2 bytes | Unit:1
16601 | Slave15 Outlet Port36 Over Power Critical | RW | 2 bytes | Unit:1
16602 | Slave15 Outlet Port37 Over Power Critical | RW | 2 bytes | Unit:1
16603 | Slave15 Outlet Port38 Over Power Critical | RW | 2 bytes | Unit:1
16604 | Slave15 Outlet Port39 Over Power Critical | RW | 2 bytes | Unit:1
16605 | Slave15 Outlet Port40 Over Power Critical | RW | 2 bytes | Unit:1
16606 | Slave15 Outlet Port41 Over Power Critical | RW | 2 bytes | Unit:1
16607 | Slave15 Outlet Port42 Over Power Critical | RW | 2 bytes | Unit:1
16608 | Master Outlet Port01 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16609 | Master Outlet Port02 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16610 | Master Outlet Port03 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16611 | Master Outlet Port04 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16612 | Master Outlet Port05 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16613 | Master Outlet Port06 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16614 | Master Outlet Port07 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16615 | Master Outlet Port08 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16616 | Master Outlet Port09 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16617 | Master Outlet Port10 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16618 | Master Outlet Port11 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16619 | Master Outlet Port12 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16620 | Master Outlet Port13 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16621 | Master Outlet Port14 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16622 | Master Outlet Port15 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16623 | Master Outlet Port16 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16624 | Master Outlet Port17 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16625 | Master Outlet Port18 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16626 | Master Outlet Port19 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16627 | Master Outlet Port20 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16628 | Master Outlet Port21 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16629 | Master Outlet Port22 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16630 | Master Outlet Port23 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16631 | Master Outlet Port24 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16632 | Master Outlet Port25 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16633 | Master Outlet Port26 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16634 | Master Outlet Port27 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16635 | Master Outlet Port28 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16636 | Master Outlet Port29 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16637 | Master Outlet Port30 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16638 | Master Outlet Port31 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16639 | Master Outlet Port32 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16640 | Master Outlet Port33 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16641 | Master Outlet Port34 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16642 | Master Outlet Port35 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16643 | Master Outlet Port36 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16644 | Master Outlet Port37 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16645 | Master Outlet Port38 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16646 | Master Outlet Port39 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16647 | Master Outlet Port40 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16648 | Master Outlet Port41 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16649 | Master Outlet Port42 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16650 | Slave01 Outlet Port01 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16651 | Slave01 Outlet Port02 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16652 | Slave01 Outlet Port03 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16653 | Slave01 Outlet Port04 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16654 | Slave01 Outlet Port05 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16655 | Slave01 Outlet Port06 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16656 | Slave01 Outlet Port07 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16657 | Slave01 Outlet Port08 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16658 | Slave01 Outlet Port09 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16659 | Slave01 Outlet Port10 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16660 | Slave01 Outlet Port11 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16661 | Slave01 Outlet Port12 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16662 | Slave01 Outlet Port13 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16663 | Slave01 Outlet Port14 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16664 | Slave01 Outlet Port15 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16665 | Slave01 Outlet Port16 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16666 | Slave01 Outlet Port17 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16667 | Slave01 Outlet Port18 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16668 | Slave01 Outlet Port19 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16669 | Slave01 Outlet Port20 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16670 | Slave01 Outlet Port21 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16671 | Slave01 Outlet Port22 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16672 | Slave01 Outlet Port23 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16673 | Slave01 Outlet Port24 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16674 | Slave01 Outlet Port25 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16675 | Slave01 Outlet Port26 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16676 | Slave01 Outlet Port27 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16677 | Slave01 Outlet Port28 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16678 | Slave01 Outlet Port29 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16679 | Slave01 Outlet Port30 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16680 | Slave01 Outlet Port31 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16681 | Slave01 Outlet Port32 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16682 | Slave01 Outlet Port33 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16683 | Slave01 Outlet Port34 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16684 | Slave01 Outlet Port35 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16685 | Slave01 Outlet Port36 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16686 | Slave01 Outlet Port37 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16687 | Slave01 Outlet Port38 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16688 | Slave01 Outlet Port39 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16689 | Slave01 Outlet Port40 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16690 | Slave01 Outlet Port41 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16691 | Slave01 Outlet Port42 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16692 | Slave02 Outlet Port01 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16693 | Slave02 Outlet Port02 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16694 | Slave02 Outlet Port03 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16695 | Slave02 Outlet Port04 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16696 | Slave02 Outlet Port05 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16697 | Slave02 Outlet Port06 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16698 | Slave02 Outlet Port07 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16699 | Slave02 Outlet Port08 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16700 | Slave02 Outlet Port09 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16701 | Slave02 Outlet Port10 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16702 | Slave02 Outlet Port11 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16703 | Slave02 Outlet Port12 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16704 | Slave02 Outlet Port13 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16705 | Slave02 Outlet Port14 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16706 | Slave02 Outlet Port15 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16707 | Slave02 Outlet Port16 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16708 | Slave02 Outlet Port17 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16709 | Slave02 Outlet Port18 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16710 | Slave02 Outlet Port19 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16711 | Slave02 Outlet Port20 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16712 | Slave02 Outlet Port21 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16713 | Slave02 Outlet Port22 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16714 | Slave02 Outlet Port23 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16715 | Slave02 Outlet Port24 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16716 | Slave02 Outlet Port25 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16717 | Slave02 Outlet Port26 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16718 | Slave02 Outlet Port27 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16719 | Slave02 Outlet Port28 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16720 | Slave02 Outlet Port29 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16721 | Slave02 Outlet Port30 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16722 | Slave02 Outlet Port31 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16723 | Slave02 Outlet Port32 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16724 | Slave02 Outlet Port33 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16725 | Slave02 Outlet Port34 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16726 | Slave02 Outlet Port35 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16727 | Slave02 Outlet Port36 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16728 | Slave02 Outlet Port37 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16729 | Slave02 Outlet Port38 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16730 | Slave02 Outlet Port39 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16731 | Slave02 Outlet Port40 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16732 | Slave02 Outlet Port41 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16733 | Slave02 Outlet Port42 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16734 | Slave03 Outlet Port01 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16735 | Slave03 Outlet Port02 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16736 | Slave03 Outlet Port03 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16737 | Slave03 Outlet Port04 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16738 | Slave03 Outlet Port05 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16739 | Slave03 Outlet Port06 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16740 | Slave03 Outlet Port07 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16741 | Slave03 Outlet Port08 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16742 | Slave03 Outlet Port09 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16743 | Slave03 Outlet Port10 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16744 | Slave03 Outlet Port11 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16745 | Slave03 Outlet Port12 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16746 | Slave03 Outlet Port13 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16747 | Slave03 Outlet Port14 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16748 | Slave03 Outlet Port15 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16749 | Slave03 Outlet Port16 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16750 | Slave03 Outlet Port17 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16751 | Slave03 Outlet Port18 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16752 | Slave03 Outlet Port19 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16753 | Slave03 Outlet Port20 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16754 | Slave03 Outlet Port21 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16755 | Slave03 Outlet Port22 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16756 | Slave03 Outlet Port23 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16757 | Slave03 Outlet Port24 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16758 | Slave03 Outlet Port25 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16759 | Slave03 Outlet Port26 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16760 | Slave03 Outlet Port27 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16761 | Slave03 Outlet Port28 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16762 | Slave03 Outlet Port29 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16763 | Slave03 Outlet Port30 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16764 | Slave03 Outlet Port31 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16765 | Slave03 Outlet Port32 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16766 | Slave03 Outlet Port33 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16767 | Slave03 Outlet Port34 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16768 | Slave03 Outlet Port35 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16769 | Slave03 Outlet Port36 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16770 | Slave03 Outlet Port37 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16771 | Slave03 Outlet Port38 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16772 | Slave03 Outlet Port39 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16773 | Slave03 Outlet Port40 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16774 | Slave03 Outlet Port41 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16775 | Slave03 Outlet Port42 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16776 | Slave04 Outlet Port01 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16777 | Slave04 Outlet Port02 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16778 | Slave04 Outlet Port03 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16779 | Slave04 Outlet Port04 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16780 | Slave04 Outlet Port05 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16781 | Slave04 Outlet Port06 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16782 | Slave04 Outlet Port07 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16783 | Slave04 Outlet Port08 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16784 | Slave04 Outlet Port09 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16785 | Slave04 Outlet Port10 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16786 | Slave04 Outlet Port11 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16787 | Slave04 Outlet Port12 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16788 | Slave04 Outlet Port13 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16789 | Slave04 Outlet Port14 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16790 | Slave04 Outlet Port15 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16791 | Slave04 Outlet Port16 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16792 | Slave04 Outlet Port17 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16793 | Slave04 Outlet Port18 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16794 | Slave04 Outlet Port19 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16795 | Slave04 Outlet Port20 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16796 | Slave04 Outlet Port21 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16797 | Slave04 Outlet Port22 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16798 | Slave04 Outlet Port23 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16799 | Slave04 Outlet Port24 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16800 | Slave04 Outlet Port25 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16801 | Slave04 Outlet Port26 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16802 | Slave04 Outlet Port27 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16803 | Slave04 Outlet Port28 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16804 | Slave04 Outlet Port29 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16805 | Slave04 Outlet Port30 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16806 | Slave04 Outlet Port31 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16807 | Slave04 Outlet Port32 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16808 | Slave04 Outlet Port33 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16809 | Slave04 Outlet Port34 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16810 | Slave04 Outlet Port35 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16811 | Slave04 Outlet Port36 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16812 | Slave04 Outlet Port37 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16813 | Slave04 Outlet Port38 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16814 | Slave04 Outlet Port39 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16815 | Slave04 Outlet Port40 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16816 | Slave04 Outlet Port41 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16817 | Slave04 Outlet Port42 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16818 | Slave05 Outlet Port01 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16819 | Slave05 Outlet Port02 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16820 | Slave05 Outlet Port03 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16821 | Slave05 Outlet Port04 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16822 | Slave05 Outlet Port05 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16823 | Slave05 Outlet Port06 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16824 | Slave05 Outlet Port07 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16825 | Slave05 Outlet Port08 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16826 | Slave05 Outlet Port09 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16827 | Slave05 Outlet Port10 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16828 | Slave05 Outlet Port11 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16829 | Slave05 Outlet Port12 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16830 | Slave05 Outlet Port13 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16831 | Slave05 Outlet Port14 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16832 | Slave05 Outlet Port15 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16833 | Slave05 Outlet Port16 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16834 | Slave05 Outlet Port17 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16835 | Slave05 Outlet Port18 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16836 | Slave05 Outlet Port19 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16837 | Slave05 Outlet Port20 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16838 | Slave05 Outlet Port21 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16839 | Slave05 Outlet Port22 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16840 | Slave05 Outlet Port23 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16841 | Slave05 Outlet Port24 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16842 | Slave05 Outlet Port25 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16843 | Slave05 Outlet Port26 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16844 | Slave05 Outlet Port27 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16845 | Slave05 Outlet Port28 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16846 | Slave05 Outlet Port29 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16847 | Slave05 Outlet Port30 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16848 | Slave05 Outlet Port31 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16849 | Slave05 Outlet Port32 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16850 | Slave05 Outlet Port33 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16851 | Slave05 Outlet Port34 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16852 | Slave05 Outlet Port35 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16853 | Slave05 Outlet Port36 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16854 | Slave05 Outlet Port37 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16855 | Slave05 Outlet Port38 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16856 | Slave05 Outlet Port39 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16857 | Slave05 Outlet Port40 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16858 | Slave05 Outlet Port41 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16859 | Slave05 Outlet Port42 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16860 | Slave06 Outlet Port01 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16861 | Slave06 Outlet Port02 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16862 | Slave06 Outlet Port03 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16863 | Slave06 Outlet Port04 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16864 | Slave06 Outlet Port05 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16865 | Slave06 Outlet Port06 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16866 | Slave06 Outlet Port07 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16867 | Slave06 Outlet Port08 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16868 | Slave06 Outlet Port09 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16869 | Slave06 Outlet Port10 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16870 | Slave06 Outlet Port11 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16871 | Slave06 Outlet Port12 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16872 | Slave06 Outlet Port13 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16873 | Slave06 Outlet Port14 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16874 | Slave06 Outlet Port15 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16875 | Slave06 Outlet Port16 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16876 | Slave06 Outlet Port17 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16877 | Slave06 Outlet Port18 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16878 | Slave06 Outlet Port19 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16879 | Slave06 Outlet Port20 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16880 | Slave06 Outlet Port21 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16881 | Slave06 Outlet Port22 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16882 | Slave06 Outlet Port23 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16883 | Slave06 Outlet Port24 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16884 | Slave06 Outlet Port25 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16885 | Slave06 Outlet Port26 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16886 | Slave06 Outlet Port27 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16887 | Slave06 Outlet Port28 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16888 | Slave06 Outlet Port29 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16889 | Slave06 Outlet Port30 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16890 | Slave06 Outlet Port31 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16891 | Slave06 Outlet Port32 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16892 | Slave06 Outlet Port33 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16893 | Slave06 Outlet Port34 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16894 | Slave06 Outlet Port35 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16895 | Slave06 Outlet Port36 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16896 | Slave06 Outlet Port37 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16897 | Slave06 Outlet Port38 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16898 | Slave06 Outlet Port39 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16899 | Slave06 Outlet Port40 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16900 | Slave06 Outlet Port41 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16901 | Slave06 Outlet Port42 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16902 | Slave07 Outlet Port01 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16903 | Slave07 Outlet Port02 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16904 | Slave07 Outlet Port03 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16905 | Slave07 Outlet Port04 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16906 | Slave07 Outlet Port05 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16907 | Slave07 Outlet Port06 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16908 | Slave07 Outlet Port07 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16909 | Slave07 Outlet Port08 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16910 | Slave07 Outlet Port09 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16911 | Slave07 Outlet Port10 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16912 | Slave07 Outlet Port11 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16913 | Slave07 Outlet Port12 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16914 | Slave07 Outlet Port13 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16915 | Slave07 Outlet Port14 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16916 | Slave07 Outlet Port15 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16917 | Slave07 Outlet Port16 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16918 | Slave07 Outlet Port17 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16919 | Slave07 Outlet Port18 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16920 | Slave07 Outlet Port19 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16921 | Slave07 Outlet Port20 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16922 | Slave07 Outlet Port21 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16923 | Slave07 Outlet Port22 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16924 | Slave07 Outlet Port23 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16925 | Slave07 Outlet Port24 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16926 | Slave07 Outlet Port25 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16927 | Slave07 Outlet Port26 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16928 | Slave07 Outlet Port27 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16929 | Slave07 Outlet Port28 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16930 | Slave07 Outlet Port29 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16931 | Slave07 Outlet Port30 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16932 | Slave07 Outlet Port31 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16933 | Slave07 Outlet Port32 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16934 | Slave07 Outlet Port33 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16935 | Slave07 Outlet Port34 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16936 | Slave07 Outlet Port35 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16937 | Slave07 Outlet Port36 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16938 | Slave07 Outlet Port37 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16939 | Slave07 Outlet Port38 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16940 | Slave07 Outlet Port39 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16941 | Slave07 Outlet Port40 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16942 | Slave07 Outlet Port41 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16943 | Slave07 Outlet Port42 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16944 | Slave08 Outlet Port01 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16945 | Slave08 Outlet Port02 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16946 | Slave08 Outlet Port03 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16947 | Slave08 Outlet Port04 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16948 | Slave08 Outlet Port05 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16949 | Slave08 Outlet Port06 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16950 | Slave08 Outlet Port07 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16951 | Slave08 Outlet Port08 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16952 | Slave08 Outlet Port09 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16953 | Slave08 Outlet Port10 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16954 | Slave08 Outlet Port11 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16955 | Slave08 Outlet Port12 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16956 | Slave08 Outlet Port13 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16957 | Slave08 Outlet Port14 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16958 | Slave08 Outlet Port15 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16959 | Slave08 Outlet Port16 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16960 | Slave08 Outlet Port17 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16961 | Slave08 Outlet Port18 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16962 | Slave08 Outlet Port19 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16963 | Slave08 Outlet Port20 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16964 | Slave08 Outlet Port21 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16965 | Slave08 Outlet Port22 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16966 | Slave08 Outlet Port23 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16967 | Slave08 Outlet Port24 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16968 | Slave08 Outlet Port25 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16969 | Slave08 Outlet Port26 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16970 | Slave08 Outlet Port27 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16971 | Slave08 Outlet Port28 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16972 | Slave08 Outlet Port29 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16973 | Slave08 Outlet Port30 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16974 | Slave08 Outlet Port31 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16975 | Slave08 Outlet Port32 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16976 | Slave08 Outlet Port33 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16977 | Slave08 Outlet Port34 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16978 | Slave08 Outlet Port35 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16979 | Slave08 Outlet Port36 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16980 | Slave08 Outlet Port37 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16981 | Slave08 Outlet Port38 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16982 | Slave08 Outlet Port39 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16983 | Slave08 Outlet Port40 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16984 | Slave08 Outlet Port41 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16985 | Slave08 Outlet Port42 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16986 | Slave09 Outlet Port01 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16987 | Slave09 Outlet Port02 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16988 | Slave09 Outlet Port03 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16989 | Slave09 Outlet Port04 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16990 | Slave09 Outlet Port05 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16991 | Slave09 Outlet Port06 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16992 | Slave09 Outlet Port07 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16993 | Slave09 Outlet Port08 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16994 | Slave09 Outlet Port09 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16995 | Slave09 Outlet Port10 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16996 | Slave09 Outlet Port11 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16997 | Slave09 Outlet Port12 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16998 | Slave09 Outlet Port13 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
16999 | Slave09 Outlet Port14 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17000 | Slave09 Outlet Port15 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17001 | Slave09 Outlet Port16 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17002 | Slave09 Outlet Port17 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17003 | Slave09 Outlet Port18 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17004 | Slave09 Outlet Port19 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17005 | Slave09 Outlet Port20 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17006 | Slave09 Outlet Port21 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17007 | Slave09 Outlet Port22 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17008 | Slave09 Outlet Port23 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17009 | Slave09 Outlet Port24 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17010 | Slave09 Outlet Port25 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17011 | Slave09 Outlet Port26 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17012 | Slave09 Outlet Port27 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17013 | Slave09 Outlet Port28 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17014 | Slave09 Outlet Port29 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17015 | Slave09 Outlet Port30 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17016 | Slave09 Outlet Port31 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17017 | Slave09 Outlet Port32 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17018 | Slave09 Outlet Port33 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17019 | Slave09 Outlet Port34 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17020 | Slave09 Outlet Port35 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17021 | Slave09 Outlet Port36 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17022 | Slave09 Outlet Port37 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17023 | Slave09 Outlet Port38 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17024 | Slave09 Outlet Port39 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17025 | Slave09 Outlet Port40 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17026 | Slave09 Outlet Port41 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17027 | Slave09 Outlet Port42 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17028 | Slave10 Outlet Port01 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17029 | Slave10 Outlet Port02 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17030 | Slave10 Outlet Port03 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17031 | Slave10 Outlet Port04 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17032 | Slave10 Outlet Port05 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17033 | Slave10 Outlet Port06 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17034 | Slave10 Outlet Port07 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17035 | Slave10 Outlet Port08 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17036 | Slave10 Outlet Port09 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17037 | Slave10 Outlet Port10 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17038 | Slave10 Outlet Port11 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17039 | Slave10 Outlet Port12 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17040 | Slave10 Outlet Port13 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17041 | Slave10 Outlet Port14 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17042 | Slave10 Outlet Port15 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17043 | Slave10 Outlet Port16 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17044 | Slave10 Outlet Port17 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17045 | Slave10 Outlet Port18 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17046 | Slave10 Outlet Port19 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17047 | Slave10 Outlet Port20 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17048 | Slave10 Outlet Port21 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17049 | Slave10 Outlet Port22 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17050 | Slave10 Outlet Port23 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17051 | Slave10 Outlet Port24 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17052 | Slave10 Outlet Port25 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17053 | Slave10 Outlet Port26 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17054 | Slave10 Outlet Port27 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17055 | Slave10 Outlet Port28 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17056 | Slave10 Outlet Port29 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17057 | Slave10 Outlet Port30 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17058 | Slave10 Outlet Port31 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17059 | Slave10 Outlet Port32 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17060 | Slave10 Outlet Port33 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17061 | Slave10 Outlet Port34 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17062 | Slave10 Outlet Port35 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17063 | Slave10 Outlet Port36 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17064 | Slave10 Outlet Port37 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17065 | Slave10 Outlet Port38 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17066 | Slave10 Outlet Port39 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17067 | Slave10 Outlet Port40 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17068 | Slave10 Outlet Port41 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17069 | Slave10 Outlet Port42 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17070 | Slave11 Outlet Port01 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17071 | Slave11 Outlet Port02 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17072 | Slave11 Outlet Port03 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17073 | Slave11 Outlet Port04 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17074 | Slave11 Outlet Port05 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17075 | Slave11 Outlet Port06 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17076 | Slave11 Outlet Port07 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17077 | Slave11 Outlet Port08 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17078 | Slave11 Outlet Port09 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17079 | Slave11 Outlet Port10 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17080 | Slave11 Outlet Port11 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17081 | Slave11 Outlet Port12 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17082 | Slave11 Outlet Port13 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17083 | Slave11 Outlet Port14 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17084 | Slave11 Outlet Port15 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17085 | Slave11 Outlet Port16 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17086 | Slave11 Outlet Port17 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17087 | Slave11 Outlet Port18 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17088 | Slave11 Outlet Port19 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17089 | Slave11 Outlet Port20 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17090 | Slave11 Outlet Port21 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17091 | Slave11 Outlet Port22 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17092 | Slave11 Outlet Port23 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17093 | Slave11 Outlet Port24 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17094 | Slave11 Outlet Port25 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17095 | Slave11 Outlet Port26 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17096 | Slave11 Outlet Port27 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17097 | Slave11 Outlet Port28 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17098 | Slave11 Outlet Port29 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17099 | Slave11 Outlet Port30 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17100 | Slave11 Outlet Port31 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17101 | Slave11 Outlet Port32 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17102 | Slave11 Outlet Port33 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17103 | Slave11 Outlet Port34 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17104 | Slave11 Outlet Port35 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17105 | Slave11 Outlet Port36 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17106 | Slave11 Outlet Port37 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17107 | Slave11 Outlet Port38 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17108 | Slave11 Outlet Port39 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17109 | Slave11 Outlet Port40 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17110 | Slave11 Outlet Port41 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17111 | Slave11 Outlet Port42 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17112 | Slave12 Outlet Port01 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17113 | Slave12 Outlet Port02 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17114 | Slave12 Outlet Port03 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17115 | Slave12 Outlet Port04 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17116 | Slave12 Outlet Port05 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17117 | Slave12 Outlet Port06 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17118 | Slave12 Outlet Port07 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17119 | Slave12 Outlet Port08 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17120 | Slave12 Outlet Port09 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17121 | Slave12 Outlet Port10 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17122 | Slave12 Outlet Port11 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17123 | Slave12 Outlet Port12 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17124 | Slave12 Outlet Port13 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17125 | Slave12 Outlet Port14 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17126 | Slave12 Outlet Port15 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17127 | Slave12 Outlet Port16 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17128 | Slave12 Outlet Port17 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17129 | Slave12 Outlet Port18 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17130 | Slave12 Outlet Port19 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17131 | Slave12 Outlet Port20 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17132 | Slave12 Outlet Port21 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17133 | Slave12 Outlet Port22 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17134 | Slave12 Outlet Port23 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17135 | Slave12 Outlet Port24 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17136 | Slave12 Outlet Port25 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17137 | Slave12 Outlet Port26 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17138 | Slave12 Outlet Port27 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17139 | Slave12 Outlet Port28 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17140 | Slave12 Outlet Port29 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17141 | Slave12 Outlet Port30 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17142 | Slave12 Outlet Port31 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17143 | Slave12 Outlet Port32 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17144 | Slave12 Outlet Port33 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17145 | Slave12 Outlet Port34 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17146 | Slave12 Outlet Port35 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17147 | Slave12 Outlet Port36 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17148 | Slave12 Outlet Port37 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17149 | Slave12 Outlet Port38 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17150 | Slave12 Outlet Port39 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17151 | Slave12 Outlet Port40 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17152 | Slave12 Outlet Port41 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17153 | Slave12 Outlet Port42 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17154 | Slave13 Outlet Port01 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17155 | Slave13 Outlet Port02 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17156 | Slave13 Outlet Port03 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17157 | Slave13 Outlet Port04 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17158 | Slave13 Outlet Port05 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17159 | Slave13 Outlet Port06 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17160 | Slave13 Outlet Port07 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17161 | Slave13 Outlet Port08 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17162 | Slave13 Outlet Port09 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17163 | Slave13 Outlet Port10 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17164 | Slave13 Outlet Port11 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17165 | Slave13 Outlet Port12 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17166 | Slave13 Outlet Port13 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17167 | Slave13 Outlet Port14 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17168 | Slave13 Outlet Port15 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17169 | Slave13 Outlet Port16 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17170 | Slave13 Outlet Port17 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17171 | Slave13 Outlet Port18 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17172 | Slave13 Outlet Port19 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17173 | Slave13 Outlet Port20 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17174 | Slave13 Outlet Port21 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17175 | Slave13 Outlet Port22 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17176 | Slave13 Outlet Port23 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17177 | Slave13 Outlet Port24 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17178 | Slave13 Outlet Port25 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17179 | Slave13 Outlet Port26 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17180 | Slave13 Outlet Port27 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17181 | Slave13 Outlet Port28 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17182 | Slave13 Outlet Port29 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17183 | Slave13 Outlet Port30 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17184 | Slave13 Outlet Port31 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17185 | Slave13 Outlet Port32 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17186 | Slave13 Outlet Port33 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17187 | Slave13 Outlet Port34 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17188 | Slave13 Outlet Port35 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17189 | Slave13 Outlet Port36 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17190 | Slave13 Outlet Port37 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17191 | Slave13 Outlet Port38 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17192 | Slave13 Outlet Port39 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17193 | Slave13 Outlet Port40 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17194 | Slave13 Outlet Port41 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17195 | Slave13 Outlet Port42 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17196 | Slave14 Outlet Port01 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17197 | Slave14 Outlet Port02 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17198 | Slave14 Outlet Port03 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17199 | Slave14 Outlet Port04 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17200 | Slave14 Outlet Port05 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17201 | Slave14 Outlet Port06 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17202 | Slave14 Outlet Port07 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17203 | Slave14 Outlet Port08 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17204 | Slave14 Outlet Port09 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17205 | Slave14 Outlet Port10 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17206 | Slave14 Outlet Port11 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17207 | Slave14 Outlet Port12 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17208 | Slave14 Outlet Port13 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17209 | Slave14 Outlet Port14 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17210 | Slave14 Outlet Port15 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17211 | Slave14 Outlet Port16 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17212 | Slave14 Outlet Port17 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17213 | Slave14 Outlet Port18 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17214 | Slave14 Outlet Port19 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17215 | Slave14 Outlet Port20 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17216 | Slave14 Outlet Port21 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17217 | Slave14 Outlet Port22 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17218 | Slave14 Outlet Port23 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17219 | Slave14 Outlet Port24 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17220 | Slave14 Outlet Port25 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17221 | Slave14 Outlet Port26 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17222 | Slave14 Outlet Port27 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17223 | Slave14 Outlet Port28 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17224 | Slave14 Outlet Port29 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17225 | Slave14 Outlet Port30 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17226 | Slave14 Outlet Port31 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17227 | Slave14 Outlet Port32 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17228 | Slave14 Outlet Port33 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17229 | Slave14 Outlet Port34 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17230 | Slave14 Outlet Port35 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17231 | Slave14 Outlet Port36 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17232 | Slave14 Outlet Port37 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17233 | Slave14 Outlet Port38 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17234 | Slave14 Outlet Port39 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17235 | Slave14 Outlet Port40 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17236 | Slave14 Outlet Port41 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17237 | Slave14 Outlet Port42 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17238 | Slave15 Outlet Port01 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17239 | Slave15 Outlet Port02 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17240 | Slave15 Outlet Port03 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17241 | Slave15 Outlet Port04 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17242 | Slave15 Outlet Port05 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17243 | Slave15 Outlet Port06 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17244 | Slave15 Outlet Port07 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17245 | Slave15 Outlet Port08 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17246 | Slave15 Outlet Port09 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17247 | Slave15 Outlet Port10 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17248 | Slave15 Outlet Port11 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17249 | Slave15 Outlet Port12 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17250 | Slave15 Outlet Port13 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17251 | Slave15 Outlet Port14 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17252 | Slave15 Outlet Port15 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17253 | Slave15 Outlet Port16 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17254 | Slave15 Outlet Port17 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17255 | Slave15 Outlet Port18 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17256 | Slave15 Outlet Port19 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17257 | Slave15 Outlet Port20 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17258 | Slave15 Outlet Port21 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17259 | Slave15 Outlet Port22 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17260 | Slave15 Outlet Port23 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17261 | Slave15 Outlet Port24 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17262 | Slave15 Outlet Port25 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17263 | Slave15 Outlet Port26 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17264 | Slave15 Outlet Port27 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17265 | Slave15 Outlet Port28 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17266 | Slave15 Outlet Port29 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17267 | Slave15 Outlet Port30 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17268 | Slave15 Outlet Port31 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17269 | Slave15 Outlet Port32 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17270 | Slave15 Outlet Port33 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17271 | Slave15 Outlet Port34 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17272 | Slave15 Outlet Port35 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17273 | Slave15 Outlet Port36 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17274 | Slave15 Outlet Port37 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17275 | Slave15 Outlet Port38 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17276 | Slave15 Outlet Port39 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17277 | Slave15 Outlet Port40 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17278 | Slave15 Outlet Port41 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17279 | Slave15 Outlet Port42 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
17280 | Master EMD-1 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17281 | Master EMD-2 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17282 | Master EMD-3 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17283 | Master EMD-4 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17284 | Master EMD-5 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17285 | Master EMD-6 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17286 | Master EMD-7 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17287 | Master EMD-8 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17288 | Slave01 EMD-1 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17289 | Slave01 EMD-2 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17290 | Slave01 EMD-3 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17291 | Slave01 EMD-4 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17292 | Slave01 EMD-5 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17293 | Slave01 EMD-6 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17294 | Slave01 EMD-7 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17295 | Slave01 EMD-8 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17296 | Slave02 EMD-1 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17297 | Slave02 EMD-2 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17298 | Slave02 EMD-3 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17299 | Slave02 EMD-4 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17300 | Slave02 EMD-5 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17301 | Slave02 EMD-6 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17302 | Slave02 EMD-7 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17303 | Slave02 EMD-8 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17304 | Slave03 EMD-1 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17305 | Slave03 EMD-2 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17306 | Slave03 EMD-3 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17307 | Slave03 EMD-4 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17308 | Slave03 EMD-5 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17309 | Slave03 EMD-6 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17310 | Slave03 EMD-7 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17311 | Slave03 EMD-8 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17312 | Slave04 EMD-1 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17313 | Slave04 EMD-2 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17314 | Slave04 EMD-3 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17315 | Slave04 EMD-4 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17316 | Slave04 EMD-5 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17317 | Slave04 EMD-6 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17318 | Slave04 EMD-7 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17319 | Slave04 EMD-8 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17320 | Slave05 EMD-1 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17321 | Slave05 EMD-2 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17322 | Slave05 EMD-3 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17323 | Slave05 EMD-4 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17324 | Slave05 EMD-5 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17325 | Slave05 EMD-6 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17326 | Slave05 EMD-7 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17327 | Slave05 EMD-8 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17328 | Slave06 EMD-1 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17329 | Slave06 EMD-2 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17330 | Slave06 EMD-3 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17331 | Slave06 EMD-4 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17332 | Slave06 EMD-5 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17333 | Slave06 EMD-6 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17334 | Slave06 EMD-7 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17335 | Slave06 EMD-8 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17336 | Slave07 EMD-1 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17337 | Slave07 EMD-2 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17338 | Slave07 EMD-3 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17339 | Slave07 EMD-4 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17340 | Slave07 EMD-5 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17341 | Slave07 EMD-6 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17342 | Slave07 EMD-7 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17343 | Slave07 EMD-8 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17344 | Slave08 EMD-1 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17345 | Slave08 EMD-2 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17346 | Slave08 EMD-3 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17347 | Slave08 EMD-4 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17348 | Slave08 EMD-5 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17349 | Slave08 EMD-6 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17350 | Slave08 EMD-7 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17351 | Slave08 EMD-8 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17352 | Slave09 EMD-1 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17353 | Slave09 EMD-2 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17354 | Slave09 EMD-3 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17355 | Slave09 EMD-4 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17356 | Slave09 EMD-5 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17357 | Slave09 EMD-6 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17358 | Slave09 EMD-7 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17359 | Slave09 EMD-8 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17360 | Slave10 EMD-1 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17361 | Slave10 EMD-2 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17362 | Slave10 EMD-3 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17363 | Slave10 EMD-4 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17364 | Slave10 EMD-5 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17365 | Slave10 EMD-6 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17366 | Slave10 EMD-7 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17367 | Slave10 EMD-8 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17368 | Slave11 EMD-1 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17369 | Slave11 EMD-2 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17370 | Slave11 EMD-3 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17371 | Slave11 EMD-4 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17372 | Slave11 EMD-5 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17373 | Slave11 EMD-6 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17374 | Slave11 EMD-7 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17375 | Slave11 EMD-8 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17376 | Slave12 EMD-1 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17377 | Slave12 EMD-2 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17378 | Slave12 EMD-3 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17379 | Slave12 EMD-4 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17380 | Slave12 EMD-5 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17381 | Slave12 EMD-6 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17382 | Slave12 EMD-7 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17383 | Slave12 EMD-8 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17384 | Slave13 EMD-1 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17385 | Slave13 EMD-2 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17386 | Slave13 EMD-3 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17387 | Slave13 EMD-4 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17388 | Slave13 EMD-5 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17389 | Slave13 EMD-6 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17390 | Slave13 EMD-7 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17391 | Slave13 EMD-8 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17392 | Slave14 EMD-1 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17393 | Slave14 EMD-2 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17394 | Slave14 EMD-3 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17395 | Slave14 EMD-4 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17396 | Slave14 EMD-5 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17397 | Slave14 EMD-6 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17398 | Slave14 EMD-7 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17399 | Slave14 EMD-8 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17400 | Slave15 EMD-1 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17401 | Slave15 EMD-2 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17402 | Slave15 EMD-3 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17403 | Slave15 EMD-4 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17404 | Slave15 EMD-5 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17405 | Slave15 EMD-6 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17406 | Slave15 EMD-7 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17407 | Slave15 EMD-8 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17408 | Master EMD-1 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17409 | Master EMD-2 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17410 | Master EMD-3 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17411 | Master EMD-4 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17412 | Master EMD-5 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17413 | Master EMD-6 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17414 | Master EMD-7 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17415 | Master EMD-8 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17416 | Slave01 EMD-1 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17417 | Slave01 EMD-2 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17418 | Slave01 EMD-3 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17419 | Slave01 EMD-4 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17420 | Slave01 EMD-5 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17421 | Slave01 EMD-6 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17422 | Slave01 EMD-7 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17423 | Slave01 EMD-8 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17424 | Slave02 EMD-1 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17425 | Slave02 EMD-2 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17426 | Slave02 EMD-3 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17427 | Slave02 EMD-4 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17428 | Slave02 EMD-5 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17429 | Slave02 EMD-6 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17430 | Slave02 EMD-7 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17431 | Slave02 EMD-8 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17432 | Slave03 EMD-1 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17433 | Slave03 EMD-2 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17434 | Slave03 EMD-3 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17435 | Slave03 EMD-4 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17436 | Slave03 EMD-5 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17437 | Slave03 EMD-6 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17438 | Slave03 EMD-7 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17439 | Slave03 EMD-8 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17440 | Slave04 EMD-1 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17441 | Slave04 EMD-2 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17442 | Slave04 EMD-3 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17443 | Slave04 EMD-4 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17444 | Slave04 EMD-5 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17445 | Slave04 EMD-6 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17446 | Slave04 EMD-7 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17447 | Slave04 EMD-8 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17448 | Slave05 EMD-1 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17449 | Slave05 EMD-2 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17450 | Slave05 EMD-3 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17451 | Slave05 EMD-4 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17452 | Slave05 EMD-5 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17453 | Slave05 EMD-6 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17454 | Slave05 EMD-7 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17455 | Slave05 EMD-8 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17456 | Slave06 EMD-1 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17457 | Slave06 EMD-2 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17458 | Slave06 EMD-3 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17459 | Slave06 EMD-4 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17460 | Slave06 EMD-5 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17461 | Slave06 EMD-6 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17462 | Slave06 EMD-7 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17463 | Slave06 EMD-8 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17464 | Slave07 EMD-1 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17465 | Slave07 EMD-2 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17466 | Slave07 EMD-3 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17467 | Slave07 EMD-4 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17468 | Slave07 EMD-5 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17469 | Slave07 EMD-6 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17470 | Slave07 EMD-7 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17471 | Slave07 EMD-8 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17472 | Slave08 EMD-1 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17473 | Slave08 EMD-2 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17474 | Slave08 EMD-3 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17475 | Slave08 EMD-4 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17476 | Slave08 EMD-5 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17477 | Slave08 EMD-6 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17478 | Slave08 EMD-7 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17479 | Slave08 EMD-8 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17480 | Slave09 EMD-1 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17481 | Slave09 EMD-2 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17482 | Slave09 EMD-3 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17483 | Slave09 EMD-4 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17484 | Slave09 EMD-5 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17485 | Slave09 EMD-6 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17486 | Slave09 EMD-7 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17487 | Slave09 EMD-8 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17488 | Slave10 EMD-1 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17489 | Slave10 EMD-2 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17490 | Slave10 EMD-3 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17491 | Slave10 EMD-4 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17492 | Slave10 EMD-5 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17493 | Slave10 EMD-6 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17494 | Slave10 EMD-7 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17495 | Slave10 EMD-8 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17496 | Slave11 EMD-1 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17497 | Slave11 EMD-2 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17498 | Slave11 EMD-3 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17499 | Slave11 EMD-4 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17500 | Slave11 EMD-5 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17501 | Slave11 EMD-6 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17502 | Slave11 EMD-7 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17503 | Slave11 EMD-8 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17504 | Slave12 EMD-1 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17505 | Slave12 EMD-2 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17506 | Slave12 EMD-3 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17507 | Slave12 EMD-4 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17508 | Slave12 EMD-5 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17509 | Slave12 EMD-6 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17510 | Slave12 EMD-7 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17511 | Slave12 EMD-8 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17512 | Slave13 EMD-1 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17513 | Slave13 EMD-2 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17514 | Slave13 EMD-3 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17515 | Slave13 EMD-4 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17516 | Slave13 EMD-5 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17517 | Slave13 EMD-6 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17518 | Slave13 EMD-7 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17519 | Slave13 EMD-8 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17520 | Slave14 EMD-1 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17521 | Slave14 EMD-2 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17522 | Slave14 EMD-3 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17523 | Slave14 EMD-4 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17524 | Slave14 EMD-5 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17525 | Slave14 EMD-6 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17526 | Slave14 EMD-7 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17527 | Slave14 EMD-8 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17528 | Slave15 EMD-1 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17529 | Slave15 EMD-2 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17530 | Slave15 EMD-3 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17531 | Slave15 EMD-4 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17532 | Slave15 EMD-5 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17533 | Slave15 EMD-6 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17534 | Slave15 EMD-7 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17535 | Slave15 EMD-8 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17536 | Master EMD-1 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17537 | Master EMD-2 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17538 | Master EMD-3 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17539 | Master EMD-4 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17540 | Master EMD-5 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17541 | Master EMD-6 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17542 | Master EMD-7 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17543 | Master EMD-8 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17544 | Slave01 EMD-1 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17545 | Slave01 EMD-2 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17546 | Slave01 EMD-3 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17547 | Slave01 EMD-4 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17548 | Slave01 EMD-5 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17549 | Slave01 EMD-6 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17550 | Slave01 EMD-7 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17551 | Slave01 EMD-8 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17552 | Slave02 EMD-1 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17553 | Slave02 EMD-2 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17554 | Slave02 EMD-3 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17555 | Slave02 EMD-4 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17556 | Slave02 EMD-5 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17557 | Slave02 EMD-6 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17558 | Slave02 EMD-7 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17559 | Slave02 EMD-8 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17560 | Slave03 EMD-1 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17561 | Slave03 EMD-2 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17562 | Slave03 EMD-3 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17563 | Slave03 EMD-4 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17564 | Slave03 EMD-5 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17565 | Slave03 EMD-6 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17566 | Slave03 EMD-7 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17567 | Slave03 EMD-8 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17568 | Slave04 EMD-1 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17569 | Slave04 EMD-2 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17570 | Slave04 EMD-3 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17571 | Slave04 EMD-4 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17572 | Slave04 EMD-5 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17573 | Slave04 EMD-6 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17574 | Slave04 EMD-7 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17575 | Slave04 EMD-8 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17576 | Slave05 EMD-1 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17577 | Slave05 EMD-2 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17578 | Slave05 EMD-3 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17579 | Slave05 EMD-4 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17580 | Slave05 EMD-5 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17581 | Slave05 EMD-6 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17582 | Slave05 EMD-7 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17583 | Slave05 EMD-8 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17584 | Slave06 EMD-1 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17585 | Slave06 EMD-2 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17586 | Slave06 EMD-3 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17587 | Slave06 EMD-4 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17588 | Slave06 EMD-5 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17589 | Slave06 EMD-6 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17590 | Slave06 EMD-7 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17591 | Slave06 EMD-8 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17592 | Slave07 EMD-1 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17593 | Slave07 EMD-2 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17594 | Slave07 EMD-3 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17595 | Slave07 EMD-4 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17596 | Slave07 EMD-5 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17597 | Slave07 EMD-6 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17598 | Slave07 EMD-7 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17599 | Slave07 EMD-8 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17600 | Slave08 EMD-1 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17601 | Slave08 EMD-2 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17602 | Slave08 EMD-3 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17603 | Slave08 EMD-4 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17604 | Slave08 EMD-5 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17605 | Slave08 EMD-6 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17606 | Slave08 EMD-7 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17607 | Slave08 EMD-8 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17608 | Slave09 EMD-1 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17609 | Slave09 EMD-2 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17610 | Slave09 EMD-3 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17611 | Slave09 EMD-4 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17612 | Slave09 EMD-5 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17613 | Slave09 EMD-6 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17614 | Slave09 EMD-7 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17615 | Slave09 EMD-8 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17616 | Slave10 EMD-1 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17617 | Slave10 EMD-2 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17618 | Slave10 EMD-3 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17619 | Slave10 EMD-4 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17620 | Slave10 EMD-5 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17621 | Slave10 EMD-6 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17622 | Slave10 EMD-7 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17623 | Slave10 EMD-8 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17624 | Slave11 EMD-1 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17625 | Slave11 EMD-2 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17626 | Slave11 EMD-3 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17627 | Slave11 EMD-4 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17628 | Slave11 EMD-5 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17629 | Slave11 EMD-6 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17630 | Slave11 EMD-7 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17631 | Slave11 EMD-8 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17632 | Slave12 EMD-1 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17633 | Slave12 EMD-2 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17634 | Slave12 EMD-3 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17635 | Slave12 EMD-4 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17636 | Slave12 EMD-5 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17637 | Slave12 EMD-6 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17638 | Slave12 EMD-7 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17639 | Slave12 EMD-8 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17640 | Slave13 EMD-1 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17641 | Slave13 EMD-2 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17642 | Slave13 EMD-3 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17643 | Slave13 EMD-4 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17644 | Slave13 EMD-5 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17645 | Slave13 EMD-6 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17646 | Slave13 EMD-7 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17647 | Slave13 EMD-8 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17648 | Slave14 EMD-1 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17649 | Slave14 EMD-2 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17650 | Slave14 EMD-3 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17651 | Slave14 EMD-4 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17652 | Slave14 EMD-5 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17653 | Slave14 EMD-6 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17654 | Slave14 EMD-7 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17655 | Slave14 EMD-8 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17656 | Slave15 EMD-1 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17657 | Slave15 EMD-2 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17658 | Slave15 EMD-3 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17659 | Slave15 EMD-4 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17660 | Slave15 EMD-5 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17661 | Slave15 EMD-6 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17662 | Slave15 EMD-7 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17663 | Slave15 EMD-8 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17664 | Master EMD-1 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17665 | Master EMD-2 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17666 | Master EMD-3 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17667 | Master EMD-4 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17668 | Master EMD-5 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17669 | Master EMD-6 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17670 | Master EMD-7 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17671 | Master EMD-8 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17672 | Slave01 EMD-1 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17673 | Slave01 EMD-2 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17674 | Slave01 EMD-3 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17675 | Slave01 EMD-4 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17676 | Slave01 EMD-5 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17677 | Slave01 EMD-6 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17678 | Slave01 EMD-7 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17679 | Slave01 EMD-8 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17680 | Slave02 EMD-1 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17681 | Slave02 EMD-2 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17682 | Slave02 EMD-3 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17683 | Slave02 EMD-4 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17684 | Slave02 EMD-5 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17685 | Slave02 EMD-6 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17686 | Slave02 EMD-7 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17687 | Slave02 EMD-8 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17688 | Slave03 EMD-1 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17689 | Slave03 EMD-2 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17690 | Slave03 EMD-3 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17691 | Slave03 EMD-4 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17692 | Slave03 EMD-5 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17693 | Slave03 EMD-6 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17694 | Slave03 EMD-7 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17695 | Slave03 EMD-8 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17696 | Slave04 EMD-1 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17697 | Slave04 EMD-2 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17698 | Slave04 EMD-3 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17699 | Slave04 EMD-4 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17700 | Slave04 EMD-5 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17701 | Slave04 EMD-6 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17702 | Slave04 EMD-7 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17703 | Slave04 EMD-8 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17704 | Slave05 EMD-1 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17705 | Slave05 EMD-2 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17706 | Slave05 EMD-3 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17707 | Slave05 EMD-4 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17708 | Slave05 EMD-5 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17709 | Slave05 EMD-6 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17710 | Slave05 EMD-7 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17711 | Slave05 EMD-8 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17712 | Slave06 EMD-1 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17713 | Slave06 EMD-2 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17714 | Slave06 EMD-3 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17715 | Slave06 EMD-4 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17716 | Slave06 EMD-5 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17717 | Slave06 EMD-6 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17718 | Slave06 EMD-7 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17719 | Slave06 EMD-8 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17720 | Slave07 EMD-1 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17721 | Slave07 EMD-2 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17722 | Slave07 EMD-3 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17723 | Slave07 EMD-4 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17724 | Slave07 EMD-5 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17725 | Slave07 EMD-6 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17726 | Slave07 EMD-7 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17727 | Slave07 EMD-8 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17728 | Slave08 EMD-1 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17729 | Slave08 EMD-2 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17730 | Slave08 EMD-3 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17731 | Slave08 EMD-4 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17732 | Slave08 EMD-5 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17733 | Slave08 EMD-6 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17734 | Slave08 EMD-7 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17735 | Slave08 EMD-8 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17736 | Slave09 EMD-1 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17737 | Slave09 EMD-2 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17738 | Slave09 EMD-3 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17739 | Slave09 EMD-4 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17740 | Slave09 EMD-5 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17741 | Slave09 EMD-6 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17742 | Slave09 EMD-7 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17743 | Slave09 EMD-8 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17744 | Slave10 EMD-1 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17745 | Slave10 EMD-2 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17746 | Slave10 EMD-3 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17747 | Slave10 EMD-4 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17748 | Slave10 EMD-5 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17749 | Slave10 EMD-6 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17750 | Slave10 EMD-7 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17751 | Slave10 EMD-8 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17752 | Slave11 EMD-1 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17753 | Slave11 EMD-2 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17754 | Slave11 EMD-3 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17755 | Slave11 EMD-4 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17756 | Slave11 EMD-5 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17757 | Slave11 EMD-6 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17758 | Slave11 EMD-7 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17759 | Slave11 EMD-8 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17760 | Slave12 EMD-1 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17761 | Slave12 EMD-2 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17762 | Slave12 EMD-3 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17763 | Slave12 EMD-4 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17764 | Slave12 EMD-5 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17765 | Slave12 EMD-6 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17766 | Slave12 EMD-7 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17767 | Slave12 EMD-8 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17768 | Slave13 EMD-1 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17769 | Slave13 EMD-2 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17770 | Slave13 EMD-3 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17771 | Slave13 EMD-4 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17772 | Slave13 EMD-5 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17773 | Slave13 EMD-6 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17774 | Slave13 EMD-7 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17775 | Slave13 EMD-8 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17776 | Slave14 EMD-1 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17777 | Slave14 EMD-2 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17778 | Slave14 EMD-3 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17779 | Slave14 EMD-4 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17780 | Slave14 EMD-5 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17781 | Slave14 EMD-6 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17782 | Slave14 EMD-7 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17783 | Slave14 EMD-8 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17784 | Slave15 EMD-1 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17785 | Slave15 EMD-2 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17786 | Slave15 EMD-3 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17787 | Slave15 EMD-4 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17788 | Slave15 EMD-5 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17789 | Slave15 EMD-6 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17790 | Slave15 EMD-7 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17791 | Slave15 EMD-8 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
17792 | Master EMD-1 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
17793 | Master EMD-2 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
17794 | Master EMD-3 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
17795 | Master EMD-4 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
17796 | Master EMD-5 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
17797 | Master EMD-6 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
17798 | Master EMD-7 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
17799 | Master EMD-8 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
17800 | Slave01 EMD-1 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
17801 | Slave01 EMD-2 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
17802 | Slave01 EMD-3 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
17803 | Slave01 EMD-4 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
17804 | Slave01 EMD-5 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
17805 | Slave01 EMD-6 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
17806 | Slave01 EMD-7 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
17807 | Slave01 EMD-8 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
17808 | Slave02 EMD-1 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
17809 | Slave02 EMD-2 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
17810 | Slave02 EMD-3 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
17811 | Slave02 EMD-4 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
17812 | Slave02 EMD-5 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
17813 | Slave02 EMD-6 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
17814 | Slave02 EMD-7 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
17815 | Slave02 EMD-8 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
17816 | Slave03 EMD-1 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
17817 | Slave03 EMD-2 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
17818 | Slave03 EMD-3 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
17819 | Slave03 EMD-4 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
17820 | Slave03 EMD-5 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
17821 | Slave03 EMD-6 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
17822 | Slave03 EMD-7 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
17823 | Slave03 EMD-8 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
17824 | Slave04 EMD-1 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
17825 | Slave04 EMD-2 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
17826 | Slave04 EMD-3 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
17827 | Slave04 EMD-4 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
17828 | Slave04 EMD-5 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
17829 | Slave04 EMD-6 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
17830 | Slave04 EMD-7 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
17831 | Slave04 EMD-8 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
17832 | Slave05 EMD-1 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
17833 | Slave05 EMD-2 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
17834 | Slave05 EMD-3 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
17835 | Slave05 EMD-4 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
17836 | Slave05 EMD-5 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
17837 | Slave05 EMD-6 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
17838 | Slave05 EMD-7 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
17839 | Slave05 EMD-8 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
17840 | Slave06 EMD-1 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
17841 | Slave06 EMD-2 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
17842 | Slave06 EMD-3 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
17843 | Slave06 EMD-4 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
17844 | Slave06 EMD-5 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
17845 | Slave06 EMD-6 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
17846 | Slave06 EMD-7 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
17847 | Slave06 EMD-8 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
17848 | Slave07 EMD-1 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
17849 | Slave07 EMD-2 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
17850 | Slave07 EMD-3 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
17851 | Slave07 EMD-4 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
17852 | Slave07 EMD-5 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
17853 | Slave07 EMD-6 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
17854 | Slave07 EMD-7 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
17855 | Slave07 EMD-8 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
17856 | Slave08 EMD-1 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
17857 | Slave08 EMD-2 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
17858 | Slave08 EMD-3 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
17859 | Slave08 EMD-4 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
17860 | Slave08 EMD-5 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
17861 | Slave08 EMD-6 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
17862 | Slave08 EMD-7 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
17863 | Slave08 EMD-8 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
17864 | Slave09 EMD-1 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
17865 | Slave09 EMD-2 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
17866 | Slave09 EMD-3 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
17867 | Slave09 EMD-4 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
17868 | Slave09 EMD-5 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
17869 | Slave09 EMD-6 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
17870 | Slave09 EMD-7 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
17871 | Slave09 EMD-8 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
17872 | Slave10 EMD-1 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
17873 | Slave10 EMD-2 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
17874 | Slave10 EMD-3 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
17875 | Slave10 EMD-4 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
17876 | Slave10 EMD-5 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
17877 | Slave10 EMD-6 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
17878 | Slave10 EMD-7 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
17879 | Slave10 EMD-8 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
17880 | Slave11 EMD-1 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
17881 | Slave11 EMD-2 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
17882 | Slave11 EMD-3 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
17883 | Slave11 EMD-4 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
17884 | Slave11 EMD-5 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
17885 | Slave11 EMD-6 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
17886 | Slave11 EMD-7 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
17887 | Slave11 EMD-8 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
17888 | Slave12 EMD-1 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
17889 | Slave12 EMD-2 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
17890 | Slave12 EMD-3 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
17891 | Slave12 EMD-4 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
17892 | Slave12 EMD-5 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
17893 | Slave12 EMD-6 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
17894 | Slave12 EMD-7 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
17895 | Slave12 EMD-8 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
17896 | Slave13 EMD-1 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
17897 | Slave13 EMD-2 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
17898 | Slave13 EMD-3 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
17899 | Slave13 EMD-4 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
17900 | Slave13 EMD-5 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
17901 | Slave13 EMD-6 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
17902 | Slave13 EMD-7 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
17903 | Slave13 EMD-8 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
17904 | Slave14 EMD-1 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
17905 | Slave14 EMD-2 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
17906 | Slave14 EMD-3 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
17907 | Slave14 EMD-4 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
17908 | Slave14 EMD-5 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
17909 | Slave14 EMD-6 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
17910 | Slave14 EMD-7 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
17911 | Slave14 EMD-8 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
17912 | Slave15 EMD-1 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
17913 | Slave15 EMD-2 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
17914 | Slave15 EMD-3 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
17915 | Slave15 EMD-4 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
17916 | Slave15 EMD-5 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
17917 | Slave15 EMD-6 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
17918 | Slave15 EMD-7 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
17919 | Slave15 EMD-8 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
17920 | Master EMD-1 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
17921 | Master EMD-2 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
17922 | Master EMD-3 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
17923 | Master EMD-4 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
17924 | Master EMD-5 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
17925 | Master EMD-6 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
17926 | Master EMD-7 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
17927 | Master EMD-8 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
17928 | Slave01 EMD-1 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
17929 | Slave01 EMD-2 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
17930 | Slave01 EMD-3 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
17931 | Slave01 EMD-4 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
17932 | Slave01 EMD-5 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
17933 | Slave01 EMD-6 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
17934 | Slave01 EMD-7 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
17935 | Slave01 EMD-8 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
17936 | Slave02 EMD-1 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
17937 | Slave02 EMD-2 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
17938 | Slave02 EMD-3 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
17939 | Slave02 EMD-4 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
17940 | Slave02 EMD-5 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
17941 | Slave02 EMD-6 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
17942 | Slave02 EMD-7 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
17943 | Slave02 EMD-8 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
17944 | Slave03 EMD-1 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
17945 | Slave03 EMD-2 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
17946 | Slave03 EMD-3 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
17947 | Slave03 EMD-4 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
17948 | Slave03 EMD-5 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
17949 | Slave03 EMD-6 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
17950 | Slave03 EMD-7 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
17951 | Slave03 EMD-8 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
17952 | Slave04 EMD-1 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
17953 | Slave04 EMD-2 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
17954 | Slave04 EMD-3 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
17955 | Slave04 EMD-4 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
17956 | Slave04 EMD-5 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
17957 | Slave04 EMD-6 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
17958 | Slave04 EMD-7 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
17959 | Slave04 EMD-8 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
17960 | Slave05 EMD-1 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
17961 | Slave05 EMD-2 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
17962 | Slave05 EMD-3 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
17963 | Slave05 EMD-4 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
17964 | Slave05 EMD-5 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
17965 | Slave05 EMD-6 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
17966 | Slave05 EMD-7 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
17967 | Slave05 EMD-8 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
17968 | Slave06 EMD-1 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
17969 | Slave06 EMD-2 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
17970 | Slave06 EMD-3 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
17971 | Slave06 EMD-4 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
17972 | Slave06 EMD-5 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
17973 | Slave06 EMD-6 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
17974 | Slave06 EMD-7 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
17975 | Slave06 EMD-8 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
17976 | Slave07 EMD-1 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
17977 | Slave07 EMD-2 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
17978 | Slave07 EMD-3 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
17979 | Slave07 EMD-4 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
17980 | Slave07 EMD-5 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
17981 | Slave07 EMD-6 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
17982 | Slave07 EMD-7 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
17983 | Slave07 EMD-8 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
17984 | Slave08 EMD-1 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
17985 | Slave08 EMD-2 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
17986 | Slave08 EMD-3 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
17987 | Slave08 EMD-4 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
17988 | Slave08 EMD-5 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
17989 | Slave08 EMD-6 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
17990 | Slave08 EMD-7 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
17991 | Slave08 EMD-8 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
17992 | Slave09 EMD-1 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
17993 | Slave09 EMD-2 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
17994 | Slave09 EMD-3 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
17995 | Slave09 EMD-4 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
17996 | Slave09 EMD-5 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
17997 | Slave09 EMD-6 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
17998 | Slave09 EMD-7 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
17999 | Slave09 EMD-8 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
18000 | Slave10 EMD-1 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
18001 | Slave10 EMD-2 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
18002 | Slave10 EMD-3 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
18003 | Slave10 EMD-4 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
18004 | Slave10 EMD-5 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
18005 | Slave10 EMD-6 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
18006 | Slave10 EMD-7 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
18007 | Slave10 EMD-8 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
18008 | Slave11 EMD-1 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
18009 | Slave11 EMD-2 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
18010 | Slave11 EMD-3 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
18011 | Slave11 EMD-4 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
18012 | Slave11 EMD-5 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
18013 | Slave11 EMD-6 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
18014 | Slave11 EMD-7 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
18015 | Slave11 EMD-8 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
18016 | Slave12 EMD-1 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
18017 | Slave12 EMD-2 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
18018 | Slave12 EMD-3 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
18019 | Slave12 EMD-4 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
18020 | Slave12 EMD-5 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
18021 | Slave12 EMD-6 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
18022 | Slave12 EMD-7 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
18023 | Slave12 EMD-8 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
18024 | Slave13 EMD-1 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
18025 | Slave13 EMD-2 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
18026 | Slave13 EMD-3 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
18027 | Slave13 EMD-4 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
18028 | Slave13 EMD-5 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
18029 | Slave13 EMD-6 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
18030 | Slave13 EMD-7 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
18031 | Slave13 EMD-8 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
18032 | Slave14 EMD-1 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
18033 | Slave14 EMD-2 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
18034 | Slave14 EMD-3 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
18035 | Slave14 EMD-4 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
18036 | Slave14 EMD-5 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
18037 | Slave14 EMD-6 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
18038 | Slave14 EMD-7 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
18039 | Slave14 EMD-8 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
18040 | Slave15 EMD-1 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
18041 | Slave15 EMD-2 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
18042 | Slave15 EMD-3 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
18043 | Slave15 EMD-4 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
18044 | Slave15 EMD-5 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
18045 | Slave15 EMD-6 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
18046 | Slave15 EMD-7 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
18047 | Slave15 EMD-8 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
18048 | Master EMD-1 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
18049 | Master EMD-2 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
18050 | Master EMD-3 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
18051 | Master EMD-4 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
18052 | Master EMD-5 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
18053 | Master EMD-6 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
18054 | Master EMD-7 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
18055 | Master EMD-8 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
18056 | Slave01 EMD-1 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
18057 | Slave01 EMD-2 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
18058 | Slave01 EMD-3 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
18059 | Slave01 EMD-4 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
18060 | Slave01 EMD-5 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
18061 | Slave01 EMD-6 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
18062 | Slave01 EMD-7 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
18063 | Slave01 EMD-8 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
18064 | Slave02 EMD-1 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
18065 | Slave02 EMD-2 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
18066 | Slave02 EMD-3 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
18067 | Slave02 EMD-4 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
18068 | Slave02 EMD-5 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
18069 | Slave02 EMD-6 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
18070 | Slave02 EMD-7 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
18071 | Slave02 EMD-8 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
18072 | Slave03 EMD-1 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
18073 | Slave03 EMD-2 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
18074 | Slave03 EMD-3 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
18075 | Slave03 EMD-4 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
18076 | Slave03 EMD-5 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
18077 | Slave03 EMD-6 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
18078 | Slave03 EMD-7 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
18079 | Slave03 EMD-8 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
18080 | Slave04 EMD-1 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
18081 | Slave04 EMD-2 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
18082 | Slave04 EMD-3 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
18083 | Slave04 EMD-4 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
18084 | Slave04 EMD-5 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
18085 | Slave04 EMD-6 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
18086 | Slave04 EMD-7 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
18087 | Slave04 EMD-8 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
18088 | Slave05 EMD-1 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
18089 | Slave05 EMD-2 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
18090 | Slave05 EMD-3 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
18091 | Slave05 EMD-4 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
18092 | Slave05 EMD-5 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
18093 | Slave05 EMD-6 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
18094 | Slave05 EMD-7 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
18095 | Slave05 EMD-8 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
18096 | Slave06 EMD-1 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
18097 | Slave06 EMD-2 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
18098 | Slave06 EMD-3 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
18099 | Slave06 EMD-4 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
18100 | Slave06 EMD-5 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
18101 | Slave06 EMD-6 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
18102 | Slave06 EMD-7 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
18103 | Slave06 EMD-8 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
18104 | Slave07 EMD-1 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
18105 | Slave07 EMD-2 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
18106 | Slave07 EMD-3 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
18107 | Slave07 EMD-4 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
18108 | Slave07 EMD-5 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
18109 | Slave07 EMD-6 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
18110 | Slave07 EMD-7 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
18111 | Slave07 EMD-8 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
18112 | Slave08 EMD-1 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
18113 | Slave08 EMD-2 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
18114 | Slave08 EMD-3 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
18115 | Slave08 EMD-4 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
18116 | Slave08 EMD-5 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
18117 | Slave08 EMD-6 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
18118 | Slave08 EMD-7 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
18119 | Slave08 EMD-8 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
18120 | Slave09 EMD-1 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
18121 | Slave09 EMD-2 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
18122 | Slave09 EMD-3 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
18123 | Slave09 EMD-4 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
18124 | Slave09 EMD-5 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
18125 | Slave09 EMD-6 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
18126 | Slave09 EMD-7 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
18127 | Slave09 EMD-8 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
18128 | Slave10 EMD-1 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
18129 | Slave10 EMD-2 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
18130 | Slave10 EMD-3 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
18131 | Slave10 EMD-4 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
18132 | Slave10 EMD-5 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
18133 | Slave10 EMD-6 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
18134 | Slave10 EMD-7 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
18135 | Slave10 EMD-8 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
18136 | Slave11 EMD-1 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
18137 | Slave11 EMD-2 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
18138 | Slave11 EMD-3 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
18139 | Slave11 EMD-4 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
18140 | Slave11 EMD-5 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
18141 | Slave11 EMD-6 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
18142 | Slave11 EMD-7 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
18143 | Slave11 EMD-8 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
18144 | Slave12 EMD-1 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
18145 | Slave12 EMD-2 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
18146 | Slave12 EMD-3 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
18147 | Slave12 EMD-4 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
18148 | Slave12 EMD-5 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
18149 | Slave12 EMD-6 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
18150 | Slave12 EMD-7 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
18151 | Slave12 EMD-8 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
18152 | Slave13 EMD-1 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
18153 | Slave13 EMD-2 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
18154 | Slave13 EMD-3 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
18155 | Slave13 EMD-4 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
18156 | Slave13 EMD-5 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
18157 | Slave13 EMD-6 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
18158 | Slave13 EMD-7 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
18159 | Slave13 EMD-8 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
18160 | Slave14 EMD-1 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
18161 | Slave14 EMD-2 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
18162 | Slave14 EMD-3 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
18163 | Slave14 EMD-4 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
18164 | Slave14 EMD-5 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
18165 | Slave14 EMD-6 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
18166 | Slave14 EMD-7 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
18167 | Slave14 EMD-8 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
18168 | Slave15 EMD-1 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
18169 | Slave15 EMD-2 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
18170 | Slave15 EMD-3 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
18171 | Slave15 EMD-4 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
18172 | Slave15 EMD-5 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
18173 | Slave15 EMD-6 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
18174 | Slave15 EMD-7 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
18175 | Slave15 EMD-8 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
18176 | Master EMD-1 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
18177 | Master EMD-2 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
18178 | Master EMD-3 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
18179 | Master EMD-4 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
18180 | Master EMD-5 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
18181 | Master EMD-6 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
18182 | Master EMD-7 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
18183 | Master EMD-8 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
18184 | Slave01 EMD-1 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
18185 | Slave01 EMD-2 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
18186 | Slave01 EMD-3 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
18187 | Slave01 EMD-4 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
18188 | Slave01 EMD-5 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
18189 | Slave01 EMD-6 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
18190 | Slave01 EMD-7 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
18191 | Slave01 EMD-8 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
18192 | Slave02 EMD-1 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
18193 | Slave02 EMD-2 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
18194 | Slave02 EMD-3 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
18195 | Slave02 EMD-4 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
18196 | Slave02 EMD-5 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
18197 | Slave02 EMD-6 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
18198 | Slave02 EMD-7 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
18199 | Slave02 EMD-8 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
18200 | Slave03 EMD-1 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
18201 | Slave03 EMD-2 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
18202 | Slave03 EMD-3 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
18203 | Slave03 EMD-4 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
18204 | Slave03 EMD-5 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
18205 | Slave03 EMD-6 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
18206 | Slave03 EMD-7 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
18207 | Slave03 EMD-8 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
18208 | Slave04 EMD-1 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
18209 | Slave04 EMD-2 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
18210 | Slave04 EMD-3 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
18211 | Slave04 EMD-4 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
18212 | Slave04 EMD-5 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
18213 | Slave04 EMD-6 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
18214 | Slave04 EMD-7 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
18215 | Slave04 EMD-8 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
18216 | Slave05 EMD-1 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
18217 | Slave05 EMD-2 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
18218 | Slave05 EMD-3 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
18219 | Slave05 EMD-4 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
18220 | Slave05 EMD-5 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
18221 | Slave05 EMD-6 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
18222 | Slave05 EMD-7 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
18223 | Slave05 EMD-8 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
18224 | Slave06 EMD-1 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
18225 | Slave06 EMD-2 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
18226 | Slave06 EMD-3 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
18227 | Slave06 EMD-4 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
18228 | Slave06 EMD-5 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
18229 | Slave06 EMD-6 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
18230 | Slave06 EMD-7 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
18231 | Slave06 EMD-8 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
18232 | Slave07 EMD-1 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
18233 | Slave07 EMD-2 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
18234 | Slave07 EMD-3 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
18235 | Slave07 EMD-4 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
18236 | Slave07 EMD-5 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
18237 | Slave07 EMD-6 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
18238 | Slave07 EMD-7 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
18239 | Slave07 EMD-8 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
18240 | Slave08 EMD-1 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
18241 | Slave08 EMD-2 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
18242 | Slave08 EMD-3 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
18243 | Slave08 EMD-4 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
18244 | Slave08 EMD-5 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
18245 | Slave08 EMD-6 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
18246 | Slave08 EMD-7 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
18247 | Slave08 EMD-8 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
18248 | Slave09 EMD-1 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
18249 | Slave09 EMD-2 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
18250 | Slave09 EMD-3 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
18251 | Slave09 EMD-4 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
18252 | Slave09 EMD-5 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
18253 | Slave09 EMD-6 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
18254 | Slave09 EMD-7 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
18255 | Slave09 EMD-8 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
18256 | Slave10 EMD-1 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
18257 | Slave10 EMD-2 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
18258 | Slave10 EMD-3 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
18259 | Slave10 EMD-4 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
18260 | Slave10 EMD-5 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
18261 | Slave10 EMD-6 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
18262 | Slave10 EMD-7 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
18263 | Slave10 EMD-8 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
18264 | Slave11 EMD-1 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
18265 | Slave11 EMD-2 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
18266 | Slave11 EMD-3 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
18267 | Slave11 EMD-4 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
18268 | Slave11 EMD-5 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
18269 | Slave11 EMD-6 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
18270 | Slave11 EMD-7 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
18271 | Slave11 EMD-8 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
18272 | Slave12 EMD-1 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
18273 | Slave12 EMD-2 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
18274 | Slave12 EMD-3 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
18275 | Slave12 EMD-4 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
18276 | Slave12 EMD-5 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
18277 | Slave12 EMD-6 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
18278 | Slave12 EMD-7 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
18279 | Slave12 EMD-8 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
18280 | Slave13 EMD-1 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
18281 | Slave13 EMD-2 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
18282 | Slave13 EMD-3 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
18283 | Slave13 EMD-4 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
18284 | Slave13 EMD-5 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
18285 | Slave13 EMD-6 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
18286 | Slave13 EMD-7 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
18287 | Slave13 EMD-8 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
18288 | Slave14 EMD-1 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
18289 | Slave14 EMD-2 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
18290 | Slave14 EMD-3 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
18291 | Slave14 EMD-4 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
18292 | Slave14 EMD-5 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
18293 | Slave14 EMD-6 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
18294 | Slave14 EMD-7 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
18295 | Slave14 EMD-8 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
18296 | Slave15 EMD-1 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
18297 | Slave15 EMD-2 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
18298 | Slave15 EMD-3 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
18299 | Slave15 EMD-4 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
18300 | Slave15 EMD-5 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
18301 | Slave15 EMD-6 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
18302 | Slave15 EMD-7 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
18303 | Slave15 EMD-8 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
18304 | Master EMD-1 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
18305 | Master EMD-2 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
18306 | Master EMD-3 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
18307 | Master EMD-4 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
18308 | Master EMD-5 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
18309 | Master EMD-6 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
18310 | Master EMD-7 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
18311 | Master EMD-8 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
18312 | Slave01 EMD-1 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
18313 | Slave01 EMD-2 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
18314 | Slave01 EMD-3 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
18315 | Slave01 EMD-4 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
18316 | Slave01 EMD-5 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
18317 | Slave01 EMD-6 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
18318 | Slave01 EMD-7 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
18319 | Slave01 EMD-8 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
18320 | Slave02 EMD-1 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
18321 | Slave02 EMD-2 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
18322 | Slave02 EMD-3 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
18323 | Slave02 EMD-4 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
18324 | Slave02 EMD-5 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
18325 | Slave02 EMD-6 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
18326 | Slave02 EMD-7 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
18327 | Slave02 EMD-8 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
18328 | Slave03 EMD-1 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
18329 | Slave03 EMD-2 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
18330 | Slave03 EMD-3 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
18331 | Slave03 EMD-4 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
18332 | Slave03 EMD-5 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
18333 | Slave03 EMD-6 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
18334 | Slave03 EMD-7 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
18335 | Slave03 EMD-8 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
18336 | Slave04 EMD-1 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
18337 | Slave04 EMD-2 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
18338 | Slave04 EMD-3 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
18339 | Slave04 EMD-4 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
18340 | Slave04 EMD-5 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
18341 | Slave04 EMD-6 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
18342 | Slave04 EMD-7 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
18343 | Slave04 EMD-8 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
18344 | Slave05 EMD-1 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
18345 | Slave05 EMD-2 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
18346 | Slave05 EMD-3 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
18347 | Slave05 EMD-4 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
18348 | Slave05 EMD-5 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
18349 | Slave05 EMD-6 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
18350 | Slave05 EMD-7 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
18351 | Slave05 EMD-8 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
18352 | Slave06 EMD-1 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
18353 | Slave06 EMD-2 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
18354 | Slave06 EMD-3 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
18355 | Slave06 EMD-4 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
18356 | Slave06 EMD-5 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
18357 | Slave06 EMD-6 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
18358 | Slave06 EMD-7 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
18359 | Slave06 EMD-8 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
18360 | Slave07 EMD-1 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
18361 | Slave07 EMD-2 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
18362 | Slave07 EMD-3 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
18363 | Slave07 EMD-4 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
18364 | Slave07 EMD-5 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
18365 | Slave07 EMD-6 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
18366 | Slave07 EMD-7 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
18367 | Slave07 EMD-8 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
18368 | Slave08 EMD-1 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
18369 | Slave08 EMD-2 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
18370 | Slave08 EMD-3 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
18371 | Slave08 EMD-4 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
18372 | Slave08 EMD-5 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
18373 | Slave08 EMD-6 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
18374 | Slave08 EMD-7 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
18375 | Slave08 EMD-8 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
18376 | Slave09 EMD-1 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
18377 | Slave09 EMD-2 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
18378 | Slave09 EMD-3 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
18379 | Slave09 EMD-4 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
18380 | Slave09 EMD-5 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
18381 | Slave09 EMD-6 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
18382 | Slave09 EMD-7 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
18383 | Slave09 EMD-8 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
18384 | Slave10 EMD-1 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
18385 | Slave10 EMD-2 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
18386 | Slave10 EMD-3 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
18387 | Slave10 EMD-4 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
18388 | Slave10 EMD-5 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
18389 | Slave10 EMD-6 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
18390 | Slave10 EMD-7 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
18391 | Slave10 EMD-8 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
18392 | Slave11 EMD-1 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
18393 | Slave11 EMD-2 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
18394 | Slave11 EMD-3 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
18395 | Slave11 EMD-4 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
18396 | Slave11 EMD-5 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
18397 | Slave11 EMD-6 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
18398 | Slave11 EMD-7 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
18399 | Slave11 EMD-8 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
18400 | Slave12 EMD-1 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
18401 | Slave12 EMD-2 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
18402 | Slave12 EMD-3 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
18403 | Slave12 EMD-4 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
18404 | Slave12 EMD-5 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
18405 | Slave12 EMD-6 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
18406 | Slave12 EMD-7 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
18407 | Slave12 EMD-8 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
18408 | Slave13 EMD-1 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
18409 | Slave13 EMD-2 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
18410 | Slave13 EMD-3 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
18411 | Slave13 EMD-4 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
18412 | Slave13 EMD-5 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
18413 | Slave13 EMD-6 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
18414 | Slave13 EMD-7 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
18415 | Slave13 EMD-8 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
18416 | Slave14 EMD-1 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
18417 | Slave14 EMD-2 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
18418 | Slave14 EMD-3 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
18419 | Slave14 EMD-4 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
18420 | Slave14 EMD-5 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
18421 | Slave14 EMD-6 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
18422 | Slave14 EMD-7 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
18423 | Slave14 EMD-8 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
18424 | Slave15 EMD-1 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
18425 | Slave15 EMD-2 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
18426 | Slave15 EMD-3 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
18427 | Slave15 EMD-4 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
18428 | Slave15 EMD-5 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
18429 | Slave15 EMD-6 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
18430 | Slave15 EMD-7 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
18431 | Slave15 EMD-8 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
18432 | Master EMD-1 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18433 | Master EMD-2 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18434 | Master EMD-3 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18435 | Master EMD-4 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18436 | Master EMD-5 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18437 | Master EMD-6 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18438 | Master EMD-7 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18439 | Master EMD-8 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18440 | Slave01 EMD-1 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18441 | Slave01 EMD-2 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18442 | Slave01 EMD-3 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18443 | Slave01 EMD-4 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18444 | Slave01 EMD-5 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18445 | Slave01 EMD-6 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18446 | Slave01 EMD-7 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18447 | Slave01 EMD-8 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18448 | Slave02 EMD-1 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18449 | Slave02 EMD-2 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18450 | Slave02 EMD-3 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18451 | Slave02 EMD-4 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18452 | Slave02 EMD-5 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18453 | Slave02 EMD-6 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18454 | Slave02 EMD-7 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18455 | Slave02 EMD-8 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18456 | Slave03 EMD-1 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18457 | Slave03 EMD-2 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18458 | Slave03 EMD-3 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18459 | Slave03 EMD-4 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18460 | Slave03 EMD-5 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18461 | Slave03 EMD-6 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18462 | Slave03 EMD-7 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18463 | Slave03 EMD-8 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18464 | Slave04 EMD-1 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18465 | Slave04 EMD-2 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18466 | Slave04 EMD-3 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18467 | Slave04 EMD-4 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18468 | Slave04 EMD-5 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18469 | Slave04 EMD-6 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18470 | Slave04 EMD-7 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18471 | Slave04 EMD-8 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18472 | Slave05 EMD-1 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18473 | Slave05 EMD-2 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18474 | Slave05 EMD-3 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18475 | Slave05 EMD-4 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18476 | Slave05 EMD-5 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18477 | Slave05 EMD-6 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18478 | Slave05 EMD-7 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18479 | Slave05 EMD-8 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18480 | Slave06 EMD-1 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18481 | Slave06 EMD-2 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18482 | Slave06 EMD-3 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18483 | Slave06 EMD-4 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18484 | Slave06 EMD-5 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18485 | Slave06 EMD-6 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18486 | Slave06 EMD-7 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18487 | Slave06 EMD-8 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18488 | Slave07 EMD-1 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18489 | Slave07 EMD-2 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18490 | Slave07 EMD-3 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18491 | Slave07 EMD-4 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18492 | Slave07 EMD-5 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18493 | Slave07 EMD-6 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18494 | Slave07 EMD-7 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18495 | Slave07 EMD-8 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18496 | Slave08 EMD-1 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18497 | Slave08 EMD-2 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18498 | Slave08 EMD-3 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18499 | Slave08 EMD-4 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18500 | Slave08 EMD-5 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18501 | Slave08 EMD-6 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18502 | Slave08 EMD-7 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18503 | Slave08 EMD-8 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18504 | Slave09 EMD-1 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18505 | Slave09 EMD-2 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18506 | Slave09 EMD-3 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18507 | Slave09 EMD-4 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18508 | Slave09 EMD-5 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18509 | Slave09 EMD-6 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18510 | Slave09 EMD-7 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18511 | Slave09 EMD-8 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18512 | Slave10 EMD-1 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18513 | Slave10 EMD-2 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18514 | Slave10 EMD-3 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18515 | Slave10 EMD-4 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18516 | Slave10 EMD-5 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18517 | Slave10 EMD-6 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18518 | Slave10 EMD-7 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18519 | Slave10 EMD-8 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18520 | Slave11 EMD-1 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18521 | Slave11 EMD-2 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18522 | Slave11 EMD-3 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18523 | Slave11 EMD-4 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18524 | Slave11 EMD-5 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18525 | Slave11 EMD-6 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18526 | Slave11 EMD-7 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18527 | Slave11 EMD-8 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18528 | Slave12 EMD-1 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18529 | Slave12 EMD-2 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18530 | Slave12 EMD-3 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18531 | Slave12 EMD-4 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18532 | Slave12 EMD-5 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18533 | Slave12 EMD-6 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18534 | Slave12 EMD-7 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18535 | Slave12 EMD-8 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18536 | Slave13 EMD-1 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18537 | Slave13 EMD-2 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18538 | Slave13 EMD-3 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18539 | Slave13 EMD-4 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18540 | Slave13 EMD-5 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18541 | Slave13 EMD-6 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18542 | Slave13 EMD-7 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18543 | Slave13 EMD-8 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18544 | Slave14 EMD-1 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18545 | Slave14 EMD-2 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18546 | Slave14 EMD-3 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18547 | Slave14 EMD-4 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18548 | Slave14 EMD-5 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18549 | Slave14 EMD-6 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18550 | Slave14 EMD-7 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18551 | Slave14 EMD-8 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18552 | Slave15 EMD-1 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18553 | Slave15 EMD-2 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18554 | Slave15 EMD-3 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18555 | Slave15 EMD-4 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18556 | Slave15 EMD-5 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18557 | Slave15 EMD-6 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18558 | Slave15 EMD-7 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18559 | Slave15 EMD-8 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18560 | Master EMD-1 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18561 | Master EMD-2 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18562 | Master EMD-3 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18563 | Master EMD-4 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18564 | Master EMD-5 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18565 | Master EMD-6 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18566 | Master EMD-7 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18567 | Master EMD-8 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18568 | Slave01 EMD-1 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18569 | Slave01 EMD-2 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18570 | Slave01 EMD-3 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18571 | Slave01 EMD-4 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18572 | Slave01 EMD-5 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18573 | Slave01 EMD-6 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18574 | Slave01 EMD-7 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18575 | Slave01 EMD-8 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18576 | Slave02 EMD-1 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18577 | Slave02 EMD-2 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18578 | Slave02 EMD-3 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18579 | Slave02 EMD-4 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18580 | Slave02 EMD-5 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18581 | Slave02 EMD-6 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18582 | Slave02 EMD-7 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18583 | Slave02 EMD-8 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18584 | Slave03 EMD-1 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18585 | Slave03 EMD-2 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18586 | Slave03 EMD-3 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18587 | Slave03 EMD-4 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18588 | Slave03 EMD-5 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18589 | Slave03 EMD-6 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18590 | Slave03 EMD-7 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18591 | Slave03 EMD-8 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18592 | Slave04 EMD-1 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18593 | Slave04 EMD-2 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18594 | Slave04 EMD-3 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18595 | Slave04 EMD-4 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18596 | Slave04 EMD-5 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18597 | Slave04 EMD-6 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18598 | Slave04 EMD-7 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18599 | Slave04 EMD-8 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18600 | Slave05 EMD-1 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18601 | Slave05 EMD-2 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18602 | Slave05 EMD-3 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18603 | Slave05 EMD-4 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18604 | Slave05 EMD-5 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18605 | Slave05 EMD-6 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18606 | Slave05 EMD-7 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18607 | Slave05 EMD-8 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18608 | Slave06 EMD-1 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18609 | Slave06 EMD-2 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18610 | Slave06 EMD-3 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18611 | Slave06 EMD-4 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18612 | Slave06 EMD-5 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18613 | Slave06 EMD-6 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18614 | Slave06 EMD-7 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18615 | Slave06 EMD-8 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18616 | Slave07 EMD-1 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18617 | Slave07 EMD-2 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18618 | Slave07 EMD-3 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18619 | Slave07 EMD-4 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18620 | Slave07 EMD-5 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18621 | Slave07 EMD-6 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18622 | Slave07 EMD-7 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18623 | Slave07 EMD-8 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18624 | Slave08 EMD-1 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18625 | Slave08 EMD-2 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18626 | Slave08 EMD-3 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18627 | Slave08 EMD-4 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18628 | Slave08 EMD-5 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18629 | Slave08 EMD-6 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18630 | Slave08 EMD-7 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18631 | Slave08 EMD-8 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18632 | Slave09 EMD-1 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18633 | Slave09 EMD-2 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18634 | Slave09 EMD-3 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18635 | Slave09 EMD-4 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18636 | Slave09 EMD-5 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18637 | Slave09 EMD-6 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18638 | Slave09 EMD-7 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18639 | Slave09 EMD-8 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18640 | Slave10 EMD-1 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18641 | Slave10 EMD-2 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18642 | Slave10 EMD-3 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18643 | Slave10 EMD-4 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18644 | Slave10 EMD-5 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18645 | Slave10 EMD-6 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18646 | Slave10 EMD-7 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18647 | Slave10 EMD-8 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18648 | Slave11 EMD-1 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18649 | Slave11 EMD-2 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18650 | Slave11 EMD-3 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18651 | Slave11 EMD-4 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18652 | Slave11 EMD-5 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18653 | Slave11 EMD-6 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18654 | Slave11 EMD-7 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18655 | Slave11 EMD-8 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18656 | Slave12 EMD-1 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18657 | Slave12 EMD-2 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18658 | Slave12 EMD-3 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18659 | Slave12 EMD-4 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18660 | Slave12 EMD-5 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18661 | Slave12 EMD-6 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18662 | Slave12 EMD-7 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18663 | Slave12 EMD-8 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18664 | Slave13 EMD-1 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18665 | Slave13 EMD-2 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18666 | Slave13 EMD-3 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18667 | Slave13 EMD-4 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18668 | Slave13 EMD-5 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18669 | Slave13 EMD-6 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18670 | Slave13 EMD-7 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18671 | Slave13 EMD-8 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18672 | Slave14 EMD-1 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18673 | Slave14 EMD-2 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18674 | Slave14 EMD-3 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18675 | Slave14 EMD-4 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18676 | Slave14 EMD-5 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18677 | Slave14 EMD-6 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18678 | Slave14 EMD-7 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18679 | Slave14 EMD-8 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18680 | Slave15 EMD-1 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18681 | Slave15 EMD-2 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18682 | Slave15 EMD-3 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18683 | Slave15 EMD-4 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18684 | Slave15 EMD-5 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18685 | Slave15 EMD-6 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18686 | Slave15 EMD-7 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18687 | Slave15 EMD-8 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18688 | Master EMD-1 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18689 | Master EMD-2 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18690 | Master EMD-3 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18691 | Master EMD-4 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18692 | Master EMD-5 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18693 | Master EMD-6 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18694 | Master EMD-7 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18695 | Master EMD-8 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18696 | Slave01 EMD-1 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18697 | Slave01 EMD-2 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18698 | Slave01 EMD-3 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18699 | Slave01 EMD-4 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18700 | Slave01 EMD-5 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18701 | Slave01 EMD-6 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18702 | Slave01 EMD-7 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18703 | Slave01 EMD-8 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18704 | Slave02 EMD-1 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18705 | Slave02 EMD-2 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18706 | Slave02 EMD-3 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18707 | Slave02 EMD-4 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18708 | Slave02 EMD-5 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18709 | Slave02 EMD-6 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18710 | Slave02 EMD-7 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18711 | Slave02 EMD-8 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18712 | Slave03 EMD-1 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18713 | Slave03 EMD-2 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18714 | Slave03 EMD-3 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18715 | Slave03 EMD-4 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18716 | Slave03 EMD-5 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18717 | Slave03 EMD-6 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18718 | Slave03 EMD-7 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18719 | Slave03 EMD-8 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18720 | Slave04 EMD-1 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18721 | Slave04 EMD-2 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18722 | Slave04 EMD-3 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18723 | Slave04 EMD-4 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18724 | Slave04 EMD-5 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18725 | Slave04 EMD-6 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18726 | Slave04 EMD-7 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18727 | Slave04 EMD-8 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18728 | Slave05 EMD-1 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18729 | Slave05 EMD-2 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18730 | Slave05 EMD-3 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18731 | Slave05 EMD-4 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18732 | Slave05 EMD-5 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18733 | Slave05 EMD-6 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18734 | Slave05 EMD-7 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18735 | Slave05 EMD-8 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18736 | Slave06 EMD-1 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18737 | Slave06 EMD-2 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18738 | Slave06 EMD-3 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18739 | Slave06 EMD-4 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18740 | Slave06 EMD-5 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18741 | Slave06 EMD-6 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18742 | Slave06 EMD-7 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18743 | Slave06 EMD-8 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18744 | Slave07 EMD-1 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18745 | Slave07 EMD-2 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18746 | Slave07 EMD-3 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18747 | Slave07 EMD-4 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18748 | Slave07 EMD-5 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18749 | Slave07 EMD-6 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18750 | Slave07 EMD-7 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18751 | Slave07 EMD-8 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18752 | Slave08 EMD-1 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18753 | Slave08 EMD-2 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18754 | Slave08 EMD-3 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18755 | Slave08 EMD-4 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18756 | Slave08 EMD-5 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18757 | Slave08 EMD-6 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18758 | Slave08 EMD-7 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18759 | Slave08 EMD-8 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18760 | Slave09 EMD-1 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18761 | Slave09 EMD-2 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18762 | Slave09 EMD-3 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18763 | Slave09 EMD-4 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18764 | Slave09 EMD-5 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18765 | Slave09 EMD-6 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18766 | Slave09 EMD-7 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18767 | Slave09 EMD-8 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18768 | Slave10 EMD-1 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18769 | Slave10 EMD-2 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18770 | Slave10 EMD-3 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18771 | Slave10 EMD-4 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18772 | Slave10 EMD-5 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18773 | Slave10 EMD-6 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18774 | Slave10 EMD-7 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18775 | Slave10 EMD-8 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18776 | Slave11 EMD-1 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18777 | Slave11 EMD-2 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18778 | Slave11 EMD-3 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18779 | Slave11 EMD-4 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18780 | Slave11 EMD-5 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18781 | Slave11 EMD-6 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18782 | Slave11 EMD-7 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18783 | Slave11 EMD-8 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18784 | Slave12 EMD-1 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18785 | Slave12 EMD-2 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18786 | Slave12 EMD-3 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18787 | Slave12 EMD-4 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18788 | Slave12 EMD-5 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18789 | Slave12 EMD-6 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18790 | Slave12 EMD-7 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18791 | Slave12 EMD-8 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18792 | Slave13 EMD-1 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18793 | Slave13 EMD-2 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18794 | Slave13 EMD-3 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18795 | Slave13 EMD-4 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18796 | Slave13 EMD-5 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18797 | Slave13 EMD-6 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18798 | Slave13 EMD-7 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18799 | Slave13 EMD-8 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18800 | Slave14 EMD-1 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18801 | Slave14 EMD-2 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18802 | Slave14 EMD-3 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18803 | Slave14 EMD-4 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18804 | Slave14 EMD-5 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18805 | Slave14 EMD-6 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18806 | Slave14 EMD-7 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18807 | Slave14 EMD-8 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18808 | Slave15 EMD-1 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18809 | Slave15 EMD-2 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18810 | Slave15 EMD-3 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18811 | Slave15 EMD-4 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18812 | Slave15 EMD-5 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18813 | Slave15 EMD-6 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18814 | Slave15 EMD-7 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18815 | Slave15 EMD-8 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18816 | Master EMD-1 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18817 | Master EMD-2 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18818 | Master EMD-3 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18819 | Master EMD-4 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18820 | Master EMD-5 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18821 | Master EMD-6 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18822 | Master EMD-7 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18823 | Master EMD-8 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18824 | Slave01 EMD-1 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18825 | Slave01 EMD-2 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18826 | Slave01 EMD-3 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18827 | Slave01 EMD-4 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18828 | Slave01 EMD-5 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18829 | Slave01 EMD-6 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18830 | Slave01 EMD-7 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18831 | Slave01 EMD-8 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18832 | Slave02 EMD-1 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18833 | Slave02 EMD-2 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18834 | Slave02 EMD-3 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18835 | Slave02 EMD-4 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18836 | Slave02 EMD-5 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18837 | Slave02 EMD-6 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18838 | Slave02 EMD-7 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18839 | Slave02 EMD-8 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18840 | Slave03 EMD-1 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18841 | Slave03 EMD-2 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18842 | Slave03 EMD-3 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18843 | Slave03 EMD-4 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18844 | Slave03 EMD-5 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18845 | Slave03 EMD-6 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18846 | Slave03 EMD-7 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18847 | Slave03 EMD-8 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18848 | Slave04 EMD-1 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18849 | Slave04 EMD-2 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18850 | Slave04 EMD-3 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18851 | Slave04 EMD-4 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18852 | Slave04 EMD-5 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18853 | Slave04 EMD-6 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18854 | Slave04 EMD-7 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18855 | Slave04 EMD-8 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18856 | Slave05 EMD-1 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18857 | Slave05 EMD-2 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18858 | Slave05 EMD-3 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18859 | Slave05 EMD-4 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18860 | Slave05 EMD-5 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18861 | Slave05 EMD-6 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18862 | Slave05 EMD-7 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18863 | Slave05 EMD-8 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18864 | Slave06 EMD-1 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18865 | Slave06 EMD-2 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18866 | Slave06 EMD-3 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18867 | Slave06 EMD-4 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18868 | Slave06 EMD-5 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18869 | Slave06 EMD-6 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18870 | Slave06 EMD-7 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18871 | Slave06 EMD-8 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18872 | Slave07 EMD-1 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18873 | Slave07 EMD-2 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18874 | Slave07 EMD-3 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18875 | Slave07 EMD-4 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18876 | Slave07 EMD-5 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18877 | Slave07 EMD-6 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18878 | Slave07 EMD-7 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18879 | Slave07 EMD-8 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18880 | Slave08 EMD-1 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18881 | Slave08 EMD-2 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18882 | Slave08 EMD-3 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18883 | Slave08 EMD-4 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18884 | Slave08 EMD-5 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18885 | Slave08 EMD-6 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18886 | Slave08 EMD-7 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18887 | Slave08 EMD-8 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18888 | Slave09 EMD-1 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18889 | Slave09 EMD-2 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18890 | Slave09 EMD-3 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18891 | Slave09 EMD-4 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18892 | Slave09 EMD-5 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18893 | Slave09 EMD-6 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18894 | Slave09 EMD-7 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18895 | Slave09 EMD-8 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18896 | Slave10 EMD-1 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18897 | Slave10 EMD-2 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18898 | Slave10 EMD-3 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18899 | Slave10 EMD-4 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18900 | Slave10 EMD-5 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18901 | Slave10 EMD-6 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18902 | Slave10 EMD-7 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18903 | Slave10 EMD-8 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18904 | Slave11 EMD-1 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18905 | Slave11 EMD-2 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18906 | Slave11 EMD-3 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18907 | Slave11 EMD-4 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18908 | Slave11 EMD-5 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18909 | Slave11 EMD-6 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18910 | Slave11 EMD-7 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18911 | Slave11 EMD-8 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18912 | Slave12 EMD-1 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18913 | Slave12 EMD-2 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18914 | Slave12 EMD-3 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18915 | Slave12 EMD-4 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18916 | Slave12 EMD-5 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18917 | Slave12 EMD-6 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18918 | Slave12 EMD-7 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18919 | Slave12 EMD-8 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18920 | Slave13 EMD-1 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18921 | Slave13 EMD-2 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18922 | Slave13 EMD-3 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18923 | Slave13 EMD-4 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18924 | Slave13 EMD-5 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18925 | Slave13 EMD-6 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18926 | Slave13 EMD-7 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18927 | Slave13 EMD-8 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18928 | Slave14 EMD-1 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18929 | Slave14 EMD-2 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18930 | Slave14 EMD-3 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18931 | Slave14 EMD-4 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18932 | Slave14 EMD-5 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18933 | Slave14 EMD-6 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18934 | Slave14 EMD-7 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18935 | Slave14 EMD-8 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18936 | Slave15 EMD-1 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18937 | Slave15 EMD-2 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18938 | Slave15 EMD-3 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18939 | Slave15 EMD-4 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18940 | Slave15 EMD-5 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18941 | Slave15 EMD-6 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18942 | Slave15 EMD-7 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18943 | Slave15 EMD-8 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
18944 | Master EMD-1 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
18945 | Master EMD-2 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
18946 | Master EMD-3 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
18947 | Master EMD-4 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
18948 | Master EMD-5 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
18949 | Master EMD-6 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
18950 | Master EMD-7 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
18951 | Master EMD-8 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
18952 | Slave01 EMD-1 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
18953 | Slave01 EMD-2 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
18954 | Slave01 EMD-3 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
18955 | Slave01 EMD-4 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
18956 | Slave01 EMD-5 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
18957 | Slave01 EMD-6 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
18958 | Slave01 EMD-7 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
18959 | Slave01 EMD-8 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
18960 | Slave02 EMD-1 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
18961 | Slave02 EMD-2 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
18962 | Slave02 EMD-3 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
18963 | Slave02 EMD-4 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
18964 | Slave02 EMD-5 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
18965 | Slave02 EMD-6 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
18966 | Slave02 EMD-7 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
18967 | Slave02 EMD-8 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
18968 | Slave03 EMD-1 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
18969 | Slave03 EMD-2 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
18970 | Slave03 EMD-3 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
18971 | Slave03 EMD-4 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
18972 | Slave03 EMD-5 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
18973 | Slave03 EMD-6 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
18974 | Slave03 EMD-7 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
18975 | Slave03 EMD-8 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
18976 | Slave04 EMD-1 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
18977 | Slave04 EMD-2 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
18978 | Slave04 EMD-3 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
18979 | Slave04 EMD-4 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
18980 | Slave04 EMD-5 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
18981 | Slave04 EMD-6 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
18982 | Slave04 EMD-7 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
18983 | Slave04 EMD-8 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
18984 | Slave05 EMD-1 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
18985 | Slave05 EMD-2 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
18986 | Slave05 EMD-3 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
18987 | Slave05 EMD-4 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
18988 | Slave05 EMD-5 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
18989 | Slave05 EMD-6 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
18990 | Slave05 EMD-7 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
18991 | Slave05 EMD-8 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
18992 | Slave06 EMD-1 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
18993 | Slave06 EMD-2 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
18994 | Slave06 EMD-3 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
18995 | Slave06 EMD-4 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
18996 | Slave06 EMD-5 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
18997 | Slave06 EMD-6 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
18998 | Slave06 EMD-7 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
18999 | Slave06 EMD-8 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
19000 | Slave07 EMD-1 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
19001 | Slave07 EMD-2 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
19002 | Slave07 EMD-3 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
19003 | Slave07 EMD-4 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
19004 | Slave07 EMD-5 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
19005 | Slave07 EMD-6 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
19006 | Slave07 EMD-7 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
19007 | Slave07 EMD-8 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
19008 | Slave08 EMD-1 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
19009 | Slave08 EMD-2 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
19010 | Slave08 EMD-3 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
19011 | Slave08 EMD-4 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
19012 | Slave08 EMD-5 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
19013 | Slave08 EMD-6 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
19014 | Slave08 EMD-7 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
19015 | Slave08 EMD-8 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
19016 | Slave09 EMD-1 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
19017 | Slave09 EMD-2 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
19018 | Slave09 EMD-3 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
19019 | Slave09 EMD-4 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
19020 | Slave09 EMD-5 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
19021 | Slave09 EMD-6 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
19022 | Slave09 EMD-7 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
19023 | Slave09 EMD-8 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
19024 | Slave10 EMD-1 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
19025 | Slave10 EMD-2 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
19026 | Slave10 EMD-3 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
19027 | Slave10 EMD-4 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
19028 | Slave10 EMD-5 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
19029 | Slave10 EMD-6 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
19030 | Slave10 EMD-7 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
19031 | Slave10 EMD-8 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
19032 | Slave11 EMD-1 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
19033 | Slave11 EMD-2 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
19034 | Slave11 EMD-3 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
19035 | Slave11 EMD-4 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
19036 | Slave11 EMD-5 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
19037 | Slave11 EMD-6 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
19038 | Slave11 EMD-7 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
19039 | Slave11 EMD-8 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
19040 | Slave12 EMD-1 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
19041 | Slave12 EMD-2 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
19042 | Slave12 EMD-3 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
19043 | Slave12 EMD-4 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
19044 | Slave12 EMD-5 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
19045 | Slave12 EMD-6 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
19046 | Slave12 EMD-7 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
19047 | Slave12 EMD-8 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
19048 | Slave13 EMD-1 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
19049 | Slave13 EMD-2 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
19050 | Slave13 EMD-3 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
19051 | Slave13 EMD-4 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
19052 | Slave13 EMD-5 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
19053 | Slave13 EMD-6 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
19054 | Slave13 EMD-7 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
19055 | Slave13 EMD-8 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
19056 | Slave14 EMD-1 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
19057 | Slave14 EMD-2 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
19058 | Slave14 EMD-3 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
19059 | Slave14 EMD-4 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
19060 | Slave14 EMD-5 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
19061 | Slave14 EMD-6 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
19062 | Slave14 EMD-7 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
19063 | Slave14 EMD-8 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
19064 | Slave15 EMD-1 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
19065 | Slave15 EMD-2 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
19066 | Slave15 EMD-3 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
19067 | Slave15 EMD-4 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
19068 | Slave15 EMD-5 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
19069 | Slave15 EMD-6 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
19070 | Slave15 EMD-7 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
19071 | Slave15 EMD-8 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
19072 | Master EMD-1 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
19073 | Master EMD-2 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
19074 | Master EMD-3 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
19075 | Master EMD-4 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
19076 | Master EMD-5 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
19077 | Master EMD-6 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
19078 | Master EMD-7 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
19079 | Master EMD-8 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
19080 | Slave01 EMD-1 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
19081 | Slave01 EMD-2 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
19082 | Slave01 EMD-3 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
19083 | Slave01 EMD-4 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
19084 | Slave01 EMD-5 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
19085 | Slave01 EMD-6 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
19086 | Slave01 EMD-7 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
19087 | Slave01 EMD-8 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
19088 | Slave02 EMD-1 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
19089 | Slave02 EMD-2 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
19090 | Slave02 EMD-3 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
19091 | Slave02 EMD-4 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
19092 | Slave02 EMD-5 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
19093 | Slave02 EMD-6 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
19094 | Slave02 EMD-7 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
19095 | Slave02 EMD-8 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
19096 | Slave03 EMD-1 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
19097 | Slave03 EMD-2 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
19098 | Slave03 EMD-3 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
19099 | Slave03 EMD-4 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
19100 | Slave03 EMD-5 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
19101 | Slave03 EMD-6 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
19102 | Slave03 EMD-7 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
19103 | Slave03 EMD-8 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
19104 | Slave04 EMD-1 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
19105 | Slave04 EMD-2 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
19106 | Slave04 EMD-3 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
19107 | Slave04 EMD-4 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
19108 | Slave04 EMD-5 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
19109 | Slave04 EMD-6 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
19110 | Slave04 EMD-7 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
19111 | Slave04 EMD-8 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
19112 | Slave05 EMD-1 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
19113 | Slave05 EMD-2 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
19114 | Slave05 EMD-3 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
19115 | Slave05 EMD-4 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
19116 | Slave05 EMD-5 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
19117 | Slave05 EMD-6 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
19118 | Slave05 EMD-7 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
19119 | Slave05 EMD-8 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
19120 | Slave06 EMD-1 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
19121 | Slave06 EMD-2 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
19122 | Slave06 EMD-3 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
19123 | Slave06 EMD-4 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
19124 | Slave06 EMD-5 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
19125 | Slave06 EMD-6 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
19126 | Slave06 EMD-7 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
19127 | Slave06 EMD-8 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
19128 | Slave07 EMD-1 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
19129 | Slave07 EMD-2 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
19130 | Slave07 EMD-3 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
19131 | Slave07 EMD-4 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
19132 | Slave07 EMD-5 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
19133 | Slave07 EMD-6 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
19134 | Slave07 EMD-7 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
19135 | Slave07 EMD-8 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
19136 | Slave08 EMD-1 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
19137 | Slave08 EMD-2 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
19138 | Slave08 EMD-3 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
19139 | Slave08 EMD-4 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
19140 | Slave08 EMD-5 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
19141 | Slave08 EMD-6 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
19142 | Slave08 EMD-7 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
19143 | Slave08 EMD-8 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
19144 | Slave09 EMD-1 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
19145 | Slave09 EMD-2 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
19146 | Slave09 EMD-3 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
19147 | Slave09 EMD-4 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
19148 | Slave09 EMD-5 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
19149 | Slave09 EMD-6 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
19150 | Slave09 EMD-7 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
19151 | Slave09 EMD-8 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
19152 | Slave10 EMD-1 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
19153 | Slave10 EMD-2 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
19154 | Slave10 EMD-3 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
19155 | Slave10 EMD-4 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
19156 | Slave10 EMD-5 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
19157 | Slave10 EMD-6 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
19158 | Slave10 EMD-7 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
19159 | Slave10 EMD-8 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
19160 | Slave11 EMD-1 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
19161 | Slave11 EMD-2 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
19162 | Slave11 EMD-3 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
19163 | Slave11 EMD-4 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
19164 | Slave11 EMD-5 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
19165 | Slave11 EMD-6 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
19166 | Slave11 EMD-7 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
19167 | Slave11 EMD-8 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
19168 | Slave12 EMD-1 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
19169 | Slave12 EMD-2 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
19170 | Slave12 EMD-3 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
19171 | Slave12 EMD-4 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
19172 | Slave12 EMD-5 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
19173 | Slave12 EMD-6 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
19174 | Slave12 EMD-7 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
19175 | Slave12 EMD-8 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
19176 | Slave13 EMD-1 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
19177 | Slave13 EMD-2 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
19178 | Slave13 EMD-3 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
19179 | Slave13 EMD-4 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
19180 | Slave13 EMD-5 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
19181 | Slave13 EMD-6 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
19182 | Slave13 EMD-7 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
19183 | Slave13 EMD-8 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
19184 | Slave14 EMD-1 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
19185 | Slave14 EMD-2 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
19186 | Slave14 EMD-3 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
19187 | Slave14 EMD-4 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
19188 | Slave14 EMD-5 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
19189 | Slave14 EMD-6 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
19190 | Slave14 EMD-7 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
19191 | Slave14 EMD-8 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
19192 | Slave15 EMD-1 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
19193 | Slave15 EMD-2 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
19194 | Slave15 EMD-3 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
19195 | Slave15 EMD-4 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
19196 | Slave15 EMD-5 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
19197 | Slave15 EMD-6 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
19198 | Slave15 EMD-7 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
19199 | Slave15 EMD-8 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
19200 | Master EMD-1 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
19201 | Master EMD-2 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
19202 | Master EMD-3 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
19203 | Master EMD-4 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
19204 | Master EMD-5 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
19205 | Master EMD-6 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
19206 | Master EMD-7 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
19207 | Master EMD-8 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
19208 | Slave01 EMD-1 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
19209 | Slave01 EMD-2 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
19210 | Slave01 EMD-3 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
19211 | Slave01 EMD-4 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
19212 | Slave01 EMD-5 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
19213 | Slave01 EMD-6 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
19214 | Slave01 EMD-7 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
19215 | Slave01 EMD-8 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
19216 | Slave02 EMD-1 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
19217 | Slave02 EMD-2 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
19218 | Slave02 EMD-3 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
19219 | Slave02 EMD-4 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
19220 | Slave02 EMD-5 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
19221 | Slave02 EMD-6 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
19222 | Slave02 EMD-7 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
19223 | Slave02 EMD-8 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
19224 | Slave03 EMD-1 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
19225 | Slave03 EMD-2 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
19226 | Slave03 EMD-3 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
19227 | Slave03 EMD-4 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
19228 | Slave03 EMD-5 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
19229 | Slave03 EMD-6 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
19230 | Slave03 EMD-7 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
19231 | Slave03 EMD-8 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
19232 | Slave04 EMD-1 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
19233 | Slave04 EMD-2 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
19234 | Slave04 EMD-3 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
19235 | Slave04 EMD-4 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
19236 | Slave04 EMD-5 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
19237 | Slave04 EMD-6 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
19238 | Slave04 EMD-7 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
19239 | Slave04 EMD-8 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
19240 | Slave05 EMD-1 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
19241 | Slave05 EMD-2 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
19242 | Slave05 EMD-3 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
19243 | Slave05 EMD-4 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
19244 | Slave05 EMD-5 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
19245 | Slave05 EMD-6 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
19246 | Slave05 EMD-7 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
19247 | Slave05 EMD-8 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
19248 | Slave06 EMD-1 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
19249 | Slave06 EMD-2 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
19250 | Slave06 EMD-3 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
19251 | Slave06 EMD-4 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
19252 | Slave06 EMD-5 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
19253 | Slave06 EMD-6 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
19254 | Slave06 EMD-7 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
19255 | Slave06 EMD-8 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
19256 | Slave07 EMD-1 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
19257 | Slave07 EMD-2 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
19258 | Slave07 EMD-3 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
19259 | Slave07 EMD-4 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
19260 | Slave07 EMD-5 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
19261 | Slave07 EMD-6 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
19262 | Slave07 EMD-7 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
19263 | Slave07 EMD-8 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
19264 | Slave08 EMD-1 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
19265 | Slave08 EMD-2 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
19266 | Slave08 EMD-3 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
19267 | Slave08 EMD-4 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
19268 | Slave08 EMD-5 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
19269 | Slave08 EMD-6 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
19270 | Slave08 EMD-7 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
19271 | Slave08 EMD-8 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
19272 | Slave09 EMD-1 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
19273 | Slave09 EMD-2 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
19274 | Slave09 EMD-3 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
19275 | Slave09 EMD-4 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
19276 | Slave09 EMD-5 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
19277 | Slave09 EMD-6 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
19278 | Slave09 EMD-7 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
19279 | Slave09 EMD-8 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
19280 | Slave10 EMD-1 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
19281 | Slave10 EMD-2 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
19282 | Slave10 EMD-3 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
19283 | Slave10 EMD-4 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
19284 | Slave10 EMD-5 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
19285 | Slave10 EMD-6 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
19286 | Slave10 EMD-7 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
19287 | Slave10 EMD-8 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
19288 | Slave11 EMD-1 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
19289 | Slave11 EMD-2 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
19290 | Slave11 EMD-3 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
19291 | Slave11 EMD-4 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
19292 | Slave11 EMD-5 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
19293 | Slave11 EMD-6 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
19294 | Slave11 EMD-7 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
19295 | Slave11 EMD-8 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
19296 | Slave12 EMD-1 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
19297 | Slave12 EMD-2 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
19298 | Slave12 EMD-3 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
19299 | Slave12 EMD-4 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
19300 | Slave12 EMD-5 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
19301 | Slave12 EMD-6 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
19302 | Slave12 EMD-7 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
19303 | Slave12 EMD-8 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
19304 | Slave13 EMD-1 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
19305 | Slave13 EMD-2 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
19306 | Slave13 EMD-3 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
19307 | Slave13 EMD-4 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
19308 | Slave13 EMD-5 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
19309 | Slave13 EMD-6 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
19310 | Slave13 EMD-7 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
19311 | Slave13 EMD-8 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
19312 | Slave14 EMD-1 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
19313 | Slave14 EMD-2 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
19314 | Slave14 EMD-3 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
19315 | Slave14 EMD-4 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
19316 | Slave14 EMD-5 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
19317 | Slave14 EMD-6 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
19318 | Slave14 EMD-7 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
19319 | Slave14 EMD-8 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
19320 | Slave15 EMD-1 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
19321 | Slave15 EMD-2 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
19322 | Slave15 EMD-3 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
19323 | Slave15 EMD-4 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
19324 | Slave15 EMD-5 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
19325 | Slave15 EMD-6 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
19326 | Slave15 EMD-7 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
19327 | Slave15 EMD-8 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
19328 | Master EMD-1 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
19329 | Master EMD-2 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
19330 | Master EMD-3 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
19331 | Master EMD-4 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
19332 | Master EMD-5 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
19333 | Master EMD-6 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
19334 | Master EMD-7 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
19335 | Master EMD-8 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
19336 | Slave01 EMD-1 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
19337 | Slave01 EMD-2 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
19338 | Slave01 EMD-3 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
19339 | Slave01 EMD-4 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
19340 | Slave01 EMD-5 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
19341 | Slave01 EMD-6 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
19342 | Slave01 EMD-7 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
19343 | Slave01 EMD-8 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
19344 | Slave02 EMD-1 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
19345 | Slave02 EMD-2 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
19346 | Slave02 EMD-3 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
19347 | Slave02 EMD-4 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
19348 | Slave02 EMD-5 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
19349 | Slave02 EMD-6 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
19350 | Slave02 EMD-7 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
19351 | Slave02 EMD-8 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
19352 | Slave03 EMD-1 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
19353 | Slave03 EMD-2 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
19354 | Slave03 EMD-3 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
19355 | Slave03 EMD-4 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
19356 | Slave03 EMD-5 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
19357 | Slave03 EMD-6 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
19358 | Slave03 EMD-7 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
19359 | Slave03 EMD-8 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
19360 | Slave04 EMD-1 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
19361 | Slave04 EMD-2 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
19362 | Slave04 EMD-3 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
19363 | Slave04 EMD-4 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
19364 | Slave04 EMD-5 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
19365 | Slave04 EMD-6 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
19366 | Slave04 EMD-7 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
19367 | Slave04 EMD-8 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
19368 | Slave05 EMD-1 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
19369 | Slave05 EMD-2 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
19370 | Slave05 EMD-3 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
19371 | Slave05 EMD-4 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
19372 | Slave05 EMD-5 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
19373 | Slave05 EMD-6 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
19374 | Slave05 EMD-7 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
19375 | Slave05 EMD-8 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
19376 | Slave06 EMD-1 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
19377 | Slave06 EMD-2 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
19378 | Slave06 EMD-3 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
19379 | Slave06 EMD-4 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
19380 | Slave06 EMD-5 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
19381 | Slave06 EMD-6 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
19382 | Slave06 EMD-7 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
19383 | Slave06 EMD-8 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
19384 | Slave07 EMD-1 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
19385 | Slave07 EMD-2 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
19386 | Slave07 EMD-3 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
19387 | Slave07 EMD-4 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
19388 | Slave07 EMD-5 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
19389 | Slave07 EMD-6 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
19390 | Slave07 EMD-7 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
19391 | Slave07 EMD-8 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
19392 | Slave08 EMD-1 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
19393 | Slave08 EMD-2 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
19394 | Slave08 EMD-3 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
19395 | Slave08 EMD-4 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
19396 | Slave08 EMD-5 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
19397 | Slave08 EMD-6 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
19398 | Slave08 EMD-7 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
19399 | Slave08 EMD-8 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
19400 | Slave09 EMD-1 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
19401 | Slave09 EMD-2 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
19402 | Slave09 EMD-3 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
19403 | Slave09 EMD-4 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
19404 | Slave09 EMD-5 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
19405 | Slave09 EMD-6 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
19406 | Slave09 EMD-7 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
19407 | Slave09 EMD-8 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
19408 | Slave10 EMD-1 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
19409 | Slave10 EMD-2 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
19410 | Slave10 EMD-3 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
19411 | Slave10 EMD-4 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
19412 | Slave10 EMD-5 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
19413 | Slave10 EMD-6 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
19414 | Slave10 EMD-7 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
19415 | Slave10 EMD-8 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
19416 | Slave11 EMD-1 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
19417 | Slave11 EMD-2 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
19418 | Slave11 EMD-3 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
19419 | Slave11 EMD-4 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
19420 | Slave11 EMD-5 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
19421 | Slave11 EMD-6 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
19422 | Slave11 EMD-7 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
19423 | Slave11 EMD-8 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
19424 | Slave12 EMD-1 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
19425 | Slave12 EMD-2 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
19426 | Slave12 EMD-3 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
19427 | Slave12 EMD-4 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
19428 | Slave12 EMD-5 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
19429 | Slave12 EMD-6 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
19430 | Slave12 EMD-7 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
19431 | Slave12 EMD-8 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
19432 | Slave13 EMD-1 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
19433 | Slave13 EMD-2 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
19434 | Slave13 EMD-3 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
19435 | Slave13 EMD-4 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
19436 | Slave13 EMD-5 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
19437 | Slave13 EMD-6 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
19438 | Slave13 EMD-7 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
19439 | Slave13 EMD-8 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
19440 | Slave14 EMD-1 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
19441 | Slave14 EMD-2 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
19442 | Slave14 EMD-3 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
19443 | Slave14 EMD-4 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
19444 | Slave14 EMD-5 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
19445 | Slave14 EMD-6 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
19446 | Slave14 EMD-7 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
19447 | Slave14 EMD-8 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
19448 | Slave15 EMD-1 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
19449 | Slave15 EMD-2 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
19450 | Slave15 EMD-3 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
19451 | Slave15 EMD-4 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
19452 | Slave15 EMD-5 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
19453 | Slave15 EMD-6 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
19454 | Slave15 EMD-7 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
19455 | Slave15 EMD-8 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
19456 | Master EMD-1 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
19457 | Master EMD-2 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
19458 | Master EMD-3 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
19459 | Master EMD-4 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
19460 | Master EMD-5 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
19461 | Master EMD-6 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
19462 | Master EMD-7 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
19463 | Master EMD-8 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
19464 | Slave01 EMD-1 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
19465 | Slave01 EMD-2 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
19466 | Slave01 EMD-3 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
19467 | Slave01 EMD-4 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
19468 | Slave01 EMD-5 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
19469 | Slave01 EMD-6 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
19470 | Slave01 EMD-7 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
19471 | Slave01 EMD-8 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
19472 | Slave02 EMD-1 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
19473 | Slave02 EMD-2 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
19474 | Slave02 EMD-3 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
19475 | Slave02 EMD-4 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
19476 | Slave02 EMD-5 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
19477 | Slave02 EMD-6 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
19478 | Slave02 EMD-7 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
19479 | Slave02 EMD-8 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
19480 | Slave03 EMD-1 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
19481 | Slave03 EMD-2 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
19482 | Slave03 EMD-3 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
19483 | Slave03 EMD-4 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
19484 | Slave03 EMD-5 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
19485 | Slave03 EMD-6 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
19486 | Slave03 EMD-7 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
19487 | Slave03 EMD-8 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
19488 | Slave04 EMD-1 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
19489 | Slave04 EMD-2 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
19490 | Slave04 EMD-3 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
19491 | Slave04 EMD-4 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
19492 | Slave04 EMD-5 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
19493 | Slave04 EMD-6 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
19494 | Slave04 EMD-7 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
19495 | Slave04 EMD-8 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
19496 | Slave05 EMD-1 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
19497 | Slave05 EMD-2 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
19498 | Slave05 EMD-3 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
19499 | Slave05 EMD-4 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
19500 | Slave05 EMD-5 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
19501 | Slave05 EMD-6 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
19502 | Slave05 EMD-7 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
19503 | Slave05 EMD-8 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
19504 | Slave06 EMD-1 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
19505 | Slave06 EMD-2 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
19506 | Slave06 EMD-3 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
19507 | Slave06 EMD-4 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
19508 | Slave06 EMD-5 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
19509 | Slave06 EMD-6 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
19510 | Slave06 EMD-7 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
19511 | Slave06 EMD-8 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
19512 | Slave07 EMD-1 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
19513 | Slave07 EMD-2 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
19514 | Slave07 EMD-3 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
19515 | Slave07 EMD-4 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
19516 | Slave07 EMD-5 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
19517 | Slave07 EMD-6 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
19518 | Slave07 EMD-7 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
19519 | Slave07 EMD-8 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
19520 | Slave08 EMD-1 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
19521 | Slave08 EMD-2 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
19522 | Slave08 EMD-3 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
19523 | Slave08 EMD-4 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
19524 | Slave08 EMD-5 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
19525 | Slave08 EMD-6 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
19526 | Slave08 EMD-7 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
19527 | Slave08 EMD-8 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
19528 | Slave09 EMD-1 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
19529 | Slave09 EMD-2 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
19530 | Slave09 EMD-3 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
19531 | Slave09 EMD-4 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
19532 | Slave09 EMD-5 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
19533 | Slave09 EMD-6 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
19534 | Slave09 EMD-7 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
19535 | Slave09 EMD-8 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
19536 | Slave10 EMD-1 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
19537 | Slave10 EMD-2 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
19538 | Slave10 EMD-3 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
19539 | Slave10 EMD-4 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
19540 | Slave10 EMD-5 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
19541 | Slave10 EMD-6 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
19542 | Slave10 EMD-7 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
19543 | Slave10 EMD-8 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
19544 | Slave11 EMD-1 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
19545 | Slave11 EMD-2 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
19546 | Slave11 EMD-3 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
19547 | Slave11 EMD-4 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
19548 | Slave11 EMD-5 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
19549 | Slave11 EMD-6 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
19550 | Slave11 EMD-7 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
19551 | Slave11 EMD-8 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
19552 | Slave12 EMD-1 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
19553 | Slave12 EMD-2 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
19554 | Slave12 EMD-3 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
19555 | Slave12 EMD-4 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
19556 | Slave12 EMD-5 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
19557 | Slave12 EMD-6 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
19558 | Slave12 EMD-7 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
19559 | Slave12 EMD-8 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
19560 | Slave13 EMD-1 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
19561 | Slave13 EMD-2 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
19562 | Slave13 EMD-3 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
19563 | Slave13 EMD-4 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
19564 | Slave13 EMD-5 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
19565 | Slave13 EMD-6 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
19566 | Slave13 EMD-7 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
19567 | Slave13 EMD-8 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
19568 | Slave14 EMD-1 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
19569 | Slave14 EMD-2 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
19570 | Slave14 EMD-3 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
19571 | Slave14 EMD-4 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
19572 | Slave14 EMD-5 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
19573 | Slave14 EMD-6 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
19574 | Slave14 EMD-7 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
19575 | Slave14 EMD-8 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
19576 | Slave15 EMD-1 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
19577 | Slave15 EMD-2 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
19578 | Slave15 EMD-3 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
19579 | Slave15 EMD-4 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
19580 | Slave15 EMD-5 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
19581 | Slave15 EMD-6 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
19582 | Slave15 EMD-7 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
19583 | Slave15 EMD-8 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
19584 | Master EMD-1 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19585 | Master EMD-2 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19586 | Master EMD-3 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19587 | Master EMD-4 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19588 | Master EMD-5 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19589 | Master EMD-6 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19590 | Master EMD-7 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19591 | Master EMD-8 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19592 | Slave01 EMD-1 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19593 | Slave01 EMD-2 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19594 | Slave01 EMD-3 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19595 | Slave01 EMD-4 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19596 | Slave01 EMD-5 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19597 | Slave01 EMD-6 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19598 | Slave01 EMD-7 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19599 | Slave01 EMD-8 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19600 | Slave02 EMD-1 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19601 | Slave02 EMD-2 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19602 | Slave02 EMD-3 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19603 | Slave02 EMD-4 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19604 | Slave02 EMD-5 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19605 | Slave02 EMD-6 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19606 | Slave02 EMD-7 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19607 | Slave02 EMD-8 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19608 | Slave03 EMD-1 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19609 | Slave03 EMD-2 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19610 | Slave03 EMD-3 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19611 | Slave03 EMD-4 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19612 | Slave03 EMD-5 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19613 | Slave03 EMD-6 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19614 | Slave03 EMD-7 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19615 | Slave03 EMD-8 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19616 | Slave04 EMD-1 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19617 | Slave04 EMD-2 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19618 | Slave04 EMD-3 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19619 | Slave04 EMD-4 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19620 | Slave04 EMD-5 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19621 | Slave04 EMD-6 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19622 | Slave04 EMD-7 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19623 | Slave04 EMD-8 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19624 | Slave05 EMD-1 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19625 | Slave05 EMD-2 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19626 | Slave05 EMD-3 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19627 | Slave05 EMD-4 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19628 | Slave05 EMD-5 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19629 | Slave05 EMD-6 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19630 | Slave05 EMD-7 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19631 | Slave05 EMD-8 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19632 | Slave06 EMD-1 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19633 | Slave06 EMD-2 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19634 | Slave06 EMD-3 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19635 | Slave06 EMD-4 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19636 | Slave06 EMD-5 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19637 | Slave06 EMD-6 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19638 | Slave06 EMD-7 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19639 | Slave06 EMD-8 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19640 | Slave07 EMD-1 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19641 | Slave07 EMD-2 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19642 | Slave07 EMD-3 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19643 | Slave07 EMD-4 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19644 | Slave07 EMD-5 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19645 | Slave07 EMD-6 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19646 | Slave07 EMD-7 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19647 | Slave07 EMD-8 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19648 | Slave08 EMD-1 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19649 | Slave08 EMD-2 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19650 | Slave08 EMD-3 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19651 | Slave08 EMD-4 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19652 | Slave08 EMD-5 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19653 | Slave08 EMD-6 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19654 | Slave08 EMD-7 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19655 | Slave08 EMD-8 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19656 | Slave09 EMD-1 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19657 | Slave09 EMD-2 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19658 | Slave09 EMD-3 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19659 | Slave09 EMD-4 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19660 | Slave09 EMD-5 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19661 | Slave09 EMD-6 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19662 | Slave09 EMD-7 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19663 | Slave09 EMD-8 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19664 | Slave10 EMD-1 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19665 | Slave10 EMD-2 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19666 | Slave10 EMD-3 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19667 | Slave10 EMD-4 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19668 | Slave10 EMD-5 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19669 | Slave10 EMD-6 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19670 | Slave10 EMD-7 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19671 | Slave10 EMD-8 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19672 | Slave11 EMD-1 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19673 | Slave11 EMD-2 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19674 | Slave11 EMD-3 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19675 | Slave11 EMD-4 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19676 | Slave11 EMD-5 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19677 | Slave11 EMD-6 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19678 | Slave11 EMD-7 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19679 | Slave11 EMD-8 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19680 | Slave12 EMD-1 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19681 | Slave12 EMD-2 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19682 | Slave12 EMD-3 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19683 | Slave12 EMD-4 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19684 | Slave12 EMD-5 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19685 | Slave12 EMD-6 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19686 | Slave12 EMD-7 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19687 | Slave12 EMD-8 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19688 | Slave13 EMD-1 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19689 | Slave13 EMD-2 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19690 | Slave13 EMD-3 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19691 | Slave13 EMD-4 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19692 | Slave13 EMD-5 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19693 | Slave13 EMD-6 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19694 | Slave13 EMD-7 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19695 | Slave13 EMD-8 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19696 | Slave14 EMD-1 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19697 | Slave14 EMD-2 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19698 | Slave14 EMD-3 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19699 | Slave14 EMD-4 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19700 | Slave14 EMD-5 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19701 | Slave14 EMD-6 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19702 | Slave14 EMD-7 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19703 | Slave14 EMD-8 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19704 | Slave15 EMD-1 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19705 | Slave15 EMD-2 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19706 | Slave15 EMD-3 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19707 | Slave15 EMD-4 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19708 | Slave15 EMD-5 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19709 | Slave15 EMD-6 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19710 | Slave15 EMD-7 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19711 | Slave15 EMD-8 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19712 | Master EMD-1 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19713 | Master EMD-2 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19714 | Master EMD-3 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19715 | Master EMD-4 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19716 | Master EMD-5 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19717 | Master EMD-6 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19718 | Master EMD-7 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19719 | Master EMD-8 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19720 | Slave01 EMD-1 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19721 | Slave01 EMD-2 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19722 | Slave01 EMD-3 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19723 | Slave01 EMD-4 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19724 | Slave01 EMD-5 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19725 | Slave01 EMD-6 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19726 | Slave01 EMD-7 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19727 | Slave01 EMD-8 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19728 | Slave02 EMD-1 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19729 | Slave02 EMD-2 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19730 | Slave02 EMD-3 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19731 | Slave02 EMD-4 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19732 | Slave02 EMD-5 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19733 | Slave02 EMD-6 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19734 | Slave02 EMD-7 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19735 | Slave02 EMD-8 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19736 | Slave03 EMD-1 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19737 | Slave03 EMD-2 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19738 | Slave03 EMD-3 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19739 | Slave03 EMD-4 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19740 | Slave03 EMD-5 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19741 | Slave03 EMD-6 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19742 | Slave03 EMD-7 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19743 | Slave03 EMD-8 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19744 | Slave04 EMD-1 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19745 | Slave04 EMD-2 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19746 | Slave04 EMD-3 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19747 | Slave04 EMD-4 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19748 | Slave04 EMD-5 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19749 | Slave04 EMD-6 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19750 | Slave04 EMD-7 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19751 | Slave04 EMD-8 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19752 | Slave05 EMD-1 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19753 | Slave05 EMD-2 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19754 | Slave05 EMD-3 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19755 | Slave05 EMD-4 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19756 | Slave05 EMD-5 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19757 | Slave05 EMD-6 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19758 | Slave05 EMD-7 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19759 | Slave05 EMD-8 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19760 | Slave06 EMD-1 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19761 | Slave06 EMD-2 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19762 | Slave06 EMD-3 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19763 | Slave06 EMD-4 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19764 | Slave06 EMD-5 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19765 | Slave06 EMD-6 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19766 | Slave06 EMD-7 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19767 | Slave06 EMD-8 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19768 | Slave07 EMD-1 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19769 | Slave07 EMD-2 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19770 | Slave07 EMD-3 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19771 | Slave07 EMD-4 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19772 | Slave07 EMD-5 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19773 | Slave07 EMD-6 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19774 | Slave07 EMD-7 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19775 | Slave07 EMD-8 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19776 | Slave08 EMD-1 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19777 | Slave08 EMD-2 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19778 | Slave08 EMD-3 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19779 | Slave08 EMD-4 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19780 | Slave08 EMD-5 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19781 | Slave08 EMD-6 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19782 | Slave08 EMD-7 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19783 | Slave08 EMD-8 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19784 | Slave09 EMD-1 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19785 | Slave09 EMD-2 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19786 | Slave09 EMD-3 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19787 | Slave09 EMD-4 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19788 | Slave09 EMD-5 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19789 | Slave09 EMD-6 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19790 | Slave09 EMD-7 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19791 | Slave09 EMD-8 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19792 | Slave10 EMD-1 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19793 | Slave10 EMD-2 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19794 | Slave10 EMD-3 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19795 | Slave10 EMD-4 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19796 | Slave10 EMD-5 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19797 | Slave10 EMD-6 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19798 | Slave10 EMD-7 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19799 | Slave10 EMD-8 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19800 | Slave11 EMD-1 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19801 | Slave11 EMD-2 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19802 | Slave11 EMD-3 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19803 | Slave11 EMD-4 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19804 | Slave11 EMD-5 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19805 | Slave11 EMD-6 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19806 | Slave11 EMD-7 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19807 | Slave11 EMD-8 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19808 | Slave12 EMD-1 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19809 | Slave12 EMD-2 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19810 | Slave12 EMD-3 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19811 | Slave12 EMD-4 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19812 | Slave12 EMD-5 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19813 | Slave12 EMD-6 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19814 | Slave12 EMD-7 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19815 | Slave12 EMD-8 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19816 | Slave13 EMD-1 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19817 | Slave13 EMD-2 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19818 | Slave13 EMD-3 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19819 | Slave13 EMD-4 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19820 | Slave13 EMD-5 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19821 | Slave13 EMD-6 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19822 | Slave13 EMD-7 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19823 | Slave13 EMD-8 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19824 | Slave14 EMD-1 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19825 | Slave14 EMD-2 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19826 | Slave14 EMD-3 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19827 | Slave14 EMD-4 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19828 | Slave14 EMD-5 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19829 | Slave14 EMD-6 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19830 | Slave14 EMD-7 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19831 | Slave14 EMD-8 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19832 | Slave15 EMD-1 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19833 | Slave15 EMD-2 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19834 | Slave15 EMD-3 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19835 | Slave15 EMD-4 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19836 | Slave15 EMD-5 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19837 | Slave15 EMD-6 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19838 | Slave15 EMD-7 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19839 | Slave15 EMD-8 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
19840 | Master Inlet Name | RW | 32 bytes
19856 | Slave01 Inlet Name | RW | 32 bytes
19872 | Slave02 Inlet Name | RW | 32 bytes
19888 | Slave03 Inlet Name | RW | 32 bytes
19904 | Slave04 Inlet Name | RW | 32 bytes
19920 | Slave05 Inlet Name | RW | 32 bytes
19936 | Slave06 Inlet Name | RW | 32 bytes
19952 | Slave07 Inlet Name | RW | 32 bytes
19968 | Slave08 Inlet Name | RW | 32 bytes
19984 | Slave09 Inlet Name | RW | 32 bytes
20000 | Slave10 Inlet Name | RW | 32 bytes
20016 | Slave11 Inlet Name | RW | 32 bytes
20032 | Slave12 Inlet Name | RW | 32 bytes
20048 | Slave13 Inlet Name | RW | 32 bytes
20064 | Slave14 Inlet Name | RW | 32 bytes
20080 | Slave15 Inlet Name | RW | 32 bytes
20096 | Master Outlet Port01 Name | RW | 32 bytes
20112 | Master Outlet Port02 Name | RW | 32 bytes
20128 | Master Outlet Port03 Name | RW | 32 bytes
20144 | Master Outlet Port04 Name | RW | 32 bytes
20160 | Master Outlet Port05 Name | RW | 32 bytes
20176 | Master Outlet Port06 Name | RW | 32 bytes
20192 | Master Outlet Port07 Name | RW | 32 bytes
20208 | Master Outlet Port08 Name | RW | 32 bytes
20224 | Master Outlet Port09 Name | RW | 32 bytes
20240 | Master Outlet Port10 Name | RW | 32 bytes
20256 | Master Outlet Port11 Name | RW | 32 bytes
20272 | Master Outlet Port12 Name | RW | 32 bytes
20288 | Master Outlet Port13 Name | RW | 32 bytes
20304 | Master Outlet Port14 Name | RW | 32 bytes
20320 | Master Outlet Port15 Name | RW | 32 bytes
20336 | Master Outlet Port16 Name | RW | 32 bytes
20352 | Master Outlet Port17 Name | RW | 32 bytes
20368 | Master Outlet Port18 Name | RW | 32 bytes
20384 | Master Outlet Port19 Name | RW | 32 bytes
20400 | Master Outlet Port20 Name | RW | 32 bytes
20416 | Master Outlet Port21 Name | RW | 32 bytes
20432 | Master Outlet Port22 Name | RW | 32 bytes
20448 | Master Outlet Port23 Name | RW | 32 bytes
20464 | Master Outlet Port24 Name | RW | 32 bytes
20480 | Master Outlet Port25 Name | RW | 32 bytes
20496 | Master Outlet Port26 Name | RW | 32 bytes
20512 | Master Outlet Port27 Name | RW | 32 bytes
20528 | Master Outlet Port28 Name | RW | 32 bytes
20544 | Master Outlet Port29 Name | RW | 32 bytes
20560 | Master Outlet Port30 Name | RW | 32 bytes
20576 | Master Outlet Port31 Name | RW | 32 bytes
20592 | Master Outlet Port32 Name | RW | 32 bytes
20608 | Master Outlet Port33 Name | RW | 32 bytes
20624 | Master Outlet Port34 Name | RW | 32 bytes
20640 | Master Outlet Port35 Name | RW | 32 bytes
20656 | Master Outlet Port36 Name | RW | 32 bytes
20672 | Master Outlet Port37 Name | RW | 32 bytes
20688 | Master Outlet Port38 Name | RW | 32 bytes
20704 | Master Outlet Port39 Name | RW | 32 bytes
20720 | Master Outlet Port40 Name | RW | 32 bytes
20736 | Master Outlet Port41 Name | RW | 32 bytes
20752 | Master Outlet Port42 Name | RW | 32 bytes
20768 | Slave01 Outlet Port01 Name | RW | 32 bytes
20784 | Slave01 Outlet Port02 Name | RW | 32 bytes
20800 | Slave01 Outlet Port03 Name | RW | 32 bytes
20816 | Slave01 Outlet Port04 Name | RW | 32 bytes
20832 | Slave01 Outlet Port05 Name | RW | 32 bytes
20848 | Slave01 Outlet Port06 Name | RW | 32 bytes
20864 | Slave01 Outlet Port07 Name | RW | 32 bytes
20880 | Slave01 Outlet Port08 Name | RW | 32 bytes
20896 | Slave01 Outlet Port09 Name | RW | 32 bytes
20912 | Slave01 Outlet Port10 Name | RW | 32 bytes
20928 | Slave01 Outlet Port11 Name | RW | 32 bytes
20944 | Slave01 Outlet Port12 Name | RW | 32 bytes
20960 | Slave01 Outlet Port13 Name | RW | 32 bytes
20976 | Slave01 Outlet Port14 Name | RW | 32 bytes
20992 | Slave01 Outlet Port15 Name | RW | 32 bytes
21008 | Slave01 Outlet Port16 Name | RW | 32 bytes
21024 | Slave01 Outlet Port17 Name | RW | 32 bytes
21040 | Slave01 Outlet Port18 Name | RW | 32 bytes
21056 | Slave01 Outlet Port19 Name | RW | 32 bytes
21072 | Slave01 Outlet Port20 Name | RW | 32 bytes
21088 | Slave01 Outlet Port21 Name | RW | 32 bytes
21104 | Slave01 Outlet Port22 Name | RW | 32 bytes
21120 | Slave01 Outlet Port23 Name | RW | 32 bytes
21136 | Slave01 Outlet Port24 Name | RW | 32 bytes
21152 | Slave01 Outlet Port25 Name | RW | 32 bytes
21168 | Slave01 Outlet Port26 Name | RW | 32 bytes
21184 | Slave01 Outlet Port27 Name | RW | 32 bytes
21200 | Slave01 Outlet Port28 Name | RW | 32 bytes
21216 | Slave01 Outlet Port29 Name | RW | 32 bytes
21232 | Slave01 Outlet Port30 Name | RW | 32 bytes
21248 | Slave01 Outlet Port31 Name | RW | 32 bytes
21264 | Slave01 Outlet Port32 Name | RW | 32 bytes
21280 | Slave01 Outlet Port33 Name | RW | 32 bytes
21296 | Slave01 Outlet Port34 Name | RW | 32 bytes
21312 | Slave01 Outlet Port35 Name | RW | 32 bytes
21328 | Slave01 Outlet Port36 Name | RW | 32 bytes
21344 | Slave01 Outlet Port37 Name | RW | 32 bytes
21360 | Slave01 Outlet Port38 Name | RW | 32 bytes
21376 | Slave01 Outlet Port39 Name | RW | 32 bytes
21392 | Slave01 Outlet Port40 Name | RW | 32 bytes
21408 | Slave01 Outlet Port41 Name | RW | 32 bytes
21424 | Slave01 Outlet Port42 Name | RW | 32 bytes
21440 | Slave02 Outlet Port01 Name | RW | 32 bytes
21456 | Slave02 Outlet Port02 Name | RW | 32 bytes
21472 | Slave02 Outlet Port03 Name | RW | 32 bytes
21488 | Slave02 Outlet Port04 Name | RW | 32 bytes
21504 | Slave02 Outlet Port05 Name | RW | 32 bytes
21520 | Slave02 Outlet Port06 Name | RW | 32 bytes
21536 | Slave02 Outlet Port07 Name | RW | 32 bytes
21552 | Slave02 Outlet Port08 Name | RW | 32 bytes
21568 | Slave02 Outlet Port09 Name | RW | 32 bytes
21584 | Slave02 Outlet Port10 Name | RW | 32 bytes
21600 | Slave02 Outlet Port11 Name | RW | 32 bytes
21616 | Slave02 Outlet Port12 Name | RW | 32 bytes
21632 | Slave02 Outlet Port13 Name | RW | 32 bytes
21648 | Slave02 Outlet Port14 Name | RW | 32 bytes
21664 | Slave02 Outlet Port15 Name | RW | 32 bytes
21680 | Slave02 Outlet Port16 Name | RW | 32 bytes
21696 | Slave02 Outlet Port17 Name | RW | 32 bytes
21712 | Slave02 Outlet Port18 Name | RW | 32 bytes
21728 | Slave02 Outlet Port19 Name | RW | 32 bytes
21744 | Slave02 Outlet Port20 Name | RW | 32 bytes
21760 | Slave02 Outlet Port21 Name | RW | 32 bytes
21776 | Slave02 Outlet Port22 Name | RW | 32 bytes
21792 | Slave02 Outlet Port23 Name | RW | 32 bytes
21808 | Slave02 Outlet Port24 Name | RW | 32 bytes
21824 | Slave02 Outlet Port25 Name | RW | 32 bytes
21840 | Slave02 Outlet Port26 Name | RW | 32 bytes
21856 | Slave02 Outlet Port27 Name | RW | 32 bytes
21872 | Slave02 Outlet Port28 Name | RW | 32 bytes
21888 | Slave02 Outlet Port29 Name | RW | 32 bytes
21904 | Slave02 Outlet Port30 Name | RW | 32 bytes
21920 | Slave02 Outlet Port31 Name | RW | 32 bytes
21936 | Slave02 Outlet Port32 Name | RW | 32 bytes
21952 | Slave02 Outlet Port33 Name | RW | 32 bytes
21968 | Slave02 Outlet Port34 Name | RW | 32 bytes
21984 | Slave02 Outlet Port35 Name | RW | 32 bytes
22000 | Slave02 Outlet Port36 Name | RW | 32 bytes
22016 | Slave02 Outlet Port37 Name | RW | 32 bytes
22032 | Slave02 Outlet Port38 Name | RW | 32 bytes
22048 | Slave02 Outlet Port39 Name | RW | 32 bytes
22064 | Slave02 Outlet Port40 Name | RW | 32 bytes
22080 | Slave02 Outlet Port41 Name | RW | 32 bytes
22096 | Slave02 Outlet Port42 Name | RW | 32 bytes
22112 | Slave03 Outlet Port01 Name | RW | 32 bytes
22128 | Slave03 Outlet Port02 Name | RW | 32 bytes
22144 | Slave03 Outlet Port03 Name | RW | 32 bytes
22160 | Slave03 Outlet Port04 Name | RW | 32 bytes
22176 | Slave03 Outlet Port05 Name | RW | 32 bytes
22192 | Slave03 Outlet Port06 Name | RW | 32 bytes
22208 | Slave03 Outlet Port07 Name | RW | 32 bytes
22224 | Slave03 Outlet Port08 Name | RW | 32 bytes
22240 | Slave03 Outlet Port09 Name | RW | 32 bytes
22256 | Slave03 Outlet Port10 Name | RW | 32 bytes
22272 | Slave03 Outlet Port11 Name | RW | 32 bytes
22288 | Slave03 Outlet Port12 Name | RW | 32 bytes
22304 | Slave03 Outlet Port13 Name | RW | 32 bytes
22320 | Slave03 Outlet Port14 Name | RW | 32 bytes
22336 | Slave03 Outlet Port15 Name | RW | 32 bytes
22352 | Slave03 Outlet Port16 Name | RW | 32 bytes
22368 | Slave03 Outlet Port17 Name | RW | 32 bytes
22384 | Slave03 Outlet Port18 Name | RW | 32 bytes
22400 | Slave03 Outlet Port19 Name | RW | 32 bytes
22416 | Slave03 Outlet Port20 Name | RW | 32 bytes
22432 | Slave03 Outlet Port21 Name | RW | 32 bytes
22448 | Slave03 Outlet Port22 Name | RW | 32 bytes
22464 | Slave03 Outlet Port23 Name | RW | 32 bytes
22480 | Slave03 Outlet Port24 Name | RW | 32 bytes
22496 | Slave03 Outlet Port25 Name | RW | 32 bytes
22512 | Slave03 Outlet Port26 Name | RW | 32 bytes
22528 | Slave03 Outlet Port27 Name | RW | 32 bytes
22544 | Slave03 Outlet Port28 Name | RW | 32 bytes
22560 | Slave03 Outlet Port29 Name | RW | 32 bytes
22576 | Slave03 Outlet Port30 Name | RW | 32 bytes
22592 | Slave03 Outlet Port31 Name | RW | 32 bytes
22608 | Slave03 Outlet Port32 Name | RW | 32 bytes
22624 | Slave03 Outlet Port33 Name | RW | 32 bytes
22640 | Slave03 Outlet Port34 Name | RW | 32 bytes
22656 | Slave03 Outlet Port35 Name | RW | 32 bytes
22672 | Slave03 Outlet Port36 Name | RW | 32 bytes
22688 | Slave03 Outlet Port37 Name | RW | 32 bytes
22704 | Slave03 Outlet Port38 Name | RW | 32 bytes
22720 | Slave03 Outlet Port39 Name | RW | 32 bytes
22736 | Slave03 Outlet Port40 Name | RW | 32 bytes
22752 | Slave03 Outlet Port41 Name | RW | 32 bytes
22768 | Slave03 Outlet Port42 Name | RW | 32 bytes
22784 | Slave04 Outlet Port01 Name | RW | 32 bytes
22800 | Slave04 Outlet Port02 Name | RW | 32 bytes
22816 | Slave04 Outlet Port03 Name | RW | 32 bytes
22832 | Slave04 Outlet Port04 Name | RW | 32 bytes
22848 | Slave04 Outlet Port05 Name | RW | 32 bytes
22864 | Slave04 Outlet Port06 Name | RW | 32 bytes
22880 | Slave04 Outlet Port07 Name | RW | 32 bytes
22896 | Slave04 Outlet Port08 Name | RW | 32 bytes
22912 | Slave04 Outlet Port09 Name | RW | 32 bytes
22928 | Slave04 Outlet Port10 Name | RW | 32 bytes
22944 | Slave04 Outlet Port11 Name | RW | 32 bytes
22960 | Slave04 Outlet Port12 Name | RW | 32 bytes
22976 | Slave04 Outlet Port13 Name | RW | 32 bytes
22992 | Slave04 Outlet Port14 Name | RW | 32 bytes
23008 | Slave04 Outlet Port15 Name | RW | 32 bytes
23024 | Slave04 Outlet Port16 Name | RW | 32 bytes
23040 | Slave04 Outlet Port17 Name | RW | 32 bytes
23056 | Slave04 Outlet Port18 Name | RW | 32 bytes
23072 | Slave04 Outlet Port19 Name | RW | 32 bytes
23088 | Slave04 Outlet Port20 Name | RW | 32 bytes
23104 | Slave04 Outlet Port21 Name | RW | 32 bytes
23120 | Slave04 Outlet Port22 Name | RW | 32 bytes
23136 | Slave04 Outlet Port23 Name | RW | 32 bytes
23152 | Slave04 Outlet Port24 Name | RW | 32 bytes
23168 | Slave04 Outlet Port25 Name | RW | 32 bytes
23184 | Slave04 Outlet Port26 Name | RW | 32 bytes
23200 | Slave04 Outlet Port27 Name | RW | 32 bytes
23216 | Slave04 Outlet Port28 Name | RW | 32 bytes
23232 | Slave04 Outlet Port29 Name | RW | 32 bytes
23248 | Slave04 Outlet Port30 Name | RW | 32 bytes
23264 | Slave04 Outlet Port31 Name | RW | 32 bytes
23280 | Slave04 Outlet Port32 Name | RW | 32 bytes
23296 | Slave04 Outlet Port33 Name | RW | 32 bytes
23312 | Slave04 Outlet Port34 Name | RW | 32 bytes
23328 | Slave04 Outlet Port35 Name | RW | 32 bytes
23344 | Slave04 Outlet Port36 Name | RW | 32 bytes
23360 | Slave04 Outlet Port37 Name | RW | 32 bytes
23376 | Slave04 Outlet Port38 Name | RW | 32 bytes
23392 | Slave04 Outlet Port39 Name | RW | 32 bytes
23408 | Slave04 Outlet Port40 Name | RW | 32 bytes
23424 | Slave04 Outlet Port41 Name | RW | 32 bytes
23440 | Slave04 Outlet Port42 Name | RW | 32 bytes
23456 | Slave05 Outlet Port01 Name | RW | 32 bytes
23472 | Slave05 Outlet Port02 Name | RW | 32 bytes
23488 | Slave05 Outlet Port03 Name | RW | 32 bytes
23504 | Slave05 Outlet Port04 Name | RW | 32 bytes
23520 | Slave05 Outlet Port05 Name | RW | 32 bytes
23536 | Slave05 Outlet Port06 Name | RW | 32 bytes
23552 | Slave05 Outlet Port07 Name | RW | 32 bytes
23568 | Slave05 Outlet Port08 Name | RW | 32 bytes
23584 | Slave05 Outlet Port09 Name | RW | 32 bytes
23600 | Slave05 Outlet Port10 Name | RW | 32 bytes
23616 | Slave05 Outlet Port11 Name | RW | 32 bytes
23632 | Slave05 Outlet Port12 Name | RW | 32 bytes
23648 | Slave05 Outlet Port13 Name | RW | 32 bytes
23664 | Slave05 Outlet Port14 Name | RW | 32 bytes
23680 | Slave05 Outlet Port15 Name | RW | 32 bytes
23696 | Slave05 Outlet Port16 Name | RW | 32 bytes
23712 | Slave05 Outlet Port17 Name | RW | 32 bytes
23728 | Slave05 Outlet Port18 Name | RW | 32 bytes
23744 | Slave05 Outlet Port19 Name | RW | 32 bytes
23760 | Slave05 Outlet Port20 Name | RW | 32 bytes
23776 | Slave05 Outlet Port21 Name | RW | 32 bytes
23792 | Slave05 Outlet Port22 Name | RW | 32 bytes
23808 | Slave05 Outlet Port23 Name | RW | 32 bytes
23824 | Slave05 Outlet Port24 Name | RW | 32 bytes
23840 | Slave05 Outlet Port25 Name | RW | 32 bytes
23856 | Slave05 Outlet Port26 Name | RW | 32 bytes
23872 | Slave05 Outlet Port27 Name | RW | 32 bytes
23888 | Slave05 Outlet Port28 Name | RW | 32 bytes
23904 | Slave05 Outlet Port29 Name | RW | 32 bytes
23920 | Slave05 Outlet Port30 Name | RW | 32 bytes
23936 | Slave05 Outlet Port31 Name | RW | 32 bytes
23952 | Slave05 Outlet Port32 Name | RW | 32 bytes
23968 | Slave05 Outlet Port33 Name | RW | 32 bytes
23984 | Slave05 Outlet Port34 Name | RW | 32 bytes
24000 | Slave05 Outlet Port35 Name | RW | 32 bytes
24016 | Slave05 Outlet Port36 Name | RW | 32 bytes
24032 | Slave05 Outlet Port37 Name | RW | 32 bytes
24048 | Slave05 Outlet Port38 Name | RW | 32 bytes
24064 | Slave05 Outlet Port39 Name | RW | 32 bytes
24080 | Slave05 Outlet Port40 Name | RW | 32 bytes
24096 | Slave05 Outlet Port41 Name | RW | 32 bytes
24112 | Slave05 Outlet Port42 Name | RW | 32 bytes
24128 | Slave06 Outlet Port01 Name | RW | 32 bytes
24144 | Slave06 Outlet Port02 Name | RW | 32 bytes
24160 | Slave06 Outlet Port03 Name | RW | 32 bytes
24176 | Slave06 Outlet Port04 Name | RW | 32 bytes
24192 | Slave06 Outlet Port05 Name | RW | 32 bytes
24208 | Slave06 Outlet Port06 Name | RW | 32 bytes
24224 | Slave06 Outlet Port07 Name | RW | 32 bytes
24240 | Slave06 Outlet Port08 Name | RW | 32 bytes
24256 | Slave06 Outlet Port09 Name | RW | 32 bytes
24272 | Slave06 Outlet Port10 Name | RW | 32 bytes
24288 | Slave06 Outlet Port11 Name | RW | 32 bytes
24304 | Slave06 Outlet Port12 Name | RW | 32 bytes
24320 | Slave06 Outlet Port13 Name | RW | 32 bytes
24336 | Slave06 Outlet Port14 Name | RW | 32 bytes
24352 | Slave06 Outlet Port15 Name | RW | 32 bytes
24368 | Slave06 Outlet Port16 Name | RW | 32 bytes
24384 | Slave06 Outlet Port17 Name | RW | 32 bytes
24400 | Slave06 Outlet Port18 Name | RW | 32 bytes
24416 | Slave06 Outlet Port19 Name | RW | 32 bytes
24432 | Slave06 Outlet Port20 Name | RW | 32 bytes
24448 | Slave06 Outlet Port21 Name | RW | 32 bytes
24464 | Slave06 Outlet Port22 Name | RW | 32 bytes
24480 | Slave06 Outlet Port23 Name | RW | 32 bytes
24496 | Slave06 Outlet Port24 Name | RW | 32 bytes
24512 | Slave06 Outlet Port25 Name | RW | 32 bytes
24528 | Slave06 Outlet Port26 Name | RW | 32 bytes
24544 | Slave06 Outlet Port27 Name | RW | 32 bytes
24560 | Slave06 Outlet Port28 Name | RW | 32 bytes
24576 | Slave06 Outlet Port29 Name | RW | 32 bytes
24592 | Slave06 Outlet Port30 Name | RW | 32 bytes
24608 | Slave06 Outlet Port31 Name | RW | 32 bytes
24624 | Slave06 Outlet Port32 Name | RW | 32 bytes
24640 | Slave06 Outlet Port33 Name | RW | 32 bytes
24656 | Slave06 Outlet Port34 Name | RW | 32 bytes
24672 | Slave06 Outlet Port35 Name | RW | 32 bytes
24688 | Slave06 Outlet Port36 Name | RW | 32 bytes
24704 | Slave06 Outlet Port37 Name | RW | 32 bytes
24720 | Slave06 Outlet Port38 Name | RW | 32 bytes
24736 | Slave06 Outlet Port39 Name | RW | 32 bytes
24752 | Slave06 Outlet Port40 Name | RW | 32 bytes
24768 | Slave06 Outlet Port41 Name | RW | 32 bytes
24784 | Slave06 Outlet Port42 Name | RW | 32 bytes
24800 | Slave07 Outlet Port01 Name | RW | 32 bytes
24816 | Slave07 Outlet Port02 Name | RW | 32 bytes
24832 | Slave07 Outlet Port03 Name | RW | 32 bytes
24848 | Slave07 Outlet Port04 Name | RW | 32 bytes
24864 | Slave07 Outlet Port05 Name | RW | 32 bytes
24880 | Slave07 Outlet Port06 Name | RW | 32 bytes
24896 | Slave07 Outlet Port07 Name | RW | 32 bytes
24912 | Slave07 Outlet Port08 Name | RW | 32 bytes
24928 | Slave07 Outlet Port09 Name | RW | 32 bytes
24944 | Slave07 Outlet Port10 Name | RW | 32 bytes
24960 | Slave07 Outlet Port11 Name | RW | 32 bytes
24976 | Slave07 Outlet Port12 Name | RW | 32 bytes
24992 | Slave07 Outlet Port13 Name | RW | 32 bytes
25008 | Slave07 Outlet Port14 Name | RW | 32 bytes
25024 | Slave07 Outlet Port15 Name | RW | 32 bytes
25040 | Slave07 Outlet Port16 Name | RW | 32 bytes
25056 | Slave07 Outlet Port17 Name | RW | 32 bytes
25072 | Slave07 Outlet Port18 Name | RW | 32 bytes
25088 | Slave07 Outlet Port19 Name | RW | 32 bytes
25104 | Slave07 Outlet Port20 Name | RW | 32 bytes
25120 | Slave07 Outlet Port21 Name | RW | 32 bytes
25136 | Slave07 Outlet Port22 Name | RW | 32 bytes
25152 | Slave07 Outlet Port23 Name | RW | 32 bytes
25168 | Slave07 Outlet Port24 Name | RW | 32 bytes
25184 | Slave07 Outlet Port25 Name | RW | 32 bytes
25200 | Slave07 Outlet Port26 Name | RW | 32 bytes
25216 | Slave07 Outlet Port27 Name | RW | 32 bytes
25232 | Slave07 Outlet Port28 Name | RW | 32 bytes
25248 | Slave07 Outlet Port29 Name | RW | 32 bytes
25264 | Slave07 Outlet Port30 Name | RW | 32 bytes
25280 | Slave07 Outlet Port31 Name | RW | 32 bytes
25296 | Slave07 Outlet Port32 Name | RW | 32 bytes
25312 | Slave07 Outlet Port33 Name | RW | 32 bytes
25328 | Slave07 Outlet Port34 Name | RW | 32 bytes
25344 | Slave07 Outlet Port35 Name | RW | 32 bytes
25360 | Slave07 Outlet Port36 Name | RW | 32 bytes
25376 | Slave07 Outlet Port37 Name | RW | 32 bytes
25392 | Slave07 Outlet Port38 Name | RW | 32 bytes
25408 | Slave07 Outlet Port39 Name | RW | 32 bytes
25424 | Slave07 Outlet Port40 Name | RW | 32 bytes
25440 | Slave07 Outlet Port41 Name | RW | 32 bytes
25456 | Slave07 Outlet Port42 Name | RW | 32 bytes
25472 | Slave08 Outlet Port01 Name | RW | 32 bytes
25488 | Slave08 Outlet Port02 Name | RW | 32 bytes
25504 | Slave08 Outlet Port03 Name | RW | 32 bytes
25520 | Slave08 Outlet Port04 Name | RW | 32 bytes
25536 | Slave08 Outlet Port05 Name | RW | 32 bytes
25552 | Slave08 Outlet Port06 Name | RW | 32 bytes
25568 | Slave08 Outlet Port07 Name | RW | 32 bytes
25584 | Slave08 Outlet Port08 Name | RW | 32 bytes
25600 | Slave08 Outlet Port09 Name | RW | 32 bytes
25616 | Slave08 Outlet Port10 Name | RW | 32 bytes
25632 | Slave08 Outlet Port11 Name | RW | 32 bytes
25648 | Slave08 Outlet Port12 Name | RW | 32 bytes
25664 | Slave08 Outlet Port13 Name | RW | 32 bytes
25680 | Slave08 Outlet Port14 Name | RW | 32 bytes
25696 | Slave08 Outlet Port15 Name | RW | 32 bytes
25712 | Slave08 Outlet Port16 Name | RW | 32 bytes
25728 | Slave08 Outlet Port17 Name | RW | 32 bytes
25744 | Slave08 Outlet Port18 Name | RW | 32 bytes
25760 | Slave08 Outlet Port19 Name | RW | 32 bytes
25776 | Slave08 Outlet Port20 Name | RW | 32 bytes
25792 | Slave08 Outlet Port21 Name | RW | 32 bytes
25808 | Slave08 Outlet Port22 Name | RW | 32 bytes
25824 | Slave08 Outlet Port23 Name | RW | 32 bytes
25840 | Slave08 Outlet Port24 Name | RW | 32 bytes
25856 | Slave08 Outlet Port25 Name | RW | 32 bytes
25872 | Slave08 Outlet Port26 Name | RW | 32 bytes
25888 | Slave08 Outlet Port27 Name | RW | 32 bytes
25904 | Slave08 Outlet Port28 Name | RW | 32 bytes
25920 | Slave08 Outlet Port29 Name | RW | 32 bytes
25936 | Slave08 Outlet Port30 Name | RW | 32 bytes
25952 | Slave08 Outlet Port31 Name | RW | 32 bytes
25968 | Slave08 Outlet Port32 Name | RW | 32 bytes
25984 | Slave08 Outlet Port33 Name | RW | 32 bytes
26000 | Slave08 Outlet Port34 Name | RW | 32 bytes
26016 | Slave08 Outlet Port35 Name | RW | 32 bytes
26032 | Slave08 Outlet Port36 Name | RW | 32 bytes
26048 | Slave08 Outlet Port37 Name | RW | 32 bytes
26064 | Slave08 Outlet Port38 Name | RW | 32 bytes
26080 | Slave08 Outlet Port39 Name | RW | 32 bytes
26096 | Slave08 Outlet Port40 Name | RW | 32 bytes
26112 | Slave08 Outlet Port41 Name | RW | 32 bytes
26128 | Slave08 Outlet Port42 Name | RW | 32 bytes
26144 | Slave09 Outlet Port01 Name | RW | 32 bytes
26160 | Slave09 Outlet Port02 Name | RW | 32 bytes
26176 | Slave09 Outlet Port03 Name | RW | 32 bytes
26192 | Slave09 Outlet Port04 Name | RW | 32 bytes
26208 | Slave09 Outlet Port05 Name | RW | 32 bytes
26224 | Slave09 Outlet Port06 Name | RW | 32 bytes
26240 | Slave09 Outlet Port07 Name | RW | 32 bytes
26256 | Slave09 Outlet Port08 Name | RW | 32 bytes
26272 | Slave09 Outlet Port09 Name | RW | 32 bytes
26288 | Slave09 Outlet Port10 Name | RW | 32 bytes
26304 | Slave09 Outlet Port11 Name | RW | 32 bytes
26320 | Slave09 Outlet Port12 Name | RW | 32 bytes
26336 | Slave09 Outlet Port13 Name | RW | 32 bytes
26352 | Slave09 Outlet Port14 Name | RW | 32 bytes
26368 | Slave09 Outlet Port15 Name | RW | 32 bytes
26384 | Slave09 Outlet Port16 Name | RW | 32 bytes
26400 | Slave09 Outlet Port17 Name | RW | 32 bytes
26416 | Slave09 Outlet Port18 Name | RW | 32 bytes
26432 | Slave09 Outlet Port19 Name | RW | 32 bytes
26448 | Slave09 Outlet Port20 Name | RW | 32 bytes
26464 | Slave09 Outlet Port21 Name | RW | 32 bytes
26480 | Slave09 Outlet Port22 Name | RW | 32 bytes
26496 | Slave09 Outlet Port23 Name | RW | 32 bytes
26512 | Slave09 Outlet Port24 Name | RW | 32 bytes
26528 | Slave09 Outlet Port25 Name | RW | 32 bytes
26544 | Slave09 Outlet Port26 Name | RW | 32 bytes
26560 | Slave09 Outlet Port27 Name | RW | 32 bytes
26576 | Slave09 Outlet Port28 Name | RW | 32 bytes
26592 | Slave09 Outlet Port29 Name | RW | 32 bytes
26608 | Slave09 Outlet Port30 Name | RW | 32 bytes
26624 | Slave09 Outlet Port31 Name | RW | 32 bytes
26640 | Slave09 Outlet Port32 Name | RW | 32 bytes
26656 | Slave09 Outlet Port33 Name | RW | 32 bytes
26672 | Slave09 Outlet Port34 Name | RW | 32 bytes
26688 | Slave09 Outlet Port35 Name | RW | 32 bytes
26704 | Slave09 Outlet Port36 Name | RW | 32 bytes
26720 | Slave09 Outlet Port37 Name | RW | 32 bytes
26736 | Slave09 Outlet Port38 Name | RW | 32 bytes
26752 | Slave09 Outlet Port39 Name | RW | 32 bytes
26768 | Slave09 Outlet Port40 Name | RW | 32 bytes
26784 | Slave09 Outlet Port41 Name | RW | 32 bytes
26800 | Slave09 Outlet Port42 Name | RW | 32 bytes
26816 | Slave10 Outlet Port01 Name | RW | 32 bytes
26832 | Slave10 Outlet Port02 Name | RW | 32 bytes
26848 | Slave10 Outlet Port03 Name | RW | 32 bytes
26864 | Slave10 Outlet Port04 Name | RW | 32 bytes
26880 | Slave10 Outlet Port05 Name | RW | 32 bytes
26896 | Slave10 Outlet Port06 Name | RW | 32 bytes
26912 | Slave10 Outlet Port07 Name | RW | 32 bytes
26928 | Slave10 Outlet Port08 Name | RW | 32 bytes
26944 | Slave10 Outlet Port09 Name | RW | 32 bytes
26960 | Slave10 Outlet Port10 Name | RW | 32 bytes
26976 | Slave10 Outlet Port11 Name | RW | 32 bytes
26992 | Slave10 Outlet Port12 Name | RW | 32 bytes
27008 | Slave10 Outlet Port13 Name | RW | 32 bytes
27024 | Slave10 Outlet Port14 Name | RW | 32 bytes
27040 | Slave10 Outlet Port15 Name | RW | 32 bytes
27056 | Slave10 Outlet Port16 Name | RW | 32 bytes
27072 | Slave10 Outlet Port17 Name | RW | 32 bytes
27088 | Slave10 Outlet Port18 Name | RW | 32 bytes
27104 | Slave10 Outlet Port19 Name | RW | 32 bytes
27120 | Slave10 Outlet Port20 Name | RW | 32 bytes
27136 | Slave10 Outlet Port21 Name | RW | 32 bytes
27152 | Slave10 Outlet Port22 Name | RW | 32 bytes
27168 | Slave10 Outlet Port23 Name | RW | 32 bytes
27184 | Slave10 Outlet Port24 Name | RW | 32 bytes
27200 | Slave10 Outlet Port25 Name | RW | 32 bytes
27216 | Slave10 Outlet Port26 Name | RW | 32 bytes
27232 | Slave10 Outlet Port27 Name | RW | 32 bytes
27248 | Slave10 Outlet Port28 Name | RW | 32 bytes
27264 | Slave10 Outlet Port29 Name | RW | 32 bytes
27280 | Slave10 Outlet Port30 Name | RW | 32 bytes
27296 | Slave10 Outlet Port31 Name | RW | 32 bytes
27312 | Slave10 Outlet Port32 Name | RW | 32 bytes
27328 | Slave10 Outlet Port33 Name | RW | 32 bytes
27344 | Slave10 Outlet Port34 Name | RW | 32 bytes
27360 | Slave10 Outlet Port35 Name | RW | 32 bytes
27376 | Slave10 Outlet Port36 Name | RW | 32 bytes
27392 | Slave10 Outlet Port37 Name | RW | 32 bytes
27408 | Slave10 Outlet Port38 Name | RW | 32 bytes
27424 | Slave10 Outlet Port39 Name | RW | 32 bytes
27440 | Slave10 Outlet Port40 Name | RW | 32 bytes
27456 | Slave10 Outlet Port41 Name | RW | 32 bytes
27472 | Slave10 Outlet Port42 Name | RW | 32 bytes
27488 | Slave11 Outlet Port01 Name | RW | 32 bytes
27504 | Slave11 Outlet Port02 Name | RW | 32 bytes
27520 | Slave11 Outlet Port03 Name | RW | 32 bytes
27536 | Slave11 Outlet Port04 Name | RW | 32 bytes
27552 | Slave11 Outlet Port05 Name | RW | 32 bytes
27568 | Slave11 Outlet Port06 Name | RW | 32 bytes
27584 | Slave11 Outlet Port07 Name | RW | 32 bytes
27600 | Slave11 Outlet Port08 Name | RW | 32 bytes
27616 | Slave11 Outlet Port09 Name | RW | 32 bytes
27632 | Slave11 Outlet Port10 Name | RW | 32 bytes
27648 | Slave11 Outlet Port11 Name | RW | 32 bytes
27664 | Slave11 Outlet Port12 Name | RW | 32 bytes
27680 | Slave11 Outlet Port13 Name | RW | 32 bytes
27696 | Slave11 Outlet Port14 Name | RW | 32 bytes
27712 | Slave11 Outlet Port15 Name | RW | 32 bytes
27728 | Slave11 Outlet Port16 Name | RW | 32 bytes
27744 | Slave11 Outlet Port17 Name | RW | 32 bytes
27760 | Slave11 Outlet Port18 Name | RW | 32 bytes
27776 | Slave11 Outlet Port19 Name | RW | 32 bytes
27792 | Slave11 Outlet Port20 Name | RW | 32 bytes
27808 | Slave11 Outlet Port21 Name | RW | 32 bytes
27824 | Slave11 Outlet Port22 Name | RW | 32 bytes
27840 | Slave11 Outlet Port23 Name | RW | 32 bytes
27856 | Slave11 Outlet Port24 Name | RW | 32 bytes
27872 | Slave11 Outlet Port25 Name | RW | 32 bytes
27888 | Slave11 Outlet Port26 Name | RW | 32 bytes
27904 | Slave11 Outlet Port27 Name | RW | 32 bytes
27920 | Slave11 Outlet Port28 Name | RW | 32 bytes
27936 | Slave11 Outlet Port29 Name | RW | 32 bytes
27952 | Slave11 Outlet Port30 Name | RW | 32 bytes
27968 | Slave11 Outlet Port31 Name | RW | 32 bytes
27984 | Slave11 Outlet Port32 Name | RW | 32 bytes
28000 | Slave11 Outlet Port33 Name | RW | 32 bytes
28016 | Slave11 Outlet Port34 Name | RW | 32 bytes
28032 | Slave11 Outlet Port35 Name | RW | 32 bytes
28048 | Slave11 Outlet Port36 Name | RW | 32 bytes
28064 | Slave11 Outlet Port37 Name | RW | 32 bytes
28080 | Slave11 Outlet Port38 Name | RW | 32 bytes
28096 | Slave11 Outlet Port39 Name | RW | 32 bytes
28112 | Slave11 Outlet Port40 Name | RW | 32 bytes
28128 | Slave11 Outlet Port41 Name | RW | 32 bytes
28144 | Slave11 Outlet Port42 Name | RW | 32 bytes
28160 | Slave12 Outlet Port01 Name | RW | 32 bytes
28176 | Slave12 Outlet Port02 Name | RW | 32 bytes
28192 | Slave12 Outlet Port03 Name | RW | 32 bytes
28208 | Slave12 Outlet Port04 Name | RW | 32 bytes
28224 | Slave12 Outlet Port05 Name | RW | 32 bytes
28240 | Slave12 Outlet Port06 Name | RW | 32 bytes
28256 | Slave12 Outlet Port07 Name | RW | 32 bytes
28272 | Slave12 Outlet Port08 Name | RW | 32 bytes
28288 | Slave12 Outlet Port09 Name | RW | 32 bytes
28304 | Slave12 Outlet Port10 Name | RW | 32 bytes
28320 | Slave12 Outlet Port11 Name | RW | 32 bytes
28336 | Slave12 Outlet Port12 Name | RW | 32 bytes
28352 | Slave12 Outlet Port13 Name | RW | 32 bytes
28368 | Slave12 Outlet Port14 Name | RW | 32 bytes
28384 | Slave12 Outlet Port15 Name | RW | 32 bytes
28400 | Slave12 Outlet Port16 Name | RW | 32 bytes
28416 | Slave12 Outlet Port17 Name | RW | 32 bytes
28432 | Slave12 Outlet Port18 Name | RW | 32 bytes
28448 | Slave12 Outlet Port19 Name | RW | 32 bytes
28464 | Slave12 Outlet Port20 Name | RW | 32 bytes
28480 | Slave12 Outlet Port21 Name | RW | 32 bytes
28496 | Slave12 Outlet Port22 Name | RW | 32 bytes
28512 | Slave12 Outlet Port23 Name | RW | 32 bytes
28528 | Slave12 Outlet Port24 Name | RW | 32 bytes
28544 | Slave12 Outlet Port25 Name | RW | 32 bytes
28560 | Slave12 Outlet Port26 Name | RW | 32 bytes
28576 | Slave12 Outlet Port27 Name | RW | 32 bytes
28592 | Slave12 Outlet Port28 Name | RW | 32 bytes
28608 | Slave12 Outlet Port29 Name | RW | 32 bytes
28624 | Slave12 Outlet Port30 Name | RW | 32 bytes
28640 | Slave12 Outlet Port31 Name | RW | 32 bytes
28656 | Slave12 Outlet Port32 Name | RW | 32 bytes
28672 | Slave12 Outlet Port33 Name | RW | 32 bytes
28688 | Slave12 Outlet Port34 Name | RW | 32 bytes
28704 | Slave12 Outlet Port35 Name | RW | 32 bytes
28720 | Slave12 Outlet Port36 Name | RW | 32 bytes
28736 | Slave12 Outlet Port37 Name | RW | 32 bytes
28752 | Slave12 Outlet Port38 Name | RW | 32 bytes
28768 | Slave12 Outlet Port39 Name | RW | 32 bytes
28784 | Slave12 Outlet Port40 Name | RW | 32 bytes
28800 | Slave12 Outlet Port41 Name | RW | 32 bytes
28816 | Slave12 Outlet Port42 Name | RW | 32 bytes
28832 | Slave13 Outlet Port01 Name | RW | 32 bytes
28848 | Slave13 Outlet Port02 Name | RW | 32 bytes
28864 | Slave13 Outlet Port03 Name | RW | 32 bytes
28880 | Slave13 Outlet Port04 Name | RW | 32 bytes
28896 | Slave13 Outlet Port05 Name | RW | 32 bytes
28912 | Slave13 Outlet Port06 Name | RW | 32 bytes
28928 | Slave13 Outlet Port07 Name | RW | 32 bytes
28944 | Slave13 Outlet Port08 Name | RW | 32 bytes
28960 | Slave13 Outlet Port09 Name | RW | 32 bytes
28976 | Slave13 Outlet Port10 Name | RW | 32 bytes
28992 | Slave13 Outlet Port11 Name | RW | 32 bytes
29008 | Slave13 Outlet Port12 Name | RW | 32 bytes
29024 | Slave13 Outlet Port13 Name | RW | 32 bytes
29040 | Slave13 Outlet Port14 Name | RW | 32 bytes
29056 | Slave13 Outlet Port15 Name | RW | 32 bytes
29072 | Slave13 Outlet Port16 Name | RW | 32 bytes
29088 | Slave13 Outlet Port17 Name | RW | 32 bytes
29104 | Slave13 Outlet Port18 Name | RW | 32 bytes
29120 | Slave13 Outlet Port19 Name | RW | 32 bytes
29136 | Slave13 Outlet Port20 Name | RW | 32 bytes
29152 | Slave13 Outlet Port21 Name | RW | 32 bytes
29168 | Slave13 Outlet Port22 Name | RW | 32 bytes
29184 | Slave13 Outlet Port23 Name | RW | 32 bytes
29200 | Slave13 Outlet Port24 Name | RW | 32 bytes
29216 | Slave13 Outlet Port25 Name | RW | 32 bytes
29232 | Slave13 Outlet Port26 Name | RW | 32 bytes
29248 | Slave13 Outlet Port27 Name | RW | 32 bytes
29264 | Slave13 Outlet Port28 Name | RW | 32 bytes
29280 | Slave13 Outlet Port29 Name | RW | 32 bytes
29296 | Slave13 Outlet Port30 Name | RW | 32 bytes
29312 | Slave13 Outlet Port31 Name | RW | 32 bytes
29328 | Slave13 Outlet Port32 Name | RW | 32 bytes
29344 | Slave13 Outlet Port33 Name | RW | 32 bytes
29360 | Slave13 Outlet Port34 Name | RW | 32 bytes
29376 | Slave13 Outlet Port35 Name | RW | 32 bytes
29392 | Slave13 Outlet Port36 Name | RW | 32 bytes
29408 | Slave13 Outlet Port37 Name | RW | 32 bytes
29424 | Slave13 Outlet Port38 Name | RW | 32 bytes
29440 | Slave13 Outlet Port39 Name | RW | 32 bytes
29456 | Slave13 Outlet Port40 Name | RW | 32 bytes
29472 | Slave13 Outlet Port41 Name | RW | 32 bytes
29488 | Slave13 Outlet Port42 Name | RW | 32 bytes
29504 | Slave14 Outlet Port01 Name | RW | 32 bytes
29520 | Slave14 Outlet Port02 Name | RW | 32 bytes
29536 | Slave14 Outlet Port03 Name | RW | 32 bytes
29552 | Slave14 Outlet Port04 Name | RW | 32 bytes
29568 | Slave14 Outlet Port05 Name | RW | 32 bytes
29584 | Slave14 Outlet Port06 Name | RW | 32 bytes
29600 | Slave14 Outlet Port07 Name | RW | 32 bytes
29616 | Slave14 Outlet Port08 Name | RW | 32 bytes
29632 | Slave14 Outlet Port09 Name | RW | 32 bytes
29648 | Slave14 Outlet Port10 Name | RW | 32 bytes
29664 | Slave14 Outlet Port11 Name | RW | 32 bytes
29680 | Slave14 Outlet Port12 Name | RW | 32 bytes
29696 | Slave14 Outlet Port13 Name | RW | 32 bytes
29712 | Slave14 Outlet Port14 Name | RW | 32 bytes
29728 | Slave14 Outlet Port15 Name | RW | 32 bytes
29744 | Slave14 Outlet Port16 Name | RW | 32 bytes
29760 | Slave14 Outlet Port17 Name | RW | 32 bytes
29776 | Slave14 Outlet Port18 Name | RW | 32 bytes
29792 | Slave14 Outlet Port19 Name | RW | 32 bytes
29808 | Slave14 Outlet Port20 Name | RW | 32 bytes
29824 | Slave14 Outlet Port21 Name | RW | 32 bytes
29840 | Slave14 Outlet Port22 Name | RW | 32 bytes
29856 | Slave14 Outlet Port23 Name | RW | 32 bytes
29872 | Slave14 Outlet Port24 Name | RW | 32 bytes
29888 | Slave14 Outlet Port25 Name | RW | 32 bytes
29904 | Slave14 Outlet Port26 Name | RW | 32 bytes
29920 | Slave14 Outlet Port27 Name | RW | 32 bytes
29936 | Slave14 Outlet Port28 Name | RW | 32 bytes
29952 | Slave14 Outlet Port29 Name | RW | 32 bytes
29968 | Slave14 Outlet Port30 Name | RW | 32 bytes
29984 | Slave14 Outlet Port31 Name | RW | 32 bytes
30000 | Slave14 Outlet Port32 Name | RW | 32 bytes
30016 | Slave14 Outlet Port33 Name | RW | 32 bytes
30032 | Slave14 Outlet Port34 Name | RW | 32 bytes
30048 | Slave14 Outlet Port35 Name | RW | 32 bytes
30064 | Slave14 Outlet Port36 Name | RW | 32 bytes
30080 | Slave14 Outlet Port37 Name | RW | 32 bytes
30096 | Slave14 Outlet Port38 Name | RW | 32 bytes
30112 | Slave14 Outlet Port39 Name | RW | 32 bytes
30128 | Slave14 Outlet Port40 Name | RW | 32 bytes
30144 | Slave14 Outlet Port41 Name | RW | 32 bytes
30160 | Slave14 Outlet Port42 Name | RW | 32 bytes
30176 | Slave15 Outlet Port01 Name | RW | 32 bytes
30192 | Slave15 Outlet Port02 Name | RW | 32 bytes
30208 | Slave15 Outlet Port03 Name | RW | 32 bytes
30224 | Slave15 Outlet Port04 Name | RW | 32 bytes
30240 | Slave15 Outlet Port05 Name | RW | 32 bytes
30256 | Slave15 Outlet Port06 Name | RW | 32 bytes
30272 | Slave15 Outlet Port07 Name | RW | 32 bytes
30288 | Slave15 Outlet Port08 Name | RW | 32 bytes
30304 | Slave15 Outlet Port09 Name | RW | 32 bytes
30320 | Slave15 Outlet Port10 Name | RW | 32 bytes
30336 | Slave15 Outlet Port11 Name | RW | 32 bytes
30352 | Slave15 Outlet Port12 Name | RW | 32 bytes
30368 | Slave15 Outlet Port13 Name | RW | 32 bytes
30384 | Slave15 Outlet Port14 Name | RW | 32 bytes
30400 | Slave15 Outlet Port15 Name | RW | 32 bytes
30416 | Slave15 Outlet Port16 Name | RW | 32 bytes
30432 | Slave15 Outlet Port17 Name | RW | 32 bytes
30448 | Slave15 Outlet Port18 Name | RW | 32 bytes
30464 | Slave15 Outlet Port19 Name | RW | 32 bytes
30480 | Slave15 Outlet Port20 Name | RW | 32 bytes
30496 | Slave15 Outlet Port21 Name | RW | 32 bytes
30512 | Slave15 Outlet Port22 Name | RW | 32 bytes
30528 | Slave15 Outlet Port23 Name | RW | 32 bytes
30544 | Slave15 Outlet Port24 Name | RW | 32 bytes
30560 | Slave15 Outlet Port25 Name | RW | 32 bytes
30576 | Slave15 Outlet Port26 Name | RW | 32 bytes
30592 | Slave15 Outlet Port27 Name | RW | 32 bytes
30608 | Slave15 Outlet Port28 Name | RW | 32 bytes
30624 | Slave15 Outlet Port29 Name | RW | 32 bytes
30640 | Slave15 Outlet Port30 Name | RW | 32 bytes
30656 | Slave15 Outlet Port31 Name | RW | 32 bytes
30672 | Slave15 Outlet Port32 Name | RW | 32 bytes
30688 | Slave15 Outlet Port33 Name | RW | 32 bytes
30704 | Slave15 Outlet Port34 Name | RW | 32 bytes
30720 | Slave15 Outlet Port35 Name | RW | 32 bytes
30736 | Slave15 Outlet Port36 Name | RW | 32 bytes
30752 | Slave15 Outlet Port37 Name | RW | 32 bytes
30768 | Slave15 Outlet Port38 Name | RW | 32 bytes
30784 | Slave15 Outlet Port39 Name | RW | 32 bytes
30800 | Slave15 Outlet Port40 Name | RW | 32 bytes
30816 | Slave15 Outlet Port41 Name | RW | 32 bytes
30832 | Slave15 Outlet Port42 Name | RW | 32 bytes
30848 | Master EMD-1 Name | RW | 32 bytes
30864 | Master EMD-2 Name | RW | 32 bytes
30880 | Master EMD-3 Name | RW | 32 bytes
30896 | Master EMD-4 Name | RW | 32 bytes
30912 | Master EMD-5 Name | RW | 32 bytes
30928 | Master EMD-6 Name | RW | 32 bytes
30944 | Master EMD-7 Name | RW | 32 bytes
30960 | Master EMD-8 Name | RW | 32 bytes
30976 | Slave01 EMD-1 Name | RW | 32 bytes
30992 | Slave01 EMD-2 Name | RW | 32 bytes
31008 | Slave01 EMD-3 Name | RW | 32 bytes
31024 | Slave01 EMD-4 Name | RW | 32 bytes
31040 | Slave01 EMD-5 Name | RW | 32 bytes
31056 | Slave01 EMD-6 Name | RW | 32 bytes
31072 | Slave01 EMD-7 Name | RW | 32 bytes
31088 | Slave01 EMD-8 Name | RW | 32 bytes
31104 | Slave02 EMD-1 Name | RW | 32 bytes
31120 | Slave02 EMD-2 Name | RW | 32 bytes
31136 | Slave02 EMD-3 Name | RW | 32 bytes
31152 | Slave02 EMD-4 Name | RW | 32 bytes
31168 | Slave02 EMD-5 Name | RW | 32 bytes
31184 | Slave02 EMD-6 Name | RW | 32 bytes
31200 | Slave02 EMD-7 Name | RW | 32 bytes
31216 | Slave02 EMD-8 Name | RW | 32 bytes
31232 | Slave03 EMD-1 Name | RW | 32 bytes
31248 | Slave03 EMD-2 Name | RW | 32 bytes
31264 | Slave03 EMD-3 Name | RW | 32 bytes
31280 | Slave03 EMD-4 Name | RW | 32 bytes
31296 | Slave03 EMD-5 Name | RW | 32 bytes
31312 | Slave03 EMD-6 Name | RW | 32 bytes
31328 | Slave03 EMD-7 Name | RW | 32 bytes
31344 | Slave03 EMD-8 Name | RW | 32 bytes
31360 | Slave04 EMD-1 Name | RW | 32 bytes
31376 | Slave04 EMD-2 Name | RW | 32 bytes
31392 | Slave04 EMD-3 Name | RW | 32 bytes
31408 | Slave04 EMD-4 Name | RW | 32 bytes
31424 | Slave04 EMD-5 Name | RW | 32 bytes
31440 | Slave04 EMD-6 Name | RW | 32 bytes
31456 | Slave04 EMD-7 Name | RW | 32 bytes
31472 | Slave04 EMD-8 Name | RW | 32 bytes
31488 | Slave05 EMD-1 Name | RW | 32 bytes
31504 | Slave05 EMD-2 Name | RW | 32 bytes
31520 | Slave05 EMD-3 Name | RW | 32 bytes
31536 | Slave05 EMD-4 Name | RW | 32 bytes
31552 | Slave05 EMD-5 Name | RW | 32 bytes
31568 | Slave05 EMD-6 Name | RW | 32 bytes
31584 | Slave05 EMD-7 Name | RW | 32 bytes
31600 | Slave05 EMD-8 Name | RW | 32 bytes
31616 | Slave06 EMD-1 Name | RW | 32 bytes
31632 | Slave06 EMD-2 Name | RW | 32 bytes
31648 | Slave06 EMD-3 Name | RW | 32 bytes
31664 | Slave06 EMD-4 Name | RW | 32 bytes
31680 | Slave06 EMD-5 Name | RW | 32 bytes
31696 | Slave06 EMD-6 Name | RW | 32 bytes
31712 | Slave06 EMD-7 Name | RW | 32 bytes
31728 | Slave06 EMD-8 Name | RW | 32 bytes
31744 | Slave07 EMD-1 Name | RW | 32 bytes
31760 | Slave07 EMD-2 Name | RW | 32 bytes
31776 | Slave07 EMD-3 Name | RW | 32 bytes
31792 | Slave07 EMD-4 Name | RW | 32 bytes
31808 | Slave07 EMD-5 Name | RW | 32 bytes
31824 | Slave07 EMD-6 Name | RW | 32 bytes
31840 | Slave07 EMD-7 Name | RW | 32 bytes
31856 | Slave07 EMD-8 Name | RW | 32 bytes
31872 | Slave08 EMD-1 Name | RW | 32 bytes
31888 | Slave08 EMD-2 Name | RW | 32 bytes
31904 | Slave08 EMD-3 Name | RW | 32 bytes
31920 | Slave08 EMD-4 Name | RW | 32 bytes
31936 | Slave08 EMD-5 Name | RW | 32 bytes
31952 | Slave08 EMD-6 Name | RW | 32 bytes
31968 | Slave08 EMD-7 Name | RW | 32 bytes
31984 | Slave08 EMD-8 Name | RW | 32 bytes
32000 | Slave09 EMD-1 Name | RW | 32 bytes
32016 | Slave09 EMD-2 Name | RW | 32 bytes
32032 | Slave09 EMD-3 Name | RW | 32 bytes
32048 | Slave09 EMD-4 Name | RW | 32 bytes
32064 | Slave09 EMD-5 Name | RW | 32 bytes
32080 | Slave09 EMD-6 Name | RW | 32 bytes
32096 | Slave09 EMD-7 Name | RW | 32 bytes
32112 | Slave09 EMD-8 Name | RW | 32 bytes
32128 | Slave10 EMD-1 Name | RW | 32 bytes
32144 | Slave10 EMD-2 Name | RW | 32 bytes
32160 | Slave10 EMD-3 Name | RW | 32 bytes
32176 | Slave10 EMD-4 Name | RW | 32 bytes
32192 | Slave10 EMD-5 Name | RW | 32 bytes
32208 | Slave10 EMD-6 Name | RW | 32 bytes
32224 | Slave10 EMD-7 Name | RW | 32 bytes
32240 | Slave10 EMD-8 Name | RW | 32 bytes
32256 | Slave11 EMD-1 Name | RW | 32 bytes
32272 | Slave11 EMD-2 Name | RW | 32 bytes
32288 | Slave11 EMD-3 Name | RW | 32 bytes
32304 | Slave11 EMD-4 Name | RW | 32 bytes
32320 | Slave11 EMD-5 Name | RW | 32 bytes
32336 | Slave11 EMD-6 Name | RW | 32 bytes
32352 | Slave11 EMD-7 Name | RW | 32 bytes
32368 | Slave11 EMD-8 Name | RW | 32 bytes
32384 | Slave12 EMD-1 Name | RW | 32 bytes
32400 | Slave12 EMD-2 Name | RW | 32 bytes
32416 | Slave12 EMD-3 Name | RW | 32 bytes
32432 | Slave12 EMD-4 Name | RW | 32 bytes
32448 | Slave12 EMD-5 Name | RW | 32 bytes
32464 | Slave12 EMD-6 Name | RW | 32 bytes
32480 | Slave12 EMD-7 Name | RW | 32 bytes
32496 | Slave12 EMD-8 Name | RW | 32 bytes
32512 | Slave13 EMD-1 Name | RW | 32 bytes
32528 | Slave13 EMD-2 Name | RW | 32 bytes
32544 | Slave13 EMD-3 Name | RW | 32 bytes
32560 | Slave13 EMD-4 Name | RW | 32 bytes
32576 | Slave13 EMD-5 Name | RW | 32 bytes
32592 | Slave13 EMD-6 Name | RW | 32 bytes
32608 | Slave13 EMD-7 Name | RW | 32 bytes
32624 | Slave13 EMD-8 Name | RW | 32 bytes
32640 | Slave14 EMD-1 Name | RW | 32 bytes
32656 | Slave14 EMD-2 Name | RW | 32 bytes
32672 | Slave14 EMD-3 Name | RW | 32 bytes
32688 | Slave14 EMD-4 Name | RW | 32 bytes
32704 | Slave14 EMD-5 Name | RW | 32 bytes
32720 | Slave14 EMD-6 Name | RW | 32 bytes
32736 | Slave14 EMD-7 Name | RW | 32 bytes
32752 | Slave14 EMD-8 Name | RW | 32 bytes
32768 | Slave15 EMD-1 Name | RW | 32 bytes
32784 | Slave15 EMD-2 Name | RW | 32 bytes
32800 | Slave15 EMD-3 Name | RW | 32 bytes
32816 | Slave15 EMD-4 Name | RW | 32 bytes
32832 | Slave15 EMD-5 Name | RW | 32 bytes
32848 | Slave15 EMD-6 Name | RW | 32 bytes
32864 | Slave15 EMD-7 Name | RW | 32 bytes
32880 | Slave15 EMD-8 Name | RW | 32 bytes
32896 | Master EMD-1 Temperature Name | RW | 32 bytes
32912 | Master EMD-2 Temperature Name | RW | 32 bytes
32928 | Master EMD-3 Temperature Name | RW | 32 bytes
32944 | Master EMD-4 Temperature Name | RW | 32 bytes
32960 | Master EMD-5 Temperature Name | RW | 32 bytes
32976 | Master EMD-6 Temperature Name | RW | 32 bytes
32992 | Master EMD-7 Temperature Name | RW | 32 bytes
33008 | Master EMD-8 Temperature Name | RW | 32 bytes
33024 | Slave01 EMD-1 Temperature Name | RW | 32 bytes
33040 | Slave01 EMD-2 Temperature Name | RW | 32 bytes
33056 | Slave01 EMD-3 Temperature Name | RW | 32 bytes
33072 | Slave01 EMD-4 Temperature Name | RW | 32 bytes
33088 | Slave01 EMD-5 Temperature Name | RW | 32 bytes
33104 | Slave01 EMD-6 Temperature Name | RW | 32 bytes
33120 | Slave01 EMD-7 Temperature Name | RW | 32 bytes
33136 | Slave01 EMD-8 Temperature Name | RW | 32 bytes
33152 | Slave02 EMD-1 Temperature Name | RW | 32 bytes
33168 | Slave02 EMD-2 Temperature Name | RW | 32 bytes
33184 | Slave02 EMD-3 Temperature Name | RW | 32 bytes
33200 | Slave02 EMD-4 Temperature Name | RW | 32 bytes
33216 | Slave02 EMD-5 Temperature Name | RW | 32 bytes
33232 | Slave02 EMD-6 Temperature Name | RW | 32 bytes
33248 | Slave02 EMD-7 Temperature Name | RW | 32 bytes
33264 | Slave02 EMD-8 Temperature Name | RW | 32 bytes
33280 | Slave03 EMD-1 Temperature Name | RW | 32 bytes
33296 | Slave03 EMD-2 Temperature Name | RW | 32 bytes
33312 | Slave03 EMD-3 Temperature Name | RW | 32 bytes
33328 | Slave03 EMD-4 Temperature Name | RW | 32 bytes
33344 | Slave03 EMD-5 Temperature Name | RW | 32 bytes
33360 | Slave03 EMD-6 Temperature Name | RW | 32 bytes
33376 | Slave03 EMD-7 Temperature Name | RW | 32 bytes
33392 | Slave03 EMD-8 Temperature Name | RW | 32 bytes
33408 | Slave04 EMD-1 Temperature Name | RW | 32 bytes
33424 | Slave04 EMD-2 Temperature Name | RW | 32 bytes
33440 | Slave04 EMD-3 Temperature Name | RW | 32 bytes
33456 | Slave04 EMD-4 Temperature Name | RW | 32 bytes
33472 | Slave04 EMD-5 Temperature Name | RW | 32 bytes
33488 | Slave04 EMD-6 Temperature Name | RW | 32 bytes
33504 | Slave04 EMD-7 Temperature Name | RW | 32 bytes
33520 | Slave04 EMD-8 Temperature Name | RW | 32 bytes
33536 | Slave05 EMD-1 Temperature Name | RW | 32 bytes
33552 | Slave05 EMD-2 Temperature Name | RW | 32 bytes
33568 | Slave05 EMD-3 Temperature Name | RW | 32 bytes
33584 | Slave05 EMD-4 Temperature Name | RW | 32 bytes
33600 | Slave05 EMD-5 Temperature Name | RW | 32 bytes
33616 | Slave05 EMD-6 Temperature Name | RW | 32 bytes
33632 | Slave05 EMD-7 Temperature Name | RW | 32 bytes
33648 | Slave05 EMD-8 Temperature Name | RW | 32 bytes
33664 | Slave06 EMD-1 Temperature Name | RW | 32 bytes
33680 | Slave06 EMD-2 Temperature Name | RW | 32 bytes
33696 | Slave06 EMD-3 Temperature Name | RW | 32 bytes
33712 | Slave06 EMD-4 Temperature Name | RW | 32 bytes
33728 | Slave06 EMD-5 Temperature Name | RW | 32 bytes
33744 | Slave06 EMD-6 Temperature Name | RW | 32 bytes
33760 | Slave06 EMD-7 Temperature Name | RW | 32 bytes
33776 | Slave06 EMD-8 Temperature Name | RW | 32 bytes
33792 | Slave07 EMD-1 Temperature Name | RW | 32 bytes
33808 | Slave07 EMD-2 Temperature Name | RW | 32 bytes
33824 | Slave07 EMD-3 Temperature Name | RW | 32 bytes
33840 | Slave07 EMD-4 Temperature Name | RW | 32 bytes
33856 | Slave07 EMD-5 Temperature Name | RW | 32 bytes
33872 | Slave07 EMD-6 Temperature Name | RW | 32 bytes
33888 | Slave07 EMD-7 Temperature Name | RW | 32 bytes
33904 | Slave07 EMD-8 Temperature Name | RW | 32 bytes
33920 | Slave08 EMD-1 Temperature Name | RW | 32 bytes
33936 | Slave08 EMD-2 Temperature Name | RW | 32 bytes
33952 | Slave08 EMD-3 Temperature Name | RW | 32 bytes
33968 | Slave08 EMD-4 Temperature Name | RW | 32 bytes
33984 | Slave08 EMD-5 Temperature Name | RW | 32 bytes
34000 | Slave08 EMD-6 Temperature Name | RW | 32 bytes
34016 | Slave08 EMD-7 Temperature Name | RW | 32 bytes
34032 | Slave08 EMD-8 Temperature Name | RW | 32 bytes
34048 | Slave09 EMD-1 Temperature Name | RW | 32 bytes
34064 | Slave09 EMD-2 Temperature Name | RW | 32 bytes
34080 | Slave09 EMD-3 Temperature Name | RW | 32 bytes
34096 | Slave09 EMD-4 Temperature Name | RW | 32 bytes
34112 | Slave09 EMD-5 Temperature Name | RW | 32 bytes
34128 | Slave09 EMD-6 Temperature Name | RW | 32 bytes
34144 | Slave09 EMD-7 Temperature Name | RW | 32 bytes
34160 | Slave09 EMD-8 Temperature Name | RW | 32 bytes
34176 | Slave10 EMD-1 Temperature Name | RW | 32 bytes
34192 | Slave10 EMD-2 Temperature Name | RW | 32 bytes
34208 | Slave10 EMD-3 Temperature Name | RW | 32 bytes
34224 | Slave10 EMD-4 Temperature Name | RW | 32 bytes
34240 | Slave10 EMD-5 Temperature Name | RW | 32 bytes
34256 | Slave10 EMD-6 Temperature Name | RW | 32 bytes
34272 | Slave10 EMD-7 Temperature Name | RW | 32 bytes
34288 | Slave10 EMD-8 Temperature Name | RW | 32 bytes
34304 | Slave11 EMD-1 Temperature Name | RW | 32 bytes
34320 | Slave11 EMD-2 Temperature Name | RW | 32 bytes
34336 | Slave11 EMD-3 Temperature Name | RW | 32 bytes
34352 | Slave11 EMD-4 Temperature Name | RW | 32 bytes
34368 | Slave11 EMD-5 Temperature Name | RW | 32 bytes
34384 | Slave11 EMD-6 Temperature Name | RW | 32 bytes
34400 | Slave11 EMD-7 Temperature Name | RW | 32 bytes
34416 | Slave11 EMD-8 Temperature Name | RW | 32 bytes
34432 | Slave12 EMD-1 Temperature Name | RW | 32 bytes
34448 | Slave12 EMD-2 Temperature Name | RW | 32 bytes
34464 | Slave12 EMD-3 Temperature Name | RW | 32 bytes
34480 | Slave12 EMD-4 Temperature Name | RW | 32 bytes
34496 | Slave12 EMD-5 Temperature Name | RW | 32 bytes
34512 | Slave12 EMD-6 Temperature Name | RW | 32 bytes
34528 | Slave12 EMD-7 Temperature Name | RW | 32 bytes
34544 | Slave12 EMD-8 Temperature Name | RW | 32 bytes
34560 | Slave13 EMD-1 Temperature Name | RW | 32 bytes
34576 | Slave13 EMD-2 Temperature Name | RW | 32 bytes
34592 | Slave13 EMD-3 Temperature Name | RW | 32 bytes
34608 | Slave13 EMD-4 Temperature Name | RW | 32 bytes
34624 | Slave13 EMD-5 Temperature Name | RW | 32 bytes
34640 | Slave13 EMD-6 Temperature Name | RW | 32 bytes
34656 | Slave13 EMD-7 Temperature Name | RW | 32 bytes
34672 | Slave13 EMD-8 Temperature Name | RW | 32 bytes
34688 | Slave14 EMD-1 Temperature Name | RW | 32 bytes
34704 | Slave14 EMD-2 Temperature Name | RW | 32 bytes
34720 | Slave14 EMD-3 Temperature Name | RW | 32 bytes
34736 | Slave14 EMD-4 Temperature Name | RW | 32 bytes
34752 | Slave14 EMD-5 Temperature Name | RW | 32 bytes
34768 | Slave14 EMD-6 Temperature Name | RW | 32 bytes
34784 | Slave14 EMD-7 Temperature Name | RW | 32 bytes
34800 | Slave14 EMD-8 Temperature Name | RW | 32 bytes
34816 | Slave15 EMD-1 Temperature Name | RW | 32 bytes
34832 | Slave15 EMD-2 Temperature Name | RW | 32 bytes
34848 | Slave15 EMD-3 Temperature Name | RW | 32 bytes
34864 | Slave15 EMD-4 Temperature Name | RW | 32 bytes
34880 | Slave15 EMD-5 Temperature Name | RW | 32 bytes
34896 | Slave15 EMD-6 Temperature Name | RW | 32 bytes
34912 | Slave15 EMD-7 Temperature Name | RW | 32 bytes
34928 | Slave15 EMD-8 Temperature Name | RW | 32 bytes
34944 | Master EMD-1 Humidity Name | RW | 32 bytes
34960 | Master EMD-2 Humidity Name | RW | 32 bytes
34976 | Master EMD-3 Humidity Name | RW | 32 bytes
34992 | Master EMD-4 Humidity Name | RW | 32 bytes
35008 | Master EMD-5 Humidity Name | RW | 32 bytes
35024 | Master EMD-6 Humidity Name | RW | 32 bytes
35040 | Master EMD-7 Humidity Name | RW | 32 bytes
35056 | Master EMD-8 Humidity Name | RW | 32 bytes
35072 | Slave01 EMD-1 Humidity Name | RW | 32 bytes
35088 | Slave01 EMD-2 Humidity Name | RW | 32 bytes
35104 | Slave01 EMD-3 Humidity Name | RW | 32 bytes
35120 | Slave01 EMD-4 Humidity Name | RW | 32 bytes
35136 | Slave01 EMD-5 Humidity Name | RW | 32 bytes
35152 | Slave01 EMD-6 Humidity Name | RW | 32 bytes
35168 | Slave01 EMD-7 Humidity Name | RW | 32 bytes
35184 | Slave01 EMD-8 Humidity Name | RW | 32 bytes
35200 | Slave02 EMD-1 Humidity Name | RW | 32 bytes
35216 | Slave02 EMD-2 Humidity Name | RW | 32 bytes
35232 | Slave02 EMD-3 Humidity Name | RW | 32 bytes
35248 | Slave02 EMD-4 Humidity Name | RW | 32 bytes
35264 | Slave02 EMD-5 Humidity Name | RW | 32 bytes
35280 | Slave02 EMD-6 Humidity Name | RW | 32 bytes
35296 | Slave02 EMD-7 Humidity Name | RW | 32 bytes
35312 | Slave02 EMD-8 Humidity Name | RW | 32 bytes
35328 | Slave03 EMD-1 Humidity Name | RW | 32 bytes
35344 | Slave03 EMD-2 Humidity Name | RW | 32 bytes
35360 | Slave03 EMD-3 Humidity Name | RW | 32 bytes
35376 | Slave03 EMD-4 Humidity Name | RW | 32 bytes
35392 | Slave03 EMD-5 Humidity Name | RW | 32 bytes
35408 | Slave03 EMD-6 Humidity Name | RW | 32 bytes
35424 | Slave03 EMD-7 Humidity Name | RW | 32 bytes
35440 | Slave03 EMD-8 Humidity Name | RW | 32 bytes
35456 | Slave04 EMD-1 Humidity Name | RW | 32 bytes
35472 | Slave04 EMD-2 Humidity Name | RW | 32 bytes
35488 | Slave04 EMD-3 Humidity Name | RW | 32 bytes
35504 | Slave04 EMD-4 Humidity Name | RW | 32 bytes
35520 | Slave04 EMD-5 Humidity Name | RW | 32 bytes
35536 | Slave04 EMD-6 Humidity Name | RW | 32 bytes
35552 | Slave04 EMD-7 Humidity Name | RW | 32 bytes
35568 | Slave04 EMD-8 Humidity Name | RW | 32 bytes
35584 | Slave05 EMD-1 Humidity Name | RW | 32 bytes
35600 | Slave05 EMD-2 Humidity Name | RW | 32 bytes
35616 | Slave05 EMD-3 Humidity Name | RW | 32 bytes
35632 | Slave05 EMD-4 Humidity Name | RW | 32 bytes
35648 | Slave05 EMD-5 Humidity Name | RW | 32 bytes
35664 | Slave05 EMD-6 Humidity Name | RW | 32 bytes
35680 | Slave05 EMD-7 Humidity Name | RW | 32 bytes
35696 | Slave05 EMD-8 Humidity Name | RW | 32 bytes
35712 | Slave06 EMD-1 Humidity Name | RW | 32 bytes
35728 | Slave06 EMD-2 Humidity Name | RW | 32 bytes
35744 | Slave06 EMD-3 Humidity Name | RW | 32 bytes
35760 | Slave06 EMD-4 Humidity Name | RW | 32 bytes
35776 | Slave06 EMD-5 Humidity Name | RW | 32 bytes
35792 | Slave06 EMD-6 Humidity Name | RW | 32 bytes
35808 | Slave06 EMD-7 Humidity Name | RW | 32 bytes
35824 | Slave06 EMD-8 Humidity Name | RW | 32 bytes
35840 | Slave07 EMD-1 Humidity Name | RW | 32 bytes
35856 | Slave07 EMD-2 Humidity Name | RW | 32 bytes
35872 | Slave07 EMD-3 Humidity Name | RW | 32 bytes
35888 | Slave07 EMD-4 Humidity Name | RW | 32 bytes
35904 | Slave07 EMD-5 Humidity Name | RW | 32 bytes
35920 | Slave07 EMD-6 Humidity Name | RW | 32 bytes
35936 | Slave07 EMD-7 Humidity Name | RW | 32 bytes
35952 | Slave07 EMD-8 Humidity Name | RW | 32 bytes
35968 | Slave08 EMD-1 Humidity Name | RW | 32 bytes
35984 | Slave08 EMD-2 Humidity Name | RW | 32 bytes
36000 | Slave08 EMD-3 Humidity Name | RW | 32 bytes
36016 | Slave08 EMD-4 Humidity Name | RW | 32 bytes
36032 | Slave08 EMD-5 Humidity Name | RW | 32 bytes
36048 | Slave08 EMD-6 Humidity Name | RW | 32 bytes
36064 | Slave08 EMD-7 Humidity Name | RW | 32 bytes
36080 | Slave08 EMD-8 Humidity Name | RW | 32 bytes
36096 | Slave09 EMD-1 Humidity Name | RW | 32 bytes
36112 | Slave09 EMD-2 Humidity Name | RW | 32 bytes
36128 | Slave09 EMD-3 Humidity Name | RW | 32 bytes
36144 | Slave09 EMD-4 Humidity Name | RW | 32 bytes
36160 | Slave09 EMD-5 Humidity Name | RW | 32 bytes
36176 | Slave09 EMD-6 Humidity Name | RW | 32 bytes
36192 | Slave09 EMD-7 Humidity Name | RW | 32 bytes
36208 | Slave09 EMD-8 Humidity Name | RW | 32 bytes
36224 | Slave10 EMD-1 Humidity Name | RW | 32 bytes
36240 | Slave10 EMD-2 Humidity Name | RW | 32 bytes
36256 | Slave10 EMD-3 Humidity Name | RW | 32 bytes
36272 | Slave10 EMD-4 Humidity Name | RW | 32 bytes
36288 | Slave10 EMD-5 Humidity Name | RW | 32 bytes
36304 | Slave10 EMD-6 Humidity Name | RW | 32 bytes
36320 | Slave10 EMD-7 Humidity Name | RW | 32 bytes
36336 | Slave10 EMD-8 Humidity Name | RW | 32 bytes
36352 | Slave11 EMD-1 Humidity Name | RW | 32 bytes
36368 | Slave11 EMD-2 Humidity Name | RW | 32 bytes
36384 | Slave11 EMD-3 Humidity Name | RW | 32 bytes
36400 | Slave11 EMD-4 Humidity Name | RW | 32 bytes
36416 | Slave11 EMD-5 Humidity Name | RW | 32 bytes
36432 | Slave11 EMD-6 Humidity Name | RW | 32 bytes
36448 | Slave11 EMD-7 Humidity Name | RW | 32 bytes
36464 | Slave11 EMD-8 Humidity Name | RW | 32 bytes
36480 | Slave12 EMD-1 Humidity Name | RW | 32 bytes
36496 | Slave12 EMD-2 Humidity Name | RW | 32 bytes
36512 | Slave12 EMD-3 Humidity Name | RW | 32 bytes
36528 | Slave12 EMD-4 Humidity Name | RW | 32 bytes
36544 | Slave12 EMD-5 Humidity Name | RW | 32 bytes
36560 | Slave12 EMD-6 Humidity Name | RW | 32 bytes
36576 | Slave12 EMD-7 Humidity Name | RW | 32 bytes
36592 | Slave12 EMD-8 Humidity Name | RW | 32 bytes
36608 | Slave13 EMD-1 Humidity Name | RW | 32 bytes
36624 | Slave13 EMD-2 Humidity Name | RW | 32 bytes
36640 | Slave13 EMD-3 Humidity Name | RW | 32 bytes
36656 | Slave13 EMD-4 Humidity Name | RW | 32 bytes
36672 | Slave13 EMD-5 Humidity Name | RW | 32 bytes
36688 | Slave13 EMD-6 Humidity Name | RW | 32 bytes
36704 | Slave13 EMD-7 Humidity Name | RW | 32 bytes
36720 | Slave13 EMD-8 Humidity Name | RW | 32 bytes
36736 | Slave14 EMD-1 Humidity Name | RW | 32 bytes
36752 | Slave14 EMD-2 Humidity Name | RW | 32 bytes
36768 | Slave14 EMD-3 Humidity Name | RW | 32 bytes
36784 | Slave14 EMD-4 Humidity Name | RW | 32 bytes
36800 | Slave14 EMD-5 Humidity Name | RW | 32 bytes
36816 | Slave14 EMD-6 Humidity Name | RW | 32 bytes
36832 | Slave14 EMD-7 Humidity Name | RW | 32 bytes
36848 | Slave14 EMD-8 Humidity Name | RW | 32 bytes
36864 | Slave15 EMD-1 Humidity Name | RW | 32 bytes
36880 | Slave15 EMD-2 Humidity Name | RW | 32 bytes
36896 | Slave15 EMD-3 Humidity Name | RW | 32 bytes
36912 | Slave15 EMD-4 Humidity Name | RW | 32 bytes
36928 | Slave15 EMD-5 Humidity Name | RW | 32 bytes
36944 | Slave15 EMD-6 Humidity Name | RW | 32 bytes
36960 | Slave15 EMD-7 Humidity Name | RW | 32 bytes
36976 | Slave15 EMD-8 Humidity Name | RW | 32 bytes
36992 | Master EMD-1 Alarm1 Name | RW | 32 bytes
37008 | Master EMD-2 Alarm1 Name | RW | 32 bytes
37024 | Master EMD-3 Alarm1 Name | RW | 32 bytes
37040 | Master EMD-4 Alarm1 Name | RW | 32 bytes
37056 | Master EMD-5 Alarm1 Name | RW | 32 bytes
37072 | Master EMD-6 Alarm1 Name | RW | 32 bytes
37088 | Master EMD-7 Alarm1 Name | RW | 32 bytes
37104 | Master EMD-8 Alarm1 Name | RW | 32 bytes
37120 | Slave01 EMD-1 Alarm1 Name | RW | 32 bytes
37136 | Slave01 EMD-2 Alarm1 Name | RW | 32 bytes
37152 | Slave01 EMD-3 Alarm1 Name | RW | 32 bytes
37168 | Slave01 EMD-4 Alarm1 Name | RW | 32 bytes
37184 | Slave01 EMD-5 Alarm1 Name | RW | 32 bytes
37200 | Slave01 EMD-6 Alarm1 Name | RW | 32 bytes
37216 | Slave01 EMD-7 Alarm1 Name | RW | 32 bytes
37232 | Slave01 EMD-8 Alarm1 Name | RW | 32 bytes
37248 | Slave02 EMD-1 Alarm1 Name | RW | 32 bytes
37264 | Slave02 EMD-2 Alarm1 Name | RW | 32 bytes
37280 | Slave02 EMD-3 Alarm1 Name | RW | 32 bytes
37296 | Slave02 EMD-4 Alarm1 Name | RW | 32 bytes
37312 | Slave02 EMD-5 Alarm1 Name | RW | 32 bytes
37328 | Slave02 EMD-6 Alarm1 Name | RW | 32 bytes
37344 | Slave02 EMD-7 Alarm1 Name | RW | 32 bytes
37360 | Slave02 EMD-8 Alarm1 Name | RW | 32 bytes
37376 | Slave03 EMD-1 Alarm1 Name | RW | 32 bytes
37392 | Slave03 EMD-2 Alarm1 Name | RW | 32 bytes
37408 | Slave03 EMD-3 Alarm1 Name | RW | 32 bytes
37424 | Slave03 EMD-4 Alarm1 Name | RW | 32 bytes
37440 | Slave03 EMD-5 Alarm1 Name | RW | 32 bytes
37456 | Slave03 EMD-6 Alarm1 Name | RW | 32 bytes
37472 | Slave03 EMD-7 Alarm1 Name | RW | 32 bytes
37488 | Slave03 EMD-8 Alarm1 Name | RW | 32 bytes
37504 | Slave04 EMD-1 Alarm1 Name | RW | 32 bytes
37520 | Slave04 EMD-2 Alarm1 Name | RW | 32 bytes
37536 | Slave04 EMD-3 Alarm1 Name | RW | 32 bytes
37552 | Slave04 EMD-4 Alarm1 Name | RW | 32 bytes
37568 | Slave04 EMD-5 Alarm1 Name | RW | 32 bytes
37584 | Slave04 EMD-6 Alarm1 Name | RW | 32 bytes
37600 | Slave04 EMD-7 Alarm1 Name | RW | 32 bytes
37616 | Slave04 EMD-8 Alarm1 Name | RW | 32 bytes
37632 | Slave05 EMD-1 Alarm1 Name | RW | 32 bytes
37648 | Slave05 EMD-2 Alarm1 Name | RW | 32 bytes
37664 | Slave05 EMD-3 Alarm1 Name | RW | 32 bytes
37680 | Slave05 EMD-4 Alarm1 Name | RW | 32 bytes
37696 | Slave05 EMD-5 Alarm1 Name | RW | 32 bytes
37712 | Slave05 EMD-6 Alarm1 Name | RW | 32 bytes
37728 | Slave05 EMD-7 Alarm1 Name | RW | 32 bytes
37744 | Slave05 EMD-8 Alarm1 Name | RW | 32 bytes
37760 | Slave06 EMD-1 Alarm1 Name | RW | 32 bytes
37776 | Slave06 EMD-2 Alarm1 Name | RW | 32 bytes
37792 | Slave06 EMD-3 Alarm1 Name | RW | 32 bytes
37808 | Slave06 EMD-4 Alarm1 Name | RW | 32 bytes
37824 | Slave06 EMD-5 Alarm1 Name | RW | 32 bytes
37840 | Slave06 EMD-6 Alarm1 Name | RW | 32 bytes
37856 | Slave06 EMD-7 Alarm1 Name | RW | 32 bytes
37872 | Slave06 EMD-8 Alarm1 Name | RW | 32 bytes
37888 | Slave07 EMD-1 Alarm1 Name | RW | 32 bytes
37904 | Slave07 EMD-2 Alarm1 Name | RW | 32 bytes
37920 | Slave07 EMD-3 Alarm1 Name | RW | 32 bytes
37936 | Slave07 EMD-4 Alarm1 Name | RW | 32 bytes
37952 | Slave07 EMD-5 Alarm1 Name | RW | 32 bytes
37968 | Slave07 EMD-6 Alarm1 Name | RW | 32 bytes
37984 | Slave07 EMD-7 Alarm1 Name | RW | 32 bytes
38000 | Slave07 EMD-8 Alarm1 Name | RW | 32 bytes
38016 | Slave08 EMD-1 Alarm1 Name | RW | 32 bytes
38032 | Slave08 EMD-2 Alarm1 Name | RW | 32 bytes
38048 | Slave08 EMD-3 Alarm1 Name | RW | 32 bytes
38064 | Slave08 EMD-4 Alarm1 Name | RW | 32 bytes
38080 | Slave08 EMD-5 Alarm1 Name | RW | 32 bytes
38096 | Slave08 EMD-6 Alarm1 Name | RW | 32 bytes
38112 | Slave08 EMD-7 Alarm1 Name | RW | 32 bytes
38128 | Slave08 EMD-8 Alarm1 Name | RW | 32 bytes
38144 | Slave09 EMD-1 Alarm1 Name | RW | 32 bytes
38160 | Slave09 EMD-2 Alarm1 Name | RW | 32 bytes
38176 | Slave09 EMD-3 Alarm1 Name | RW | 32 bytes
38192 | Slave09 EMD-4 Alarm1 Name | RW | 32 bytes
38208 | Slave09 EMD-5 Alarm1 Name | RW | 32 bytes
38224 | Slave09 EMD-6 Alarm1 Name | RW | 32 bytes
38240 | Slave09 EMD-7 Alarm1 Name | RW | 32 bytes
38256 | Slave09 EMD-8 Alarm1 Name | RW | 32 bytes
38272 | Slave10 EMD-1 Alarm1 Name | RW | 32 bytes
38288 | Slave10 EMD-2 Alarm1 Name | RW | 32 bytes
38304 | Slave10 EMD-3 Alarm1 Name | RW | 32 bytes
38320 | Slave10 EMD-4 Alarm1 Name | RW | 32 bytes
38336 | Slave10 EMD-5 Alarm1 Name | RW | 32 bytes
38352 | Slave10 EMD-6 Alarm1 Name | RW | 32 bytes
38368 | Slave10 EMD-7 Alarm1 Name | RW | 32 bytes
38384 | Slave10 EMD-8 Alarm1 Name | RW | 32 bytes
38400 | Slave11 EMD-1 Alarm1 Name | RW | 32 bytes
38416 | Slave11 EMD-2 Alarm1 Name | RW | 32 bytes
38432 | Slave11 EMD-3 Alarm1 Name | RW | 32 bytes
38448 | Slave11 EMD-4 Alarm1 Name | RW | 32 bytes
38464 | Slave11 EMD-5 Alarm1 Name | RW | 32 bytes
38480 | Slave11 EMD-6 Alarm1 Name | RW | 32 bytes
38496 | Slave11 EMD-7 Alarm1 Name | RW | 32 bytes
38512 | Slave11 EMD-8 Alarm1 Name | RW | 32 bytes
38528 | Slave12 EMD-1 Alarm1 Name | RW | 32 bytes
38544 | Slave12 EMD-2 Alarm1 Name | RW | 32 bytes
38560 | Slave12 EMD-3 Alarm1 Name | RW | 32 bytes
38576 | Slave12 EMD-4 Alarm1 Name | RW | 32 bytes
38592 | Slave12 EMD-5 Alarm1 Name | RW | 32 bytes
38608 | Slave12 EMD-6 Alarm1 Name | RW | 32 bytes
38624 | Slave12 EMD-7 Alarm1 Name | RW | 32 bytes
38640 | Slave12 EMD-8 Alarm1 Name | RW | 32 bytes
38656 | Slave13 EMD-1 Alarm1 Name | RW | 32 bytes
38672 | Slave13 EMD-2 Alarm1 Name | RW | 32 bytes
38688 | Slave13 EMD-3 Alarm1 Name | RW | 32 bytes
38704 | Slave13 EMD-4 Alarm1 Name | RW | 32 bytes
38720 | Slave13 EMD-5 Alarm1 Name | RW | 32 bytes
38736 | Slave13 EMD-6 Alarm1 Name | RW | 32 bytes
38752 | Slave13 EMD-7 Alarm1 Name | RW | 32 bytes
38768 | Slave13 EMD-8 Alarm1 Name | RW | 32 bytes
38784 | Slave14 EMD-1 Alarm1 Name | RW | 32 bytes
38800 | Slave14 EMD-2 Alarm1 Name | RW | 32 bytes
38816 | Slave14 EMD-3 Alarm1 Name | RW | 32 bytes
38832 | Slave14 EMD-4 Alarm1 Name | RW | 32 bytes
38848 | Slave14 EMD-5 Alarm1 Name | RW | 32 bytes
38864 | Slave14 EMD-6 Alarm1 Name | RW | 32 bytes
38880 | Slave14 EMD-7 Alarm1 Name | RW | 32 bytes
38896 | Slave14 EMD-8 Alarm1 Name | RW | 32 bytes
38912 | Slave15 EMD-1 Alarm1 Name | RW | 32 bytes
38928 | Slave15 EMD-2 Alarm1 Name | RW | 32 bytes
38944 | Slave15 EMD-3 Alarm1 Name | RW | 32 bytes
38960 | Slave15 EMD-4 Alarm1 Name | RW | 32 bytes
38976 | Slave15 EMD-5 Alarm1 Name | RW | 32 bytes
38992 | Slave15 EMD-6 Alarm1 Name | RW | 32 bytes
39008 | Slave15 EMD-7 Alarm1 Name | RW | 32 bytes
39024 | Slave15 EMD-8 Alarm1 Name | RW | 32 bytes
39040 | Master EMD-1 Alarm2 Name | RW | 32 bytes
39056 | Master EMD-2 Alarm2 Name | RW | 32 bytes
39072 | Master EMD-3 Alarm2 Name | RW | 32 bytes
39088 | Master EMD-4 Alarm2 Name | RW | 32 bytes
39104 | Master EMD-5 Alarm2 Name | RW | 32 bytes
39120 | Master EMD-6 Alarm2 Name | RW | 32 bytes
39136 | Master EMD-7 Alarm2 Name | RW | 32 bytes
39152 | Master EMD-8 Alarm2 Name | RW | 32 bytes
39168 | Slave01 EMD-1 Alarm2 Name | RW | 32 bytes
39184 | Slave01 EMD-2 Alarm2 Name | RW | 32 bytes
39200 | Slave01 EMD-3 Alarm2 Name | RW | 32 bytes
39216 | Slave01 EMD-4 Alarm2 Name | RW | 32 bytes
39232 | Slave01 EMD-5 Alarm2 Name | RW | 32 bytes
39248 | Slave01 EMD-6 Alarm2 Name | RW | 32 bytes
39264 | Slave01 EMD-7 Alarm2 Name | RW | 32 bytes
39280 | Slave01 EMD-8 Alarm2 Name | RW | 32 bytes
39296 | Slave02 EMD-1 Alarm2 Name | RW | 32 bytes
39312 | Slave02 EMD-2 Alarm2 Name | RW | 32 bytes
39328 | Slave02 EMD-3 Alarm2 Name | RW | 32 bytes
39344 | Slave02 EMD-4 Alarm2 Name | RW | 32 bytes
39360 | Slave02 EMD-5 Alarm2 Name | RW | 32 bytes
39376 | Slave02 EMD-6 Alarm2 Name | RW | 32 bytes
39392 | Slave02 EMD-7 Alarm2 Name | RW | 32 bytes
39408 | Slave02 EMD-8 Alarm2 Name | RW | 32 bytes
39424 | Slave03 EMD-1 Alarm2 Name | RW | 32 bytes
39440 | Slave03 EMD-2 Alarm2 Name | RW | 32 bytes
39456 | Slave03 EMD-3 Alarm2 Name | RW | 32 bytes
39472 | Slave03 EMD-4 Alarm2 Name | RW | 32 bytes
39488 | Slave03 EMD-5 Alarm2 Name | RW | 32 bytes
39504 | Slave03 EMD-6 Alarm2 Name | RW | 32 bytes
39520 | Slave03 EMD-7 Alarm2 Name | RW | 32 bytes
39536 | Slave03 EMD-8 Alarm2 Name | RW | 32 bytes
39552 | Slave04 EMD-1 Alarm2 Name | RW | 32 bytes
39568 | Slave04 EMD-2 Alarm2 Name | RW | 32 bytes
39584 | Slave04 EMD-3 Alarm2 Name | RW | 32 bytes
39600 | Slave04 EMD-4 Alarm2 Name | RW | 32 bytes
39616 | Slave04 EMD-5 Alarm2 Name | RW | 32 bytes
39632 | Slave04 EMD-6 Alarm2 Name | RW | 32 bytes
39648 | Slave04 EMD-7 Alarm2 Name | RW | 32 bytes
39664 | Slave04 EMD-8 Alarm2 Name | RW | 32 bytes
39680 | Slave05 EMD-1 Alarm2 Name | RW | 32 bytes
39696 | Slave05 EMD-2 Alarm2 Name | RW | 32 bytes
39712 | Slave05 EMD-3 Alarm2 Name | RW | 32 bytes
39728 | Slave05 EMD-4 Alarm2 Name | RW | 32 bytes
39744 | Slave05 EMD-5 Alarm2 Name | RW | 32 bytes
39760 | Slave05 EMD-6 Alarm2 Name | RW | 32 bytes
39776 | Slave05 EMD-7 Alarm2 Name | RW | 32 bytes
39792 | Slave05 EMD-8 Alarm2 Name | RW | 32 bytes
39808 | Slave06 EMD-1 Alarm2 Name | RW | 32 bytes
39824 | Slave06 EMD-2 Alarm2 Name | RW | 32 bytes
39840 | Slave06 EMD-3 Alarm2 Name | RW | 32 bytes
39856 | Slave06 EMD-4 Alarm2 Name | RW | 32 bytes
39872 | Slave06 EMD-5 Alarm2 Name | RW | 32 bytes
39888 | Slave06 EMD-6 Alarm2 Name | RW | 32 bytes
39904 | Slave06 EMD-7 Alarm2 Name | RW | 32 bytes
39920 | Slave06 EMD-8 Alarm2 Name | RW | 32 bytes
39936 | Slave07 EMD-1 Alarm2 Name | RW | 32 bytes
39952 | Slave07 EMD-2 Alarm2 Name | RW | 32 bytes
39968 | Slave07 EMD-3 Alarm2 Name | RW | 32 bytes
39984 | Slave07 EMD-4 Alarm2 Name | RW | 32 bytes
40000 | Slave07 EMD-5 Alarm2 Name | RW | 32 bytes
40016 | Slave07 EMD-6 Alarm2 Name | RW | 32 bytes
40032 | Slave07 EMD-7 Alarm2 Name | RW | 32 bytes
40048 | Slave07 EMD-8 Alarm2 Name | RW | 32 bytes
40064 | Slave08 EMD-1 Alarm2 Name | RW | 32 bytes
40080 | Slave08 EMD-2 Alarm2 Name | RW | 32 bytes
40096 | Slave08 EMD-3 Alarm2 Name | RW | 32 bytes
40112 | Slave08 EMD-4 Alarm2 Name | RW | 32 bytes
40128 | Slave08 EMD-5 Alarm2 Name | RW | 32 bytes
40144 | Slave08 EMD-6 Alarm2 Name | RW | 32 bytes
40160 | Slave08 EMD-7 Alarm2 Name | RW | 32 bytes
40176 | Slave08 EMD-8 Alarm2 Name | RW | 32 bytes
40192 | Slave09 EMD-1 Alarm2 Name | RW | 32 bytes
40208 | Slave09 EMD-2 Alarm2 Name | RW | 32 bytes
40224 | Slave09 EMD-3 Alarm2 Name | RW | 32 bytes
40240 | Slave09 EMD-4 Alarm2 Name | RW | 32 bytes
40256 | Slave09 EMD-5 Alarm2 Name | RW | 32 bytes
40272 | Slave09 EMD-6 Alarm2 Name | RW | 32 bytes
40288 | Slave09 EMD-7 Alarm2 Name | RW | 32 bytes
40304 | Slave09 EMD-8 Alarm2 Name | RW | 32 bytes
40320 | Slave10 EMD-1 Alarm2 Name | RW | 32 bytes
40336 | Slave10 EMD-2 Alarm2 Name | RW | 32 bytes
40352 | Slave10 EMD-3 Alarm2 Name | RW | 32 bytes
40368 | Slave10 EMD-4 Alarm2 Name | RW | 32 bytes
40384 | Slave10 EMD-5 Alarm2 Name | RW | 32 bytes
40400 | Slave10 EMD-6 Alarm2 Name | RW | 32 bytes
40416 | Slave10 EMD-7 Alarm2 Name | RW | 32 bytes
40432 | Slave10 EMD-8 Alarm2 Name | RW | 32 bytes
40448 | Slave11 EMD-1 Alarm2 Name | RW | 32 bytes
40464 | Slave11 EMD-2 Alarm2 Name | RW | 32 bytes
40480 | Slave11 EMD-3 Alarm2 Name | RW | 32 bytes
40496 | Slave11 EMD-4 Alarm2 Name | RW | 32 bytes
40512 | Slave11 EMD-5 Alarm2 Name | RW | 32 bytes
40528 | Slave11 EMD-6 Alarm2 Name | RW | 32 bytes
40544 | Slave11 EMD-7 Alarm2 Name | RW | 32 bytes
40560 | Slave11 EMD-8 Alarm2 Name | RW | 32 bytes
40576 | Slave12 EMD-1 Alarm2 Name | RW | 32 bytes
40592 | Slave12 EMD-2 Alarm2 Name | RW | 32 bytes
40608 | Slave12 EMD-3 Alarm2 Name | RW | 32 bytes
40624 | Slave12 EMD-4 Alarm2 Name | RW | 32 bytes
40640 | Slave12 EMD-5 Alarm2 Name | RW | 32 bytes
40656 | Slave12 EMD-6 Alarm2 Name | RW | 32 bytes
40672 | Slave12 EMD-7 Alarm2 Name | RW | 32 bytes
40688 | Slave12 EMD-8 Alarm2 Name | RW | 32 bytes
40704 | Slave13 EMD-1 Alarm2 Name | RW | 32 bytes
40720 | Slave13 EMD-2 Alarm2 Name | RW | 32 bytes
40736 | Slave13 EMD-3 Alarm2 Name | RW | 32 bytes
40752 | Slave13 EMD-4 Alarm2 Name | RW | 32 bytes
40768 | Slave13 EMD-5 Alarm2 Name | RW | 32 bytes
40784 | Slave13 EMD-6 Alarm2 Name | RW | 32 bytes
40800 | Slave13 EMD-7 Alarm2 Name | RW | 32 bytes
40816 | Slave13 EMD-8 Alarm2 Name | RW | 32 bytes
40832 | Slave14 EMD-1 Alarm2 Name | RW | 32 bytes
40848 | Slave14 EMD-2 Alarm2 Name | RW | 32 bytes
40864 | Slave14 EMD-3 Alarm2 Name | RW | 32 bytes
40880 | Slave14 EMD-4 Alarm2 Name | RW | 32 bytes
40896 | Slave14 EMD-5 Alarm2 Name | RW | 32 bytes
40912 | Slave14 EMD-6 Alarm2 Name | RW | 32 bytes
40928 | Slave14 EMD-7 Alarm2 Name | RW | 32 bytes
40944 | Slave14 EMD-8 Alarm2 Name | RW | 32 bytes
40960 | Slave15 EMD-1 Alarm2 Name | RW | 32 bytes
40976 | Slave15 EMD-2 Alarm2 Name | RW | 32 bytes
40992 | Slave15 EMD-3 Alarm2 Name | RW | 32 bytes
41008 | Slave15 EMD-4 Alarm2 Name | RW | 32 bytes
41024 | Slave15 EMD-5 Alarm2 Name | RW | 32 bytes
41040 | Slave15 EMD-6 Alarm2 Name | RW | 32 bytes
41056 | Slave15 EMD-7 Alarm2 Name | RW | 32 bytes
41072 | Slave15 EMD-8 Alarm2 Name | RW | 32 bytes
41088 | Master PDU Status | RO | 2 bytes